OPERATING CODE NO. 9

(OC9)

GRID CODE MODIFICATION GC0156

DATED 15 JUNE 2023

CONTINGENCY PLANNING

Text taken from GC0148 when submitted to Ofgem in October 2022

CONTENTS

(This contents page does not form part of the Grid Code)

Paragraph No/Title	Page Number

OC9.1   INTRODUCTION	2

OC9.2   OBJECTIVE	3

OC9.3   SCOPE	4

OC9.4   SYSTEM RESTORATION	4

OC9.4.1 - OC9.4.4   Total Shutdown And Partial Shutdown	4

OC9.4.5   Contribution to System Restoration	5

OC9.5   RE-SYNCHRONISATION OF DE-SYNCHRONISED ISLANDS	21

OC9.5.2   Options	22

OC9.5.3   Choice Of Option	24

OC9.5.4   Agreeing Procedures	25

OC9.6   JOINT SYSTEM INCIDENT PROCEDURE	27

OC9.1	INTRODUCTION

Operating Code No.9 ("OC9") covers the

processes and procedures by which The Company in coordination and liaison with Users, will restore the Total System or parts of the System following a Total Shutdown or Partial Shutdown.

OC9.1.1	Approach to System Restoration

The Company is obliged through its Licence  to achieve System Restoration within the parameters of the Electricity System Restoration Standard.

Electricity System Demand in the context of the “Electricity System Restoration Standard”, is considered by The Company to be the forecast peak National Demand which would have occurred within the 24 hour period following the start of the Total Shutdown or Partial Shutdown had the Total Shutdown or Partial Shutdown not occurred.  Under the Electricity System Restoration Standard, 60% of peak National Demand is to be restored across all System Restoration Regions in 24 hours and 100% peak National Demand is to be restored across System Restoration Regions in 5 days.

Following a Total Shutdown or Partial Shutdown, there are two ways in which the Total System (or the disconnected part of the System in the case of a Partial Shutdown) can be re-established.  These being a top-down approach using Local Joint Restoration Plans or a bottom-up approach using Distribution Restoration Zone Plans.

Any Local Joint Restoration Plan and/or Distribution Restoration Zone Plan comprising common Transmission Licensees’s, Network Operator’s or Restoration Contractor’s assets cannot be activated at the same time.  However, this would not preclude a Local Joint Restoration Plan or Distributed Restoration Zone Plan from being activated at the same site(s) where there is segregation between them.

OC9.1.2	Re-Synchronisation of Power Islands

Following the establishment of Power Islands (either through the implementation of Local Joint Restoration Plans or Distribution Restoration Zone Plans), The Company will then co-ordinate the Re-Synchronisation of parts of the Total System which have become Out of Synchronism with each other irrespective of whether or not a Total Shutdown or Partial Shutdown has occurred.

OC9.1.3	Joint System Incident Procedure

A Joint System Incident procedure requires the establishment of communication routes and arrangements between senior management representatives of The Company and Users involved in, or who may be involved in, an actual or potential serious or widespread disruption to the Total System or a part of the Total System, which requires, or may require, urgent managerial response, day or night, but which does not fall within the provisions of OC9.1.5.

OC9.1.4	Relevant Transmission Licensees shall comply with OC9.4 and OC9.5 as provided for in STCP 06-1 and any relevant Local Joint Restoration Plan or Distribution Restoration Zone Plan or OC9 De-Synchronised Island Procedure where and to the extent that such matters apply to them.

OC9.1.5	Directions Issued by the Secretary of State

It should be noted that under section 96 of the Act, the Secretary of State may give directions to The Company and/or any Generator and/or any Supplier, for the purpose of "mitigating the effects of any civil emergency which may occur" (ie. for the purposes of planning for a civil emergency); a civil emergency is defined in the Act as "any natural disaster or other emergency which, in the opinion of the Secretary of State, is or may be likely to disrupt electricity supplies".  Under the Energy Act 1976, the Secretary of State has powers to make orders and give directions controlling the production, supply, acquisition or use of electricity, where an Order in Council under section 3 is in force declaring that there is an actual or imminent emergency affecting electricity supplies.  In the event that any such directions are given, or orders made under the Energy Act 1976, the provisions of the Grid Code will be suspended in so far as they are inconsistent with them.

OC9.2	OBJECTIVE

The overall objectives of OC9 are:

OC9.2.1	To achieve the requirements of the Electricity System Restoration Standard, taking into account the capability of Restoration Contractor’s Plant and Apparatus as well as other Users’ Plant and Apparatus capabilities, including Embedded Generating Units and External Interconnections and the operational constraints of the Total System.

OC9.2.2	To initiate the restoration process through the activation of Local Joint Restoration Plans and/or Distribution Restoration Zone Plans followed by the subsequent Re-Synchronisation and expansion of Power Islands.

OC9.2.3	To achieve the Re-Synchronisation of parts of the Total System which have become Out of Synchronism with each other.

OC9.2.4	To ensure that communication routes and arrangements are available to enable senior management representatives of The Company and Users, who are authorised to make binding decisions on behalf of The Company or the relevant User, as the case may be, to communicate with each other in the situation described in OC9.1.3.

OC9.2.5	To describe the role that The Company, Relevant Transmission Licensees, Network Operators and Restoration Contractors may have in the restoration processes as detailed in the relevant OC9 De-Synchronised Island Procedures, Local Joint Restoration Plans and Distribution Restoration Zone Plans.

OC9.2.6	To identify and address as far as possible the events and processes necessary to enable the restoration of the Total System, after a Total Shutdown or Partial Shutdown.  This is likely to require the following key processes to be implemented, typically, but not necessarily, in the order given below:

- Selectively implement Local Joint Restoration Plans

- Selectively implement Distribution Restoration Zone Plans in conjunction with Network Operators

(iii)	Expand Power Islands to supply Power Stations

(iv)	Expand and merge Power Islands leading to Total System energisation

(v)	Selectively reconnect Demand

(vi) 	Facilitate and co-ordinate returning the Total System back to normal operation

(vii) 	Resumption of the Balancing Mechanism if suspended in accordance with the provisions of the BSC.

OC9.3	SCOPE

OC9.3.1	OC9 applies to The Company and to Users, which in OC9 means:-

(a)	Generators;

(b)	Network Operators;

(c)	Non-Embedded Customers;

(d)	HVDC System Owners;

(e)	DC Converter owners including DC Converter Station owners

(f)	Restoration Contractors; and

(h)	Relevant Transmission Licensees as provided for in the STC.

OC9.3.2	The procedure for the establishment of emergency support/contingency planning between The Company and Externally Interconnected System Operators is set out in the Interconnection Agreement with each Externally Interconnected System Operator.

OC9.4

SYSTEM RESTORATION

Total Shutdown and Partial Shutdown

OC9.4.1	A "Total Shutdown" is the situation existing when all generation has ceased and there is no electricity supply from External Interconnections. Therefore, the Total System has shutdown with the result that it is not possible for the Total System to begin to function again without The Company's directions relating to System Restoration.

OC9.4.2	A "Partial Shutdown" is the same as a Total Shutdown except that all generation has ceased in a separate part of the Total System and there is no electricity supply from External Interconnections or other parts of the Total System to that part of the Total System. Therefore, that part of the Total System is shutdown with the result that it is not possible for that part of the Total System to begin to function again without The Company's directions relating to  System Restoration.

OC9.4.3	During a Total Shutdown or Partial Shutdown and during the subsequent recovery, the Licence Standards may not apply and the Total System may be operated outside normal voltage and Frequency standards.

OC9.4.4	In a Total Shutdown and in a Partial Shutdown and during the subsequent recovery, it is likely to be necessary for The Company to issue Emergency Instructions in accordance with BC2.9.

OC9.4.5	Contribution to System Restoration

The Company will initially start to restore the System following a Total Shutdown or Partial Shutdown by issuing instructions directly to Restoration Contractors through one or more Local Joint Restoration Plans as provided for in OC9.4.5.1 and/or by instructing Network Operators to activate one or more Distribution Restoration Zone Plans as provided for in OC9.4.5.2.

OC9.4.5.1 		Local Joint Restoration

OC9.4.5.1.1	Local Joint Restoration Plans are dependent upon Anchor Restoration Contractors who upon instruction from The Company (or Relevant Transmission Licensee in Scotland), shall Start-Up their Anchor Plant from Shutdown and energise a part of the Total System, within two hours, without an external electrical power supply

.  Local Joint Restoration Plans may also be dependent upon Top Up Restoration Contractors.  A Local Joint Restoration Plan may include more than one Restoration Contractor whose Plant has an Anchor Plant Capability or Top Up Capability. When a Local Joint Restoration Plan is activated, only one Restoration Contractor will operate as the Anchor Generator with the other Restoration Contractors potentially taking roles as Top-Up Contractors.  The Local Joint Restoration Plan will detail how these responsibilities will be allocated.

OC9.4.5.1.2	Local Joint Restoration Plans will be produced jointly by The Company, Relevant Transmission Licensees, relevant Restoration Contractors and relevant Network Operators in accordance with the provisions of OC9.4.7.6.1(a). The Local Joint Restoration Plan will detail the agreed method and procedure by which Anchor Plant will energise part of the Total System and in combination with Top Up Restoration Plant (where necessary) to meet complementary local Demand so as to form a Power Island.

OC9.4.5.	2	Distribution Restoration Zones

OC9.4.5.2.1	Distribution Restoration Zone Plans are dependent upon Anchor Restoration Contractors who, upon instruction from relevant Network Operators, shall Start-Up their Anchor Plant from Shutdown and energise a part of a Network Operator’s System, , within eight hours, without an external electrical power supply.  A Distribution Restoration Zone Plan may also be dependent upon Top Up Restoration Contractors.

OC9.4.5.2.2	For each Distribution Restoration Zone, a Distribution Restoration Zone Plan will be produced jointly by the Network Operator, The Company, Relevant Transmission Licensee, and Restoration Contractors in accordance with the provisions of OC9.4.7.6.1(b).  The Distribution Restoration Zone Plan will detail the agreed method and procedure by which an Anchor Plant will energise part of the Total System and in combination with Top Up Restoration Plant (where necessary) meet complementary local Demand so as to form a Power Island.  A Distribution Restoration Zone Plan may include more than one Restoration Contractor whose Plant has an Anchor Plant Capability or Top Up Restoration Capability. When a Distribution Restoration Zone Plan is activated, only one Restoration Contractor will operate as the Anchor Restoration Contractor with the other Restoration Contractors potentially taking roles as Top-Up Restoration Contractors.  The Distribution Restoration Zone Plan will detail how these responsibilities will be allocated.

OC9.4.6 	Situations requiring System Restoration

In the event of a Total Shutdown or Partial Shutdown, The Company will, as soon as reasonably practical, inform Users (or, in the case of a Partial Shutdown, Users which in The Company's opinion need to be informed) and the BSCCo that a Total Shutdown, or, as the case may be, a Partial Shutdown, exists and that The Company intends to implement System Restoration. The Company shall (as soon as is practicable) determine, in its reasonable opinion, the time and date with effect from which the Total Shutdown or Partial Shutdown commenced and notify the BSCCo of that time and date.

In the event of a Total Shutdown and following such notification, in accordance with the provisions of the BSC, the BSCCo will determine the Settlement Period with effect from which the Balancing Mechanism is suspended.

In the event of a Partial Shutdown and following such notification, the Balancing Mechanism will not be suspended until such time and date that the Market Suspension Threshold has been met, or deemed to have been met, in accordance with the provisions of the BSC. The Company shall carry out the monitoring activities required by paragraph G3.1 of the BSC.

Following determination by The Company pursuant to its obligations under the BSC that the Market Suspension Threshold has been met, or deemed to have been met, The Company shall (as soon as practicable) inform the BSCCo of that time and date at which the Market Suspension Threshold was met, or deemed to have been met, and the BSCCo will determine the Settlement Period in accordance with the provisions of the BSC with effect from which the Balancing Mechanism will be suspended.

Should The Company determine that the Total System is capable of returning to normal operation without meeting the Market Suspension Threshold, The Company will follow the procedure given in OC9.4.7.11.

System Restoration will conclude with effect from the time and date determined in accordance with OC9.4.7.6.3(d).

In respect of Scottish Transmission Systems, in exceptional circumstances, as specified in the Local Joint Restoration Plan, SPT or SHETL, may invoke such Local Joint Restoration Plan for their own Transmission Systems, Scottish Offshore Transmission Systems and relevant Scottish CATO Transmission Systems . Under such circumstances, SPT or SHETL, may instruct relevant Network Operators to activate one or more Distribution Restoration Zone Plans.

OC9.4.7 	SYSTEM RESTORATION PROCEDURE

OC9.4.7.1 	The procedure necessary for a recovery from a Total Shutdown or Partial Shutdown is known as a System Restoration. The procedure for a Partial Shutdown is the same as that for a Total Shutdown except that it applies only to a part of the Total System. It should be remembered that a Partial Shutdown may affect parts of the Total System which are not themselves shutdown.

OC9.4.7.2 	The complexities and uncertainties of recovery from a Total Shutdown or Partial Shutdown require that OC9 is sufficiently flexible in order to accommodate the full range of User’s Plant and Apparatus and Total System characteristics and operational possibilities, and this precludes the setting out in the Grid Code itself of concise chronological sequences. The overall strategy will, in general, include the overlapping phases of the use of generating Plant, at an isolated Power Station, or isolated HVDC System or isolated DC Converter Station, together with complementary local Demand, termed Power Islands, step by step integration of these Power Islands into larger sub-systems which includes utilising the procedures in OC9.5 (Re-Synchronisation of Power Islands) and eventually re-establishment of the complete Total System.

The Company Instructions

OC9.4.7.3 	The Company will determine and instruct relevant Users to start System Restoration. These instructions will normally recognise any applicable Local Joint Restoration Plan and/or Distribution Restoration Zone Plan. User’s shall abide by The Company's instructions during System Restoration, even if these conflict with the general overall strategy outlined in OC9.4.7.6.3 or any applicable Local Joint Restoration Plan and/or Distribution Restoration Zone Plan although a User may still reject an Emergency Instruction but only on safety grounds (relating to personnel or plant) and this must be notified to The Company immediately by telephone in accordance with the requirements of BC2.9.2.1. The Company's and/or Network Operator’s instructions may (although this list should not be regarded as exhaustive) be issued to;-

- Restoration Contractors relating to the start of supplying Active Power and subsequent pick up of Demand;

- Network Operators or Non-Embedded Customers relating to the restoration of Demand;

- Generators or HVDC System Owners or DC Converter Station owners relating to the preparations for starting to supply Active Power when an external power supply is made available to it;

- Network Operators to activate a Distribution Restoration Zone Plan.

Each of the above cases may include the requirement to undertake switching.

In respect of Scottish Transmission Systems, SPT and SHETL will act on The Company’s behalf in accordance with its duties under the relevant Local Joint Restoration Plan or Distribution Restoration Zone Plan.  Restoration Contractors and Scottish CATOs in Scotland shall abide by SPT’s or SHETL’s instructions given in accordance with the Local Joint Restoration Plan or Network Operator’s instructions given in accordance with the Distribution Restoration Zone Plan.

OC9.4.7.4 	(a)		System Restoration following a Total Shutdown or where the Balancing Mechanism 	has been suspended following a Partial Shutdown

During System Restoration where the Balancing Mechanism has been suspended, all instructions by The Company to Users will be deemed to be Emergency Instructions under BC2.9.2.2 (iii).  All such Emergency Instructions will recognise any differing operational capabilities (however termed) set out in the relevant Ancillary Services Agreement in preference to the declared operational capability as registered pursuant to BC1 (or as amended from time to time in accordance with the BC).

Instructions issued to Network Operators in England and Wales to activate a Distribution Restoration Zone Plan will be issued by The Company as Emergency Instructions.  Network Operators will then proceed in accordance with the provisions of the Distribution Restoration Zone Plan.  Such instructions will be deemed to be Emergency Instructions under BC2.9.2.2 (iii).  The Network Operator will be responsible for the operation of the Distribution Restoration Zone which will take into account the capabilities of Restoration Contractors’ Plant and Apparatus and other Plant and Apparatus within the Network Operator’s System. A Restoration Contractor may reject an Emergency Instruction but only on safety grounds (relating to personnel or plant) and this must be notified to The Network Operator immediately.  Such instructions shall be pursuant to the terms of the Distribution Restoration Zone Plan.

SPT and SHETL in Scotland may issue instructions (which shall be deemed to be Emergency Instructions) to relevant Scottish Network Operators to activate one or more Distribution Restoration Zone Plans.   Network Operators in Scotland will be responsible for the operation of the relevant Distribution Restoration Zone which will take into account the capabilities of Restoration Contractors’ Plant and Apparatus and other Plant and Apparatus within the Network Operator’s System. A Restoration Contractor may reject an Emergency Instruction but only on safety grounds (relating to personnel or plant) and this must be notified to the relevant Scottish Network Operator immediately.  Such instructions shall be pursuant to the terms of the Distribution Restoration Zone Plan.

(b) 	System Restoration following a Partial Shutdown where the Balancing Mechanism has not been suspended

During a Partial Shutdown where the Balancing Mechanism has not been suspended, all instructions to Users connected to the Power Island will be deemed to be Emergency Instructions under BC2.9.2.2 (iv).  All such Emergency Instructions will recognise any differing operational capabilities (however termed) set out in the relevant Ancillary Services Agreement in preference to the declared operational capability as registered pursuant to BC1 (or as amended from time to time in accordance with the BC).

During System Restoration where the Balancing Mechanism has not been suspended, The Company may issue instructions to Network Operators in England and Wales to activate a Distribution Restoration Zone Plan.  Such instructions will be deemed to be Emergency Instructions under BC2.9.2.2 (iv).  The Network Operator will be responsible for the operation of the Distribution Restoration Zone which will take into account the capabilities of Restoration Contractor’s Plant and other Plant and Apparatus within the Network Operator’s System. Such instructions would be pursuant to the terms of the Distribution Restoration Zone Plan.

In Scotland, SPT and/or SHETL may issue instructions (which would be deemed to be Emergency Instructions) to Scottish Network Operators, to activate on one or more Distribution Restoration Zone Plans.

OC9.4.7.

5	Requirements to inform The Company and/or Network Operator where a Genset, HVDC System, DC Converter or Restoration Contractor’s Plant and Apparatus cannot operate within its safe operating limits during the Demand restoration process

OC9.4.7.5.1	If following the successful initiation and subsequent termination of a Local Joint Restoration Plan or Distribution Restoration Zone Plan and during the wider System Restoration process, any Genset or HVDC System or DC Converter Station or Restoration Contractor’s Plant and Apparatus cannot, because of the Demand being experienced, keep within its safe operating parameters, the Generator or HVDC System Owner or DC Converter Station owner or Restoration Contractor shall, inform The Company and relevant Network Operator. The Company or relevant Network Operator (as appropriate) will, where possible, either instruct Demand to be altered or will re-configure the Total System or will instruct a User or Restoration Contractors to re-configure its System in order to alleviate the problem being experienced by the Genset or HVDC System or DC Converter or Restoration Contractor’s Plant and Apparatus. If a Local Joint Restoration Plan or Distribution Restoration Zone Plan is in operation, then the arrangements set out therein shall apply. In both scenarios, The Company and/or Network Operator accepts that any decision to keep a Genset or HVDC System or DC Converter Station or Restoration Contractor’s Plant and Apparatus operating, if outside its safe operating parameters, is one for the User or Restoration Contractor concerned alone and accepts that the User or Restoration Contractor may change output on that Genset or HVDC System or DC Converter or Restoration Contractor’s Plant and Apparatus if it believes it is necessary for safety reasons (whether relating to personnel or Plant and/or Apparatus). If such a change is made without prior notice, then the User or Restoration Contractor shall inform The Company and/or Network Operator as soon as reasonably practical (unless a Local Joint Restoration Plan and/or Distribution Restoration Zone Plan is in operation in which case the arrangements set out therein shall apply).  In the case of a Distribution Restoration Zone, where the Network Operator experiences situations where any Restoration Contractor’s Plant and Apparatus is unable to keep within safe operating parameters and this is likely to affect the integrity and progression of the Distribution Restoration Zone, the Network Operator shall inform The Company without delay.

OC9.4.7.6	Local Joint Restoration Plan and Distribution Restoration Zone Plan Establishment, Testing and Provisions

OC9.4.7.6		.1 	Restoration Plan Establishment

The following process shall apply for the establishment of Restoration Plans:

- For a Local Joint Restoration Plan, The Company will identify the need to introduce or modify a Local Joint Restoration Plan and coordinate with the relevant parties as required in this OC9.4.7.6.1.

- For a Distribution Restoration Zone Plan where The Company and a relevant Network Operator agree that introducing or modifying a Distribution Restoration Zone may be beneficial, The Company, the Relevant Transmission Licensee (where appropriate) and the Network Operator shall explore the possibility of establishing a Distribution Restoration Zone Plan as required in this OC9.4.7.6.1.

- The Company, the Relevant Transmission Licensee (where appropriate) and the Network Operator will discuss and agree the detail of a Restoration Plan as soon as reasonably practicable after the potential requirement for a Restoration Plan is identified.  This may involve discussions between relevant potential Restoration Contractors, The Company and the Network Operator.

- For a Distribution Restoration Zone Plan an initial feasibility assessment carried out jointly by The Company and Network Operator may result in The Company running a procurement / tender process.  If after discussions or analysis, The Company, the Relevant Transmission Licensee (where appropriate) and Network Operator agree a Distribution Restoration Zone Plan is not viable, then no further work to develop the Distribution Restoration Zone Plan needs to be carried out.

- Each Restoration Plan will be in relation to a specific Anchor Plant and may include one of more Top Up Restoration Plants.

- The preparation of each Restoration Plan shall include a check whether any network assets cited in each Restoration Plan are included in any other Restoration Plan, and if so, all the Local Joint Restoration Plans or Distribution Restoration Zone Plans containing common assets shall include a specific step that prohibits more than one of any of these Restoration Plans from being activated at any one point in time.

- The Restoration Plan will record which Restoration Contractors and which Restoration Contractor’s sites are covered by the Restoration Plan and set out what is required from The Company, the Network Operator, each Relevant Transmission Licensees and each Restoration Contractor should a System Restoration situation arise.

- Restoration Plans will allow for one of several Restoration Contractors to take the single role of Anchor Generator within the Restoration Plan and for others to provide Top-Up Restoration Capabilities.  When the Restoration Plan is activated, one of the first tasks shall be the designation of the Anchor Generator and confirmation of which parties are acting as Top Up Restoration Contractors.

- Each Local Joint Restoration Plan shall be prepared by The Company. Each Distribution Restoration Zone Plan shall be prepared by the relevant Network Operator.  In both cases the Restoration Plan will be agreed between Network Operator, The Company, the Relevant Transmission Licensee and relevant Restoration Contractors.

- Each page of the Restoration Plan shall bear a date of issue and the issue number.

- When a Restoration Plan has been prepared, it shall be sent to all parties involved for confirmation of its accuracy.

- The Restoration Plan shall then (if its accuracy has been confirmed) be signed on behalf of The Company, the Network Operator, each Relevant Transmission Licensee and each relevant Restoration Contractor by way of written confirmation of its accuracy.

- Once agreed under this OC9.4.7.6.1, the procedure will become a Restoration Plan under the Grid Code and (subject to any change pursuant to this OC9) will apply to The Company, the Network Operator, the Relevant Transmission Licensees and the relevant Restoration Contractors as if it were part of the Grid Code.

- A copy of each signed Local Joint Restoration Plan will be distributed by The Company to the Network Operator, each Relevant Transmission Licensee and to each Restoration Contractor accompanied by a note indicating the date of implementation.

- A copy of each signed Distribution Restoration Zone Plan will be distributed by the Network Operator to The Company, each Relevant Transmission Licensee and to each Restoration Contractor accompanied by a note indicating the date of implementation.

- The Company, Network Operators, the Relevant Transmission Licensees and Restoration Contractors must make the Restoration Plan readily available to the relevant operational staff.

- Each Restoration Plan will include the test criteria to be satisfied by each Restoration Contractor’s Plant and Apparatus when subject to the testing requirements of OC5.7.

- If any party to a Restoration Plan becomes aware that a change is needed to that Restoration Plan, it shall, in the case of Local Joint Restoration Plan, contact The Company or in the case of a Distribution Restoration Zone Plan, the Network Operator to initiate a discussion between The Company, or the Network Operator and the relevant parties to seek to agree the relevant change.  The principles applying to establishing or modifying a Restoration Plan under this OC9.4.7.6.1 shall apply to such discussions and to any consequent changes.

OC9.4.7.6.2	Restoration Plan Testing

The Company, Relevant Transmission Licensees, the Network Operator and the relevant  Restoration Contractors shall conduct regular joint exercises of the Restoration Plan to which they are parties.  The objectives of such exercises include:

To test the effectiveness of the Restoration Plan;

To provide for joint training of the parties in respect of the Restoration Plan;

To maintain the parties’ awareness and familiarity of the Restoration Plan;

To promote understanding of each party’s role under the Restoration Plan; and

•     	To identify any improvement areas which should be incorporated into the Restoration Plan.

The Company shall propose to the parties to a Restoration Plan a date for the exercise to take place.  All the Restoration Plan parties will jointly share the task of planning, preparing, participating in, and facilitating the exercises, which will normally be in desktop format or as otherwise agreed.  The precise timing of the exercise for each Restoration Plan will be agreed by all parties, but will not be less than once every 3 years. These exercises shall be run as part of the wider assurance activities as provided for under OC5.7.4

OC9.4.7.6.3	Restoration Plan Provisions

The following provisions in this OC9.4.7.6.3 apply in relation to Restoration Plans. For Local Joint Restoration Plans, The Company (or in Scotland the relevant Transmission Licensee as assigned by The Company under STCP 06-1) are designated as the lead operator; for Distribution Restoration Zone Plans, the Network Operator is the lead operator.

- Where the lead operator, issues instructions which conflict with a Restoration Plan these instructions will take precedence over the requirements of the Restoration Plan (as set out in OC9.4.7.6.1).

  - When issuing such instructions, the lead operator will state whether or not it wishes the remainder of the Restoration Plan to apply. Where the lead operator has stated that it wishes the remainder of the Restoration Plan to apply, the other parties to the plan may give notice that it is not possible to operate the Restoration Plan to the lead operator and the other parties to plan.

  - The lead operator shall immediately consult with all parties to the Restoration Plan.  Unless all parties reach agreement as to how the Restoration Plan shall operate in those circumstances, operation in accordance with the Restoration Plan will terminate and parties will be relieved of their obligations under the Restoration Plan in accordance with OC9.4.7.6.3(d) below.

(b)	The preparation of each Restoration Plan shall include a check whether any network assets cited in another Local Joint Restoration Plan or another Distribution Restoration Zone Plan are included in the plan, and if so, all the Local Joint Restoration Plans or Distribution Restoration Zone Plans containing common assets shall include a specific step that prohibits more than one of any of these plans from being activated at any one point in time.

(c)	The lead operator will advise other relevant parties of the requirement to switch their User Systems to segregate their Demand and to carry out such other actions as set out in the Restoration Plan.  The relevant party will then operate in accordance with the provisions of the Restoration Plan.

(d)	Operation of the Restoration Plan shall be terminated by the lead operator either when:

  - the Restoration Plan has been successfully implemented and the resulting Power Island has been synchronised to another Power Island following instruction from The Company.  In this case, the arrangements for synchronising the Power Island to the System will be set out in the Restoration Plan; or

  - the Restoration Plan has not been / is not being successfully implemented.  In this circumstance, provided for in OC9.4.7.6.3(a), if an agreement is not reached on whether or not to apply the remainder of the plan or if The Company, in coordination with the other parties, confirms that it does not wish the remainder of the Restoration Plan to apply, the Restoration Plan shall be terminated.  In this case The Company and the Network Operator in conjunction with the Restoration Contractors shall agree and implement the most appropriate course of action which should aim to maintain supplies to as many customers as possible.

In both cases the lead operator shall notify all parties to the Restoration Plan accordingly.

OC9.4.7.7	Local Joint Restoration Plan Operation

Following a Total Shutdown or Partial Shutdown the following shall apply:

OC9.4.7.7.1	Where The Company, as part of System Restoration, has given an instruction to a Restoration Contractor to initiate Start-Up, the relevant Restoration Contractor will prepare to Start-Up their Plant in accordance with the Local Joint Restoration Plan.

OC9.4.7.7.2	The Company will advise the relevant Network Operator of the requirement to switch 	its User System so as to segregate its Demand and to carry out such other actions as set out in the Local Joint Restoration Plan. The relevant Network Operator will then operate in accordance with the provisions of the Local Joint Restoration Plan.

OC9.4.7.7.3	The Company, in coordination with Relevant Transmission Licensees, will ensure that switching carried out on the National Electricity 	Transmission System and other actions are as set out in the Local Joint Restoration Plan.

OC9.4.7.7.4	Following notification from the Anchor Restoration Contractor that their Anchor Plant is ready to accept load and, where provided for in the Local Joint Restoration Plan, Top Up Restoration Contractors are in a position to subsequently synchronise to the Total System as soon as external site supplies are restored, The Company will instruct the Anchor Restoration Contractor (as provided for in OC9.4.5.2.2) to energise part of the Total System. The Anchor Restoration Contractor and the relevant Network Operator will then, in accordance with the requirements of the Local Joint Restoration Plan, establish communication and agree the output of the relevant Anchor Plant and the connection of Demand so as to establish a Power Island.  As part of establishing a Power Island, The Company may instruct one or more Top Up Restoration Contractors to subsequently synchronise their Plant and Apparatus to the System to facilitate supplying more Demand in the Power Island in accordance with the requirements of the Local Joint Restoration Plan.  During this period, Restoration Contractors will be required to regulate the output of their relevant Plant to the Demand prevailing in the Power Island in which it is situated, on the basis that it will (where practicable) seek to maintain the Target Frequency. The Restoration Contractor’s Plant and Apparatus will (where practical) also seek to follow the requirements relating to Reactive Power (which may include the requirement to maintain a target voltage) set out in the Local Joint Restoration Plan.

OC9.4.7.7.5 	Operation in accordance with the Local Joint Restoration Plan will be terminated by The Company or SPT and/ or SHETL in Scotland (by notifying the Network Operator and relevant Restoration Contractors) immediately after successfully connecting the Power Island to another Power Island, or to the User System of another Network Operator, or to the synchronising of Gensets at other Power Stations (which are not owned and operated by Restoration Contractors) or HVDC Systems or DC Converter Stations. Operation in accordance with the Local Joint Restoration Plan will also terminate in the circumstances provided for in OC9.4.7.6.3(d) if an agreement is not reached or if The Company states that it does not wish the remainder of the Local Joint Restoration Plan to apply. Users will then comply with the Bid-Offer Acceptances or Emergency Instructions of The Company.

OC9.4.7.8	Distribution Restoration Zone Operation

Following a Total or Partial Shutdown the following shall apply:

OC9.4.7.8.1	Where The Company wishes a Network Operator to activate a Distribution Restoration Zone Plan, The Company will issue an Emergency Instruction to that Network Operator for it to activate the relevant Distribution Restoration Zone Plan whilst also informing the Relevant Transmission Licensee.  In Scotland the instruction to a Scottish Network Operator to activate a Scottish Distribution Restoration Zone Plan would be given by SPT and / or SHETL.  For the avoidance of doubt, The Company will issue instructions to initiate System Restoration in Scotland via STCP 06-1 which includes arrangements for the activation of Scottish Distribution Restoration Zone Plans.

OC9.4.7.8.2	Upon receipt of an Emergency Instruction from The Company (or instruction from SPT and / or SHETL), the Network Operator will confirm and acknowledge receipt in accordance with the requirements of BC2.9.2 and activate a Distribution Restoration Zone Plan as provided for in OC9.4.7.6.1(b). All instructions to relevant Restoration Contractors party to the Distribution Restoration Zone Plan will be issued by the Network Operator.

OC9.4.7.8.3	The operation of the Distribution Restoration Zone will then continue in accordance with the Distribution Restoration Zone Plan until it is terminated in accordance with the requirements of OC9.4.7.6.3(d).

OC9.4.7.8.4	Where The Company issues an Emergency Instruction (or in Scotland where SPT and / or SHETL issues an instruction) to a Network Operator to activate a Distribution Restoration Zone Plan, the Network Operator will first issue instructions to the Restoration Contractor (as provided for in OC9.4.5.1.1) informing them of the requirement to prepare their Anchor Plant to re-energise a Distribution Restoration Zone (or part thereof) and will (if applicable) then consequently issue instructions to Restoration Contractors in respect of their Top Up Restoration Plant informing them of the requirement to prepare their Top Up Restoration Plant accordance with the Distribution Restoration Zone Plan.  The Network Operator shall also liaise with the Relevant Transmission Licensee where they are party to the Distribution Restoration Zone Plan to ensure switching can take place in the appropriate timescales.  The Network Operator in liaison with the Restoration Contractor(s) will discuss when their Anchor Plant and Top Up Plant are expected to be available.  For the avoidance of doubt, the Anchor Restoration Contractor shall not start to re-energise the Distribution Restoration Zone until instructed by the Network Operator in accordance with OC9.4.7.8.10 and this instruction shall only be given once the Network Operator has configured its System and taken the necessary additional actions to prepare the Distribution Restoration Zone to be re-energised.  This may include any automatic switching that takes place through the action of any Distribution Restoration Zone Control System.  It is only then, that once external site supplies have been restored, and as appliable to the Distribution Restoration Zone Plan, that Network Operators will give instructions (by manual or automatic means) to Restoration Contractors in respect of Top Up Restoration Plant to synchronise to the Network Operator’s System in accordance with OC9.4.7.8.10.

OC9.4.7.8.5	All relevant Restoration Contractors and where applicable Relevant Transmission Licensees will inform the Network Operator of the indicative time when their Plant and Apparatus will be ready to energise or synchronise to the Distribution Restoration Zone.

OC9.4.7.8.6	The Network Operator shall inform The Company (and the Relevant Scottish Transmission Licensee in the case of a Scottish Distribution Restoration Zone) and Transmission Licensees where they are party to the Distribution Restoration Zone Plan advising that it has contacted the appropriate Restoration Contractors in accordance with the Distribution Restoration Zone Plan and the expected time when the Anchor Generator will energise the Distribution Restoration Zone.

OC9.4.7.8.7	In addition to the requirements of OC9.4.7.8.4 to OC9.4.7.8.6, and in accordance with the Distribution Restoration Zone Plan, the Network Operator shall start to reconfigure its System (by manual or automatic means) such that it is ready to enable the Anchor Restoration Contractor to re-energise the Distribution Restoration Zone (or part thereof), and where provided for in the Distribution Restoration Zone Plan, the subsequent synchronisation of Top Up Restoration Plant.  To enable this process to take place, the Network Operator may need to change the topology and status of its System which may include but shall not be limited to changing the status of circuit breakers in addition to switching between pre agreed control system and Protection settings.  Reconfiguration of the Network Operator’s System prior to re-energisation of the Distribution Restoration Zone, may be achieved by instructions carried out manually, switching carried out remotely from the Network Operators Control Centre or via fully automatic means which could include a Distribution Restoration Zone Control System.  Where a Transmission Licensee is party to the Distribution Restoration Zone Plan, the Network Operator shall liaise with the Relevant Transmission Licensee as part of this process to ensure that parts of the Transmission System can be energised from the Distribution Restoration Zone.

OC9.4.7.8.8	Once the Network Operator (and where necessary in accordance with the Relevant Transmission Licensee) has reconfigured its System and associated Plant and Apparatus (including but not limited to Protection and control system settings) it will contact the Anchor Restoration Contractor (be it by manual or automatic means) and agree a time for the Anchor Plant to re-energise the Distribution Restoration Zone (or part thereof). Where the Anchor Restoration Contractor or Network Operator needs to change the agreed proposed re-energisation time as a result of an unforeseen event such as, but not limited to, a faulty item of Plant or Apparatus, safety issue or unavailability of personnel, the Anchor Restoration Contractor and/or Network Operator will agree a revised re-energisation time.  The Anchor Restoration Contractor and the relevant Network Operator will in accordance with the requirements of the Distribution Restoration Zone Plan, establish communication and agree the planned output of the relevant Anchor Plant and the connection of Demand to plan the formation of the Power Island.

OC9.4.7.8.9	The Network Operator will inform The Company (or relevant Scottish Transmission Licensee in the case of a Scottish Distribution Restoration Zone) or Relevant Transmission Licensee where they are party to the Distribution Restoration Zone Plan of the time when the Anchor Restoration Contractor is estimated  to re-energise a section of the Network Operator’s System.  Should this estimated time vary, the Network Operator will inform The Company (or relevant Scottish Transmission Licensee in the case of a Scottish Distribution Restoration Zone) to state the revised estimated re-energisation time and the reason for the change.

OC9.4.7.8.10	The Restoration Contractor shall contact the Network Operator once their Anchor Plant is ready to re-energise the network. The Network Operator shall then assess their network status, the estimated re-energisation time as detailed in OC9.4.7.8.8 and if conditions are suitable, the Network Operator will issue an instruction to the Anchor Restoration Contractor (by manual or automatic means) to re-energise the Distribution Restoration Zone (or part thereof).  Following the issue of instructions to the Anchor Restoration Contractor, and successful re-energisation of the Distribution Restoration Zone (or part thereof) the Network Operator will instruct (by manual or automatic means) Top Up Restoration Contractors party to the Distribution Restoration Zone Plan to synchronise to the Distribution Restoration Zone.  The Network Operator shall also inform the Relevant Transmission Licensee when an instruction has been issued to the Restoration Contractor where they are party to the Distribution Restoration Zone Plan.

OC9.4.7.8.11	Once the Distribution Restoration Zone (or part thereof) has been re-energised and feeding some local Demand or controllable Demand provided by a relevant Restoration Contractor, they will be required to follow instructions from the Network Operator (by manual or automatic means) in accordance with the Distribution Restoration Zone Plan.  The Network Operator and/or Distribution Restoration Zone Control System shall issue instructions to Restoration Contractors as necessary to ensure the Distribution Restoration Zone continues to run in a stable manner.  As part of this process, the Network Operator, in coordination with  Restoration Contractors, shall ensure risks to the Network Operator’s System or the Restoration Contractor’s Plant, that could arise through disturbances in the Distribution Restoration Zone, are minimised as far as reasonably practicable.  This may be assisted through a planned series of re-energisation steps within the Distribution Restoration Zone, taking account of the capability and performance of the Restoration Contractor’s Plant at that time.

OC9.4.7.8.12	Demand within the Distribution Restoration Zone can be restored by manual or remote controlled switching, or automatically by a Distribution Restoration Zone Control System.  If during the Demand restoration process, any relevant Restoration Contractor’s Plant or Apparatus cannot keep within its safe operating parameters, because of the nature of the Demand being supplied, the relevant Restoration Contractor shall inform the Network Operator without undue delay who in turn shall inform The Company.  In the case of a Distribution Restoration Zone in Scotland, the Scottish Network Operator shall inform the relevant Scottish Transmission Licensee.

In order to help alleviate issues the Network Operator or Distribution Restoration Zone Control System will, where possible:

- Instruct relevant Restoration Contractors to alter their Demand; or

- re-configure the topology of the Distribution Restoration Zone; or

- will instruct the relevant Restoration Contractor forming part of the Distribution Restoration Zone to re-configure its System.

The Company and Network Operator (and Relevant Transmission Licensee in Scotland) accepts that any decision to keep a relevant Restoration Contractor’s Plant or Apparatus operating, if outside its safe operating parameters, is one for the Restoration Contractor concerned alone.  The Company, the Network Operator, and the Relevant Scottish Transmission Licensee (for Distribution Restoration Zones in Scotland) accepts that the relevant Restoration Contractor’s Plant and Apparatus may have its operating point changed by the relevant Restoration Contractor if it believes it is necessary for safety reasons (whether relating to personnel or Plant and/or Apparatus).  If such a change is made without prior notice, then the relevant Restoration Contractor shall inform the Network Operator as soon as reasonably practical. A Restoration Contractor may also reject an instruction issued by a Network Operator but only on safety grounds (relating to personnel or plant) and this must be notified to Network Operator immediately.

OC9.4.7.8.13	To stabilise the voltage and Frequency of the Network Operator’s System and increase the Demand supplied within the Distribution Restoration Zone, the Network Operator may need to instruct (by manual or automatic means) additional relevant Restoration Contractors to Synchronise their Plant to the Distribution Restoration Zone which would be part of the Distribution Restoration Zone Plan.  The Network Operator and/or the Distribution Restoration Zone Control System shall ensure Restoration Contractors are able (where applicable) to contribute to voltage and Frequency control and ensure that adequate positive and negative headroom is maintained on Restoration Contractor’s Plant and Apparatus to enable the management of Power Island contingences.  For the avoidance of doubt, The Company may require Transmission Licensees in Scotland to manage the Frequency and voltage of Power Islands in Scotland as provided for in STCP 06-1 or Network Operators to manage the Frequency and voltage of Distribution Restoration Zones whilst recognising The Company has overall responsibility to the wider restoration process in the GB Synchronous Area.

OC9.4.7.8.14	As the Distribution Restoration Zone supports increasing Demand, and as implementation of the Distribution Restoration Zone Plan progresses, the Network Operator may need to switch between predefined control and Protection settings as the need arises.

OC9.4.7.8.15	Expansion of a Distribution Restoration Zone to an unenergised Transmission busbar and to wider parts of the unenergised Transmission System could be part of the Distribution Restoration Zone Plan in addition to the requirements of OC9.5.

OC9.4.7.8.16	Operation in accordance with the Distribution Restoration Zone Plan will be terminated by the Network Operator in accordance OC9.4.7.6.3(d).

OC9.4.7.9	Expansion of Power Islands

The Company will instruct relevant Users to expand Power Islands to achieve larger Power Islands following the successful termination of Local Joint Restoration Plans and Distribution Restoration Zone Plans.

OC9.4.7.10	Interconnection of Power Islands

The Company will subsequently interconnect the expanded Power Islands detailed in OC9.4.7.9 to form larger Power Islands which will then be connected to form an integrated system as detailed in OC9.5 which is a fundamental component of the Electricity System Restoration Standard. This should eventually achieve the re-establishment of the Total System or that part of the Total System subject to the Partial Shutdown, as the case may be. The interconnection of Power Islands will utilise the provisions of all or part of OC9.5 (Re-Synchronisation of De-synchronised Power Islands) and in such a situation such provisions will be part of the System Restoration.

OC9.4.7.

Return the Total System Back to Normal Operation

OC9.4.7.11 	The Company shall, as soon as reasonably practical, inform Users and the BSCCo when the Total System could return to normal operation. Any such determination by The Company does not mean that the provisions of Section G paragraph 3 (System Restoration) of the BSC shall cease to apply.

In making the determination that the Total System could return to normal operation, The Company, would consider, amongst other things, the following areas:

(a) 	the extent to which the National Electricity Transmission System is contiguous and energised;

(b) 	the integrity and stability of the National Electricity Transmission System and its ability to operate in accordance with the Licence Standards;

(c) 	the impact that returning to normal may have on transmission constraints and the corresponding ability to maximise the Demand connected; and

(d) 	the volume of generation, Electricity Storage or Demand not connected to the National Electricity Transmission System; and

(e) 	the functionality of normal communication systems (ie electronic data communication facilities, Control Telephony, etc).

In the event that the Balancing Mechanism has been suspended, it will not resume until the start of the Settlement Period determined by the BSC Panel in accordance with paragraph G3.1.2(d)(i) of the BSC.

For the avoidance of doubt, until resumption of the Balancing Mechanism, The Company is likely to continue to issue Emergency Instructions in accordance with BC2.9.

Users shall use reasonable endeavours to submit Physical notifications ten hours prior to the start of the Settlement Period determined by the BSC Panel in accordance with paragraph G3.1.2(d)(i) of the BSC and as notified by The Company to Users, in preparation for a return to normal operations.

- In the event that the Balancing Mechanism has not been suspended and The Company has determined that the Total System has returned to normal operation, The Company shall inform Users and the BSCCo as soon as possible of the time and date at which (in The Company’s determination) the Total System returned to normal operation.

Conclusion of System Restoration

OC9.4.7.12 	The provisions of this OC9 shall cease to apply with effect from either:

(a) 	Where the Balancing Mechanism was suspended, the start of the Settlement Period that the Balancing Mechanism resumed normal operation, as determined by the BSC Panel and notified by the BSCCo in accordance with the provisions of the BSC; or

- (b) 	Where the Balancing Mechanism was not suspended, the end of the Settlement Period determined and notified by the BSCCo (in accordance with the provisions of the BSC) and corresponding to the time and date that The Company determined that the Total System had returned to normal operation.

Externally Interconnected System Operators

- OC9.4.7.13 	Unless an Interconnector has an Anchor Restoration Contract, The Company will, pursuant to the Interconnection Agreement with Externally Interconnected System Operators, agree with Externally Interconnected System Operators when their transmission systems can be Re-Synchronised, if they have become separated.

The objectives of such exercises include:

OC9.5	RE-SYNCHRONISATION OF POWER ISLANDS

The provisions in this OC9.5 do not apply to the parts of the Total System that normally operate Out of Synchronism with the rest of the National Electricity Transmission System.

Further requirements, including the provision of information, applying to Re-synchronisation of a Power Island following any Total Shutdown or Partial Shutdown are detailed in OC9.5.6.

OC9.5.1	(a)	Where parts of the Total System are Out of Synchronism with each other (each such part being termed a Power Island), but where there has been no Total Shutdown or Partial Shutdown, The Company will instruct Users to regulate generation or Demand, as the case may be, to enable the Power Islands to be Re-Synchronised and The Company will inform those Users when Re-Synchronisation has taken place.

(b)	As part of that process, there may be a need to deal specifically with Embedded generation or storage in those Power Islands.  This OC9.5 provides for how such Embedded generation or storage should be dealt with. In Scotland, this OC9.5 also provides for how Transmission connected generation in Power Islands should be dealt with.

(c)	In accordance with the provisions of the BC, The Company may decide that, to enable Re-Synchronisation, it will issue Emergency Instructions in accordance with BC2.9 and it may be necessary to depart from normal Balancing Mechanism operation in accordance with BC2 in issuing Bid-Offer Acceptances.

(d)	The provisions of this OC9.5 shall also apply during System Restoration to the Re-Synchronising of parts of the System following a Total or Partial Shutdown, as indicated in OC9.4.  In such cases, the provisions of OC9.5 shall apply when the relevant Restoration Plan(s) referred to in OC9.4.7.6.3(d) are terminated.

OC9.5.2	Island loading and generation data management

Generation in those Power Islands may be dealt with as described in OC.9.5.2.1 and OC9.5.2.2. The method deployed will vary in relation to any particular incident:-

OC9.5.2.1	Data Submission between Generators and Network Operators via The Company

(a)	In this section, OC9.5.2.1, relevant loading and other operational parameters are exchanged indirectly between Generators and/or HVDC System Owners and DC Converter Station Owners and Network Operators via The Company.

(b)	The Company, each Generator, HVDC Owner and/or DC Converter Station owner with Synchronised (or connected and available to generate although not Synchronised) Genset(s) in the Power Island and the Network Operator whose User System forms all or part of the Power Island shall exchange information as set out in this OC9.5.2.1 to enable The Company to issue a Bid-Offer Acceptance or an Emergency Instruction to that Generator and/or HVDC System Owner and/or DC Converter Station Owner in relation to its Genset(s) in the Power Island until Re-Synchronisation takes place, on the basis that it will (where practicable) seek to maintain the Target Frequency.

(c)	The information to The Company from the Generator and/or HVDC System Owner and/or DC Converter Station owner will cover its relevant operational parameters as outlined in the Balancing Codes (BC) and from The Company to the Generator and/or HVDC System Owner and/or DC Converter Station owner will cover data on Demand and changes in Demand in the Power Island.

(d)	The information from the Network Operator to The Company will comprise data on Demand in the Power Island, including data on any constraints within the Power Island.

(e)	The Company will keep the Network Operator informed of the Bid-Offer Acceptances or Emergency Instructions it is issuing to Embedded Genset(s) within the Network Operator’s User System forming part of the Power Island.

OC9.5.2.2	Direct Data Submission between Generators, HVDC System Owners, DC Converter Station Owners and Network Operators

(a)	In this section, OC9.5.2.2, relevant loading and other operational parameters are exchanged directly between Generators, and/or HVDC System Owners and DC Converter Station Owners and Network Operators.

(b)	The Company will issue an Emergency Instruction and/or a Bid-Offer Acceptance, to the Generator and/or HVDC System Owner and/or DC Converter Station Owner to "float" local Demand and maintain Frequency at Target Frequency.  In this situation, the Generator and/or HVDC System Owner and/or DC Converter Station owner will be required to regulate the output of its Genset(s) at the Power Station in question to the Demand prevailing in the Power Island in which it is situated, until Re-Synchronisation takes place, on the basis that it will (where practicable) seek to maintain the Target Frequency.

(c)	The Network Operator is required to be in contact with the Generator and/or HVDC System Operator and/or DC Converter Station owner so that the Network Operator can supply data to the Generator and/or HVDC System Owner and/or DC Converter Station owner on Demand changes within the Power Island.

(d)	If more than one Generating Unit and/or HVDC System and/or DC Converter  is Synchronised to the Power Island, or is connected to the Power Island and available to generate although not Synchronised, the Network Operator will need to liaise with The Company to agree which Generating Units and/or HVDC Systems and/or DC Converter stations will be utilised to accommodate changes in Demand in the Power Island. The Network Operator will then maintain contact with the relevant Generator(s) and/or HVDC System Owner(s) and/or DC Converter Station Owner(s) in relation to that Plant.

(e)	The Generator at the Power Station and/or HVDC System Owner and/or DC Converter Station owner must contact the Network Operator if the level of Demand which it has been asked to meet as a result of the Emergency Instruction and/or Bid-Offer Acceptance to "float" and the detail on Demand passed on by the Network Operator, is likely to cause problems for safety reasons (whether relating to personnel or Plant and/or Apparatus) in the operation of its Generating Unit(s) or HVDC System(s) or DC Converter Station(s), in order that the Network Operator can alter the level of Demand which that Generator and/or HVDC System Owner and/or DC Converter Station owner needs to meet. Any decision to operate outside any relevant parameters is one entirely for the Generator and/or HVDC System Owner and/or DC Converter Station owner.

OC9.5.2.3	Control Features

(a)	A system may be established in relation to a part of the National Electricity Transmission System and a Network Operator’s User System, if agreed between The Company and the Network Operator and any relevant Generator(s), HVDC System Owner or DC Converter Station Owner, whereby upon a defined fault(s) occurring, manual or automatic control features will operate to protect the National Electricity Transmission System and relevant Network Operator’s User System and  Generator(s), HVDC System Owner(s) or DC Converter Station Owner(s) Plant and simplify the restoration of Demand in the Power Island.

(b)	In agreeing the establishment of such a system of control features, The Company will need to consider its impact on the operation of the National Electricity Transmission System.

(c)	The Company will work with Network Operators involved in the wider System Restoration process to help balance generation and Demand, and help ensure that it does not have a destabilising effect on the Total System.

OC9.5.2.4	Absence of Control Features System

If a system of control features under OC9.5.2.3 has not been agreed as part of an OC9 De-Synchronised Island Procedure under OC9.5.4 below, The Company may choose to utilise the procedures set out in OC9.5.2.1 or OC9.5.2.2, or may instruct the Generators or HVDC System Owner or DC Converter Station owners (or some of them in respect of the Plant they own or operate) in the Power Island to De-Synchronise.

OC9.5.3	Choice of Option

In relation to each of the methods set out in OC9.5.2, where a Power Island has come into existence and where an OC9 De-Synchronised Island Procedure under OC9.5.4 has been agreed, The Company, the Network Operator and the relevant Generator(s), HVDC System Owners or DC Converter Station owners will operate in accordance with that OC9 De-Synchronised Island Procedure unless The Company considers that the nature of the De-Synchronised Island situation is such that either:-

(i)	the OC9 De-Synchronised Island Procedure does not cover the situation; or

(ii)	the provisions of the OC9 De-Synchronised Island Procedure are not appropriate,

in which case The Company will instruct the relevant Users and the Users will comply with The Company's instructions (which in the case of Generators and/or HVDC System Owners and/or DC Converter Station owners will relate to Active Power supplied to the Power Island and in the case of Network Operators will relate to Demand).

OC9.5.4	Agreeing Procedures

In relation to each relevant part of the Total System, The Company, the Network Operator and the relevant Generator and/or HVDC System Owner and/or DC Converter Station owner will discuss and may agree a local procedure (an "OC9 De-Synchronised Island Procedure").

Where the need for an OC9 De-Synchronised Island Procedure arises for the first time, the following provisions shall apply:

(a)	The Company, the Network Operator(s) and the relevant Generator(s) and/or HVDC System Owners or DC Converter Station owners will discuss the need for, and the detail of, the OC9 De-Synchronised Island Procedure.  As soon as the need for an OC9 De-Synchronised Island Procedure is identified by The Company or a User, and the party which identifies such a need will notify all affected Users (and The Company, if that party is a User), and The Company will initiate these discussions.

(b)	Each OC9 De-Synchronised Island Procedure will be in relation to a specific Grid Supply Point, but if there is more than one Grid Supply Point involved, then the OC9 De-Synchronised Island Procedure may cover all relevant Grid Supply Points. In Scotland, the OC9 De-Synchronised Island Procedure may also cover parts of the National Electricity Transmission System connected to the User’s System(s) and Power Stations and HVDC Systems and DC Converter Station owners directly connected to the National Electricity Transmission System which are also likely to form part of the Power Island.

(c)	The OC9 De-Synchronised Island Procedure will:

(i)	record which Users and which User Sites are covered by the OC9 De-Synchronised Island Procedure;

(ii)	record which of the methods set out in OC9.5 shall apply, with any conditions as to applicability being set out as well;

(iii)	set out what is required from The Company and each User should a Power Island arise;

(iv)	set out what action should be taken if the OC9 De-Synchronised Island Procedure does not cover a particular set of circumstances and will reflect that in the absence of any specified action, the provisions of OC9.5.3 will apply;

(v)	in respect of Scottish Transmission Systems, the OC9 De-Synchronised Island procedure may be produced with and include obligations on the Relevant Scottish Transmission Licensee(s); and

(vi)	in respect of Scottish Transmission Systems, where the OC9 De-Synchronised Island Procedure includes the establishment of a Power Island, describe the route for establishment of the Power Island.

(d)	Each OC9 De-Synchronised Island Procedure shall be prepared by The Company to reflect the above discussions.

(e)	Each page of the OC9 De-Synchronised Island Procedure shall bear a date of issue and the issue number.

(f)	When an OC9 De-Synchronised Island Procedure is prepared, it shall be sent by The Company to the Users involved for confirmation of its accuracy.

(g)	The OC9 De-Synchronised Island Procedure shall then be signed on behalf of The Company and on behalf of each relevant User by way of written confirmation of its accuracy.

(h)	Once agreed under this OC9.5.4, the procedure will become an OC9 De-Synchronised Island Procedure under the Grid Code and (subject to any change pursuant to this OC9) will apply between The Company, Relevant Transmission Licensee and the relevant Users as if it were part of the Grid Code.

(i)	Once signed, a copy will be distributed by The Company to each User which is a party accompanied by a note indicating the issue number and the date of implementation.

(j)	The Company and Users must make the OC9 De-Synchronised Island Procedure readily available to the relevant operational staff.

(k)	If a new User connects to the Total System and needs to be included with an existing OC9 De-Synchronised Island Procedure, The Company will initiate a discussion with that User and the Users which are parties to the relevant OC9 De-Synchronised Island Procedure.  The principles applying to a new OC9 De-Synchronised Island Procedure under this OC9.5.4 shall apply to such discussions and to any consequent changes.

(l)	If The Company, or any User which is a party to an OC9 De-Synchronised Island Procedure, becomes aware that a change is needed to that OC9 De-Synchronised Island Procedure, it shall (in the case of The Company) initiate a discussion between The Company and the relevant Users to seek to agree the relevant change.  The principles applying to establishing a new OC9 De-Synchronised Island Procedure under this OC9.5.4 shall apply to such discussions and to any consequent changes.  If a User becomes so aware, it shall contact The Company who will then initiate such discussions.

(m)	If in relation to any discussions, agreement cannot be reached between The Company and the relevant Users, The Company will operate the System on the basis that it will discuss which of the methods set out in OC9.5.2.1 or OC9.5.2.2 would be most appropriate at the time, if practicable.  The complexities and uncertainties of recovery from a

Power Island means that The Company will decide, having discussed the situation with the relevant Users and taking into account the fact that the three methods may not cover the situation or be appropriate, the approach which is to be followed.  The Company will instruct the relevant Users and the Users will comply with The Company's instructions as provided in OC9.5.3.

OC9.5.5	Where the National Electricity Transmission System is Out of Synchronism with the Transmission System of an Externally Interconnected System Operator, The Company will, pursuant to the Interconnection Agreement with that Externally Interconnected System Operator, agree with that Externally Interconnected System Operator when its Transmission System can be Re-Synchronised to the National Electricity Transmission System.

OC9.5.6	Further requirements regarding Re-synchronisation of De-synchronised Islands following any Total Shutdown or Partial Shutdown

Following any Total Shutdown or Partial Shutdown, The Company expects that it will be necessary to interconnect Power Islands utilising the provisions of OC9.5.  The complexities and uncertainties of recovery from a Total Shutdown or Partial Shutdown requires the provisions of OC9.5 to be flexible, however, the strategies which The Company will, where practicable, be seeking to follow when Re-synchronising Power Islands following any Total Shutdown or Partial Shutdown, include the following:

- the provision of supplies to appropriate Power Stations to facilitate their synchronisation as soon as practicable;

(b)	energisation of a skeletal National Electricity Transmission System;

(c)	the strategic restoration of Demand in co-ordination with relevant Network Operators.

As highlighted in OC9.4.3, during a Total Shutdown or Partial Shutdown and during the subsequent recovery, which includes any period during which the procedures in this OC9.5 apply, the Licence Standards may not apply and the Total System may be operated outside normal voltage and Frequency standards.

OC9.5.7	To manage effectively and co-ordinate the restoration strategies of the Total System (any Re-Synchronisation of Power Islands) following any Total Shutdown or Partial Shutdown, requires The Company and relevant Users to undertake certain planning activities as set out below:

(a)	The Company and Network Operators shall review on a regular basis the processes by which each Power Island will be interconnected.  This is likely to cover an exchange of information regarding the typical size, location and timing requirements for Demand to be reconnected and also include details (ability to change/disable) of the low frequency trip relay settings of the Demand identified.

(b)	Each Generator shall provide to The Company information to assist The Company in the formulation of the restoration strategies of Power Island expansion.  This information shall be provided in accordance with PC.A.5.7.

OC9.6	JOINT SYSTEM INCIDENT PROCEDURE

OC9.6.1	A "Joint System Incident" is

(a)	an Event, wherever occurring (other than on an Embedded Small Power Station or Embedded Medium Power Station), which, in the opinion of The Company or a User, has or may have a serious and/or widespread effect.

(b)	In the case of an Event on a User(s) System(s) (other than on an Embedded Small Power Station or Embedded Medium Power Station), the effect must be on the National Electricity Transmission System, and in the case of an Event on the National Electricity Transmission System, the effect must be on a User(s) System(s) (other than on an Embedded Small Power Station or Embedded Medium Power Station).

Where an Event on a User(s) System(s) has or may have no effect on the National Electricity Transmission System, then such an Event does not fall within OC9 and accordingly OC9 shall not apply to it.

OC9.6.2	(a)	(i)	Each User (other than Generators which only have Embedded Small Power Stations and/or Embedded Medium Power Stations) will provide in writing to The Company, and

(ii)	The Company will provide in writing to each User (other than Generators which only have Embedded Small Power Stations and/or Embedded Medium Power Stations), a telephone number or numbers at which, or through which, senior management representatives nominated for this purpose and who are fully authorised to make binding decisions on behalf of The Company or the relevant User, as the case may be, can be contacted day or night when there is a Joint System Incident.

(b)	The lists of telephone numbers will be provided in accordance with the timing requirements of the Bilateral Agreement and/or Construction Agreement with that User, prior to the time that a User connects to the National Electricity Transmission System and must be up-dated (in writing) as often as the information contained in them changes.

OC9.6.3	Following notification of an Event under OC7, The Company or a User, as the case may be, will, if it considers necessary, telephone the User or The Company, as the case may be, on the telephone number referred to in OC9.6.2, to obtain such additional information as it requires.

OC9.6.4	Following notification of an Event under OC7, and/or the receipt of any additional information requested pursuant to OC9.6.3, The Company or a User, as the case may be, will determine whether or not the Event is a Joint System Incident, and, if so, The Company and/or the User may set up an Incident Centre in order to avoid overloading the existing, operational/control arrangements be they The Company’s or User’s.

OC9.6.5	Where The Company has determined that an Event is a Joint System Incident, The Company shall, as soon as possible, notify all relevant Users that a Joint System Incident has occurred and, if appropriate, that it has established an Incident Centre and the telephone number(s) of its Incident Centre if different from those already supplied pursuant to OC9.6.2.

OC9.6.6	If a User establishes an Incident Centre it shall, as soon as possible, notify The Company that it has been established and the telephone number(s) of the Incident Centre if different from those already supplied pursuant to OC9.6.2.

OC9.6.7	The Company's Incident Centre and/or the User's Incident Centre will not assume any responsibility for the operation of the National Electricity Transmission System or User's System, as the case may be, but will be the focal point in The Company or the User, as the case may be, for:

(a)	the communication and dissemination of information between The Company and the senior management representatives of User(s); or

(b)	between the User and the senior management representatives of The Company, as the case may be,

relating to the Joint System Incident.  The term "Incident Centre" does not imply a specially built centre for dealing with Joint System Incidents, but is a communications focal point.  During a Joint System Incident, the normal communication channels, for operational/control communication between The Company and Users will continue to be used.

OC9.6.8	All communications between the senior management representatives of the relevant parties with regard to The Company's role in the Joint System Incident shall be made via The Company's Incident Centre if it has been established.

OC9.6.9	All communications between the senior management representatives of The Company and a User with regard to that User's role in the Joint System Incident shall be made via that User's Incident Centre if it has been established.

OC9.6.10	The Company will decide when conditions no longer justify the need to use its Incident Centre and will inform all relevant Users of this decision.

OC9.6.11	Each User which has established an Incident Centre will decide when conditions no longer justify the need to use that Incident Centre and will inform The Company of this decision.

APPENDIX 1 – SYSTEM RESTORATION REGIONS

< END OF OPERATING CODE NO. 9 >