BALANCING CODE NO. 1

(BC1)

PRE GATE CLOSURE PROCESS

CONTENTS

(This contents page does not form part of the Grid Code)

Paragraph No/Title	Page Number

BC1.1   INTRODUCTION	3

BC1.2   OBJECTIVE	3

BC1.3   SCOPE	3

BC1.4   SUBMISSION OF DATA	3

BC1.4.1   Communication With Users	4

BC1.4.2   Day Ahead Submissions	4

BC1.4.3   Data Revisions………………………………………………………………………………….	8

BC1.4.4   Receipt Of BM Unit Data Prior To Gate Closure	8

BC1.4.5   BM Unit Defaulting, Validity And Consistency Checking	7

BC1.4.6   Special Provisions Relating To Interconnector Users	7

BC1.5   INFORMATION PROVIDED BY THE COMPANY	9

BC1.5.1   Demand Estimates	9

BC1.5.2   Indicated Margin And Indicated Imbalance	10

BC1.5.3   Provision Of Updated Information	10

BC1.5.4   Reserve And Inadequate System Margin	10

BC1.5.5   System And Localised NRAPM (Negative Reserve Active Power Margin)	11

BC1.6   SPECIAL PROVISIONS RELATING TO NETWORK OPERATORS	12

BC1.6.1   User System Data From Network Operators	12

BC1.6.2   Notification Times To Network Operators	14

BC1.7   SPECIAL ACTIONS	14

BC1.8   PROVISION OF REACTIVE POWER CAPABILITY	14

APPENDIX 1 - BM UNIT DATA	16

BC1.A.1.1   Physical Notifications	16

BC1.A.1.2    Not Used	16

BC1.A.1.3   Export And Import Limits	16

BC1.A.1.4   Bid Offer Data	17

BC1.A.1.5   Dynamic Parameters	18

BC1.A.1.6   CCGT Module Matrix	18

BC1.A.1.7   Cascade Hydro Scheme Matrix	20

BC1.A.1.8   Power Park Module Availability Matrix	20

BC1.A.1.6   CCGT Module Matrix	21

APPENDIX 2 - DATA TO BE MADE AVAILABLE BY THE COMPANY	24

BC1.A.2.1   Initial Day Ahead Demand Forecast	24

BC1.A.2.2   Initial Day Ahead Market Information	24

BC1.A.2.3   Current Day & Day Ahead Updated Market Information	24

BC1.1	INTRODUCTION

Balancing Code No1 (BC1) sets out the procedure for:

(a)	the submission of BM Unit Data and/or Generating Unit Data (which could be part of a Power Generating Module) by each BM Participant;

(b)	the submission of certain System data by each Network Operator; and

(c)	the provision of data by The Company,

in the period leading up to Gate Closure.

BC1.2	OBJECTIVE

The procedure for the submission of BM Unit Data and/or Generating Unit Data is intended to enable The Company to assess which BM Units and Generating Units (which could be part of a Power Generating Module) are expected to be operating in order that The Company can ensure (so far as possible) the integrity of the National Electricity Transmission System, and the security and quality of supply.

Where reference is made in this BC1 to Generating Units and/or Power Generating Modules (unless otherwise stated) it only applies:

(a)	to each Generating Unit which forms part of the BM Unit of a Cascade Hydro Scheme; and

(b)	at an Embedded Exemptable Large Power Station where the relevant Bilateral Agreement specifies that compliance with BC1 is required:

(i)	to each Generating Unit which could be part of a Synchronous Power Generating Module, or

(ii)	to each Power Park Module where the Power Station comprises Power Park Modules.

Generators in respect of Embedded Large Power Stations where Purchase Contracts or a Substantial Modification in respect of its Main Plant and Apparatus had been concluded on or after 1st June 2027, and which applied for a Connection Agreement on or after XXXXXX [XXXXXX this being the Implementation Date,  which is ten working days after the Authority Decision date] shall be required to submit BM Unit Data and not Generating Unit Data as provided for in BC1.2(a) or BC1.2(b).

BC1.3	SCOPE

BC1 applies to The Company and to Users, which in this BC1 means:-

(a)	BM Participants;

(b)	Externally Interconnected System Operators; and

(c)	Network Operators.

BC1.4	SUBMISSION OF DATA

In the case of Additional BM Units or Secondary BM Units any data submitted by Users under this BC1 must represent the value of the data at the relevant GSP Group.

In the case of all other BM Units or Generating Units Embedded in a User System, any data submitted by Users under this BC1 must represent the value of the data at the relevant Grid Supply Point.

BC1.4.1	Communication With Users

(a)	Submission of BM Unit Data and Generating Unit Data by Users to The Company specified in BC1.4.2 to BC1.4.4 (with the exception of BC1.4.2(f)) is to be by use of electronic data communications facilities, as provided for in CC.6.5.8 or ECC.6.5.8 (as applicable). However, data specified in BC1.4.2(c) and BC1.4.2(e) only, may be submitted by telephone or fax.

(b)	In the event of a failure of the electronic data communication facilities, the data to apply in relation to a pre-Gate Closure period will be determined in accordance with the Data Validation, Consistency and Defaulting Rules, based on the most recent data received and acknowledged by The Company.

(c)	Planned Maintenance Outages will normally be arranged to take place during periods of low data transfer activity.

(d)	Upon any Planned Maintenance Outage, or following an unplanned outage described in BC1.4.1(b) (where it is termed a "failure") in relation to a pre-Gate Closure period:

(i)	BM Participants should continue to act in relation to any period of time in accordance with the Physical Notifications current at the time of the start of the Planned Maintenance Outage or the computer system failure in relation to each such period of time subject to the provisions of BC2.5.1. Depending on when in relation to Gate Closure the planned or unplanned maintenance outage arises such operation will either be operation in preparation for the relevant output in real time, or will be operation in real time. No further submissions of BM Unit Data and/or Generating Unit Data (other than data specified in BC1.4.2(c) and BC1.4.2(e)) should be attempted. Plant failure or similar problems causing significant deviation from Physical Notification should be notified to The Company by the submission of a revision to Export and Import Limits in relation to the BM Unit and /or Generating Unit so affected;

(ii)	during the outage, revisions to the data specified in BC1.4.2(c) and BC1.4.2(e) may be submitted. Communication between Users Control Points and The Company during the outage will be conducted by telephone; and

(iii)	no data will be transferred from The Company to the BMRA until the communication facilities are re-established.

BC1.4.2	Day Ahead Submissions

Data for any Operational Day may be submitted to The Company up to several days in advance of the day to which it applies, as provided in the Data Validation, Consistency and Defaulting Rules. However, Interconnector Users must submit Physical Notifications, and any associated data as necessary, each day by 11:00 hours in respect of the next following Operational Day in order that the information used in relation to the capability of the respective External Interconnection is expressly provided. The Company shall not by the inclusion of this provision be prevented from utilising the provisions of BC1.4.5 if necessary.

The data may be modified by further data submissions at any time prior to Gate Closure, in accordance with the other provisions of BC1. The data to be used by The Company for operational planning will be determined from the most recent data that has been received by The Company by 11:00 hours on the day before the Operational Day to which the data applies, or from the data that has been defaulted at 11:00 hours on that day in accordance with BC1.4.5. Any subsequent revisions received by The Company under the Grid Code will also be utilised by The Company. In the case of all data items listed below, with the exception of item (e), Dynamic Parameters (Day Ahead), the latest submitted or defaulted data, as modified by any subsequent revisions, will be carried forward into operational timescales. The individual data items are listed below:

(a)	Physical Notifications

Physical Notifications, being the data listed in BC1 Appendix 1 under that heading, are required by The Company at 11:00 hours each day for each Settlement Period of the next following Operational Day, in respect of;

(1)	BM Units:

(i)	with a Demand Capacity with a magnitude of 50MW or more in NGET’s Transmission Area or 10MW or more in SHETL’s Transmission Area or 30MW or more in SPT’s Transmission Area; or

(ii)	comprising Generating Units (as defined in the Glossary and Definitions and not limited by BC1.2) and/or Power Generating Modules and/or CCGT Modules and/or Power Park Modules in each case at Large Power Stations, Medium Power Stations and Small Power Stations where such Small Power Stations are directly connected to the Transmission System; or

(iii)	where the BM Participant chooses to submit Bid-Offer Data in accordance with BC1.4.2(d) for BM Units not falling within (i) or (ii) above,

and

(2)	each Generating Unit where applicable under BC1.2.

Physical Notifications may be submitted to The Company by BM Participants, for the BM Units, and Generating Units, specified in this BC1.4.2(a) at an earlier time, or BM Participants may rely upon the provisions of BC1.4.5 to create the Physical Notifications by data defaulting pursuant to the Grid Code utilising the rules referred to in that paragraph at 11:00 hours in any day.

Physical Notifications (which must comply with the limits on maximum rates of change listed in BC1 Appendix 1) must, subject to the following operating limits, represent the User’s best estimate of expected input or output of Active Power, except where a BM Unit is affected by a Stage 2 or higher Network Gas Supply Emergency load shedding event.  Physical Notifications shall be prepared in accordance with Good Industry Practice. Physical Notifications for any BM Unit, and any Generating Units, should normally be consistent with the Dynamic Parameters and Export and Import Limits and must not reflect any BM Unit or any Generating Units, proposing to operate outside the limits of its Demand Capacity and (and in the case of BM Units) Generation Capacity and, in the case of a BM Unit comprising a Generating Unit (as defined in the Glossary and Definitions and not limited by BC1.2) and/or Power Generating Module and/or CCGT Module and/or Power Park Module, its Registered Capacity.

These Physical Notifications provide, amongst other things, indicative Synchronising and De-Synchronising times to The Company in respect of any BM Unit comprising a Generating Unit (as defined in the Glossary and Definitions and not limited by BC1.2) and/or Power Generating Module and/or CCGT Module and/or Power Park Module, and for any Generating Units, and provide an indication of significant Demand changes in respect of other BM Units.

In the case where a BM Unit is affected by a Network Gas Supply Emergency load shedding event, once Stage 2 or higher has been declared, then their Physical Notifications shall represent the User's best estimate of the contracted power position of the affected BM Unit at the time of the event, taking into account any mitigating actions to reduce the difference between the contracted power position and the volume to be shed.

(b)	 Not Used.

(c)	Export and Import Limits

Each BM Participant may, in respect of each of its BM Units and its Generating Units submit to The Company for any part or for the whole of the next following Operational Day the data listed in BC1 Appendix 1 under the heading of “Export and Import Limits” to amend the data already held by The Company in relation to Export and Import Limits, which would otherwise apply for those Settlement Periods.

Export and Import Limits respectively represent the maximum export to or import from the National Electricity Transmission System for a BM Unit and a Generating Unit and are the maximum levels that the BM Participant wishes to make available and must be prepared in accordance with Good Industry Practice.

(d)	Bid-Offer Data

Each BM Participant may, in respect of each of its BM Units, but must not in respect of its Generating Units submit to The Company for any Settlement Period of the next following Operational Day the data listed in BC1 Appendix 1 under the heading of “Bid-Offer Data” to amend the data already held by The Company in relation to Bid-Offer Data, which would otherwise apply to those Settlement Periods.  The submitted Bid-Offer Data will be utilised by The Company in the preparation and analysis of its operational plans for the next following Operational Day. Bid-Offer Data may not be submitted unless an automatic logging device has been installed at the Control Point for the BM Unit in accordance with CC.6.5.8(b) or ECC.6.5.8(b) (as applicable).

(e)	Dynamic Parameters (Day Ahead)

Each BM Participant may, in respect of each of its BM Units, but must not in respect of its Generating Units submit to The Company for the next following Operational Day the data listed in BC1 Appendix 1 under the heading of “Dynamic Parameters” to amend that data already held by The Company.

These Dynamic Parameters shall reasonably reflect the expected true operating characteristics of the BM Unit and shall be prepared in accordance with Good Industry Practice.

The Dynamic Parameters applicable to the next following Operational Day will be utilised by The Company in the preparation and analysis of its operational plans for the next following Operational Day and may be used to instruct certain Ancillary Services. For the avoidance of doubt, the Dynamic Parameters to be used in the current Operational Day  will be those submitted in accordance with BC2.5.3.1.

(f)	Other Relevant Data

By 11:00 hours each day, each BM Participant, in respect of each of its BM Units and Generating Units for which Physical Notifications are being submitted, shall, if it has not already done so, submit to The Company (save in respect of item (vi) and (vii) where the item shall be submitted only when reasonably required by The Company), in respect of the next following Operational Day the following:

(i)	in the case of a CCGT Module and/or a Synchronous Power Generating Module, a CCGT Module Matrix and/or a Synchronous Power Generating Module Matrix as described in BC1 Appendix 1;

(ii)	details of any special factors which in the reasonable opinion of the BM Participant may have a material effect or present an enhanced risk of a material effect on the likely output (or consumption) of such BM Unit(s). Such factors may include risks, or potential interruptions, to BM Unit fuel supplies, or developing plant problems, details of tripping tests, etc. This information will normally only be used to assist in determining the appropriate level of Operating Margin that is required under OC2.4.6;

(iii)	in the case of Generators, any temporary changes, and their possible duration, to the Registered Data of such BM Unit;

(iv)	in the case of Suppliers, details of Customer Demand Management taken into account in the preparation of its BM Unit Data;

(v)	details of any other factors which The Company may take account of when issuing Bid-Offer Acceptances for a BM Unit (e.g., Synchronising or De-Synchronising Intervals);

(vi)	in the case of a Cascade Hydro Scheme, the Cascade Hydro Scheme Matrix as described in BC1 Appendix 1;

(vii)	in the case of a Power Park Module, a Power Park Module Availability Matrix as described in BC1 Appendix 1;

(viii) in the case of an Additional BM Unit or a Secondary BM Unit an Aggregator Impact Matrix as described in BC1 Appendix 1.

BC1.4.3	Data Revisions

The BM Unit Data, and Generating Unit Data, derived at 1100 hours each day under BC1.4.2 above may need to be revised by the BM Participant for a number of reasons, including for example, changes to expected output or input arising from revised contractual positions, plant breakdowns, changes to expected Synchronising or De-Synchronising times, etc, occurring before Gate Closure. BM Participants should use reasonable endeavours to ensure that the data held by The Company in relation to its BM Units and Generating Units, is accurate at all times. Revisions to BM Unit Data, and Generating Unit Data for any period of time up to Gate Closure should be submitted to The Company as soon as reasonably practicable after a change becomes apparent to the BM Participant. The Company will use reasonable endeavours to utilise the most recent data received from Users, subject to the application of the provisions of BC1.4.5, for its preparation and analysis of operational plans.

BC1.4.4	Receipt of BM Unit Data Prior To Gate Closure

BM Participants submitting Bid-Offer Data, in respect of any BM Unit for use in the Balancing Mechanism for any particular Settlement Period in accordance with the BSC, must ensure that Physical Notifications and Bid-Offer Data for such BM Units are received in their entirety and logged into The Company’s computer systems by the time of Gate Closure for that Settlement Period. In all cases the data received will be subject to the application under the Grid Code of the provisions of BC1.4.5.

For the avoidance of doubt, no changes to the Physical Notification or Bid-Offer Data for any Settlement Period may be submitted to The Company after Gate Closure for that Settlement Period.

BC1.4.5	BM Unit Data Defaulting, Validity And Consistency Checking

In the event that no submission of any or all of the BM Unit Data and Generating Unit Data in accordance with BC1.4.2 in respect of an Operational Day, is received by The Company by 11:00 hours on the day before that Operational Day, The Company will apply the Data Validation, Consistency and Defaulting Rules, with the default rules applicable to Physical Notifications and Export and Import Limits data selected as follows:

(a)	for an Interconnector Users BM Unit, the defaulting rules will set some or all of the data for that Operational Day to zero, unless the relevant Interconnector arrangements, as agreed with The Company, state otherwise (in which case (b) applies); and

(b)	for all other BM Units or Generating Units, the defaulting rules will set some or all of the data for that Operational Day to the values prevailing in the current Operational Day.

A subsequent submission by a User of a data item which has been so defaulted under the Grid Code will operate as an amendment to that defaulted data and thereby replace it. Any such subsequent submission is itself subject to the application under the Grid Code of the Data Validation, Consistency and Defaulting Rules.

BM Unit Data and Generating Unit Data submitted in accordance with the provisions of BC1.4.2 to BC1.4.4 will be checked under the Grid Code for validity and consistency in accordance with the Data Validation, Consistency and Defaulting Rules. If any BM Unit Data and Generating Unit Data so submitted fails the data validity and consistency checking, this will result in the rejection of all data submitted for that BM Unit or Generating Unit included in the electronic data file containing that data item and that BM Unit’s or Generating Unit’s data items will be defaulted under the Grid Code in accordance with the Data Validation, Consistency and Defaulting Rules. Data for other BM Units and Generating Units included in the same electronic data file will not be affected by such rejection and will continue to be validated and checked for consistency prior to acceptance. In the event that rejection of any BM Unit Data and Generating Unit Data occurs, details will be made available to the relevant BM Participant via the electronic data communication facilities.  In the event of a difference between the BM Unit Data for the Cascade Hydro Scheme and sum of the data submitted for the Generating Units forming part of such Cascade Hydro Scheme, the BM Unit Data shall take precedence.

BC1.4.6	Special Provisions Relating To Interconnector Users

(a)	The total of the relevant Physical Notifications submitted by Interconnector Users in respect of any period of time should not exceed the capability (in MW) of the respective External Interconnection for that period of time. In the event that it does, then The Company shall advise the Externally Interconnected System Operator accordingly. In the period between such advice and Gate Closure, one or more of the relevant Interconnector Users would be expected to submit revised Physical Notifications to The Company to eliminate any such over-provision.

(b)	In any case where, as a result of a reduction in the capability (in MW) of the External Interconnection in any period during an Operational Day which is agreed between The Company and an Externally Interconnected System Operator after 0900 hours on the day before the beginning of such Operational Day, the total of the Physical Notifications in the relevant period using that External Interconnection, as stated in the BM Unit Data exceeds the reduced capability (in MW) of the respective External Interconnection in that period then The Company shall notify the Externally Interconnected System Operator accordingly.

BC1.5	INFORMATION PROVIDED BY THE COMPANY

The Company shall provide data to the Balancing Mechanism Reporting Agent or BSCCo each day in accordance with the requirements of the BSC in order that the data may be made available to Users via the Balancing Mechanism Reporting Service (or by such other means) in each case as provided in the BSC. Where The Company provides such information associated with the secure operation of the System to the Balancing Mechanism Reporting Agent, the provision of that information is additionally provided for in the following sections of this BC1.5. The Company shall be taken to have fulfilled its obligations to provide data under BC1.5.1, BC1.5.2, and BC1.5.3 by so providing such data to the Balancing Mechanism Reporting Agent.

BC1.5.1	Demand Estimates

Normally by 0900 hours each day, The Company will make available to Users a forecast of National Demand and the Demand for a number of pre-determined constraint groups (which may be updated from time to time, as agreed between The Company and BSCCo) for each Settlement Period of the next following Operational Day. Normally by 1200 hours each day, The Company will make available to Users a forecast of National Electricity Transmission System Demand for each Settlement Period of the next Operational Day. Further details are provided in Appendix 2.

BC1.5.2	Indicated Margin And Indicated Imbalance

Normally by 1200 hours each day, The Company will make available to Users an Indicated Margin and an Indicated Imbalance for each Settlement Period of the next following Operational Day. The Company will use reasonable endeavours to utilise the most recent data received from Users in preparing for this release of data. Further details are provided in Appendix 2.

BC1.5.3	Provision Of Updated Information

The Company will provide updated information on Demand and other information at various times throughout each day, as detailed in Appendix 2. The Company will use reasonable endeavours to utilise the most recent data received from Users in preparing for this release of data.

BC1.5.4	Reserve And System Margin

Contingency Reserve

(a)	The amount of Contingency Reserve required at the day ahead stage and in subsequent timescales will be decided by The Company on the basis of historical trends in the reduction in availability of Large Power Stations and increases in forecast Demand up to real time operation.  Where Contingency Reserve is to be allocated to thermal Gensets, The Company will instruct through a combination of Ancillary Services instructions and Bid-Offer Acceptances, the time at which such Gensets are required to synchronise, such instructions to be consistent with Dynamic Parameters and other contractual arrangements.

Operating Reserve

(b)	The amount of Operating Reserve required at any time will be determined by The Company having regard to the Demand levels, Large Power Station availability shortfalls and the greater of the largest secured loss of generation (ie, the loss of generation against which, as a requirement of the Licence Standards, the National Electricity Transmission System must be secured) or loss of import from or sudden export to External Interconnections. The Company will allocate Operating Reserve to the appropriate BM Units and Generating Units so as to fulfil its requirements according to the Ancillary Services available to it and as provided in the BC.

System Margin

(c)	In the period following 1200 hours each day and in relation to the following Operational Day, The Company will monitor the total of the Maximum Export Limit component of the Export and Import Limits received against forecast National Electricity Transmission System Demand and the Operating Margin and will take account of Dynamic Parameters to see whether the anticipated level of the System Margin for any period is insufficient.

(d)	Where the level of the System Margin for any period is, in The Company's reasonable opinion, anticipated to be insufficient, The Company will send (by such data transmission facilities as have been agreed) a National Electricity Transmission System Warning - Electricity Margin Notice in accordance with OC7.4.8 to each Generator, Supplier, Externally Interconnected System Operator, Network Operator and Non-Embedded Customer.

(e) 	Where, in The Company’s judgement the System Margin at any time during the current Operational Day is such that there is a high risk of Demand reduction being instructed, a National Electricity Transmission System Warning - High Risk of Demand Reduction will be issued, in accordance with OC7.4.8.

(f)	The monitoring will be conducted on a regular basis and a revised National Electricity Transmission System Warning - Electricity Margin Notice or High Risk of Demand Reduction may be sent out from time to time, including within the post Gate Closure phase. This will reflect any changes in Physical Notifications and Export and Import Limits which have been notified to The Company, and will reflect any Demand Control which has also been so notified. This will also reflect generally any changes in the forecast Demand and the relevant Operating Margin.

(g)	To reflect changing conditions, a National Electricity Transmission System Warning - Electricity Margin Notice may be superseded by a National Electricity Transmission System Warning - High Risk of Demand Reduction and vice-versa.

(h)	If the continuing monitoring identifies that the System Margin is anticipated, in The Company's reasonable opinion, to be sufficient for the period for which previously a National Electricity Transmission System Warning had been issued, The Company will send (by such data transmission facilities as have been agreed) a Cancellation of National Electricity Transmission System Warning to each User who had received a National Electricity Transmission System Warning - Electricity Margin Notice or High Risk of Demand Reduction for that period. The issue of a Cancellation of National Electricity Transmission System Warning is not an assurance by The Company that in the event, the System Margin will be adequate, but reflects The Company's reasonable opinion that the insufficiency is no longer anticipated.

(i)	If continued monitoring indicates the System Margin becoming reduced The Company may issue further National Electricity Transmission System Warnings - Electricity Margin Notice or High Risk of Demand Reduction.

(j)	The Company may issue a National Electricity Transmission System Warning - Electricity Margin Notice or High Risk of Demand Reduction for any period, not necessarily relating to the following Operational Day, where it has reason to believe there will be a reduced System Margin over a period (for example in periods of protracted Plant shortage, the provisions of OC7.4.8.6 apply).

BC1.5.5	System And Localised NRAPM (Negative Reserve Active Power Margin)

(a)	(i)	System Negative Reserve Active Power Margin

Synchronised Gensets must at all times be capable of reducing output such that the total reduction in output of all Synchronised Gensets is sufficient to offset the loss of the largest secured demand on the System and must be capable of sustaining this response;

(ii)	Localised Negative Reserve Active Power Margin

Synchronised Gensets must at all times be capable of reducing output to allow transfers to and from the System Constraint Group (as the case may be) to be contained within such reasonable limit as The Company may determine and must be capable of sustaining this response.

(b)	The Company will monitor the total of Physical Notifications of exporting BM Units and Generating Units (where appropriate) received against forecast Demand and, where relevant, the appropriate limit on transfers to and from a System Constraint Group and will take account of Dynamic Parameters and Export and Import Limits received to see whether the level of System NRAPM or Localised NRAPM for any period is likely to be insufficient. In addition, The Company may increase the required margin of System NRAPM or Localised NRAPM to allow for variations in forecast Demand. In the case of System NRAPM, this may be by an amount (in The Company's reasonable discretion) not exceeding five per cent of forecast Demand for the period in question. In the case of Localised NRAPM, this may be by an amount (in The Company's reasonable discretion) not exceeding ten per cent of the forecast Demand for the period in question;

(c)	Where the level of System NRAPM or Localised NRAPM for any period is, in The Company's reasonable opinion, likely to be insufficient, then this will be treated as a National Electricity Transmission System Warning as defined in OC7.4.8. The Company may contact all Generators in the case of low System NRAPM and may contact Generators in relation to relevant Gensets in the case of low Localised NRAPM. The Company will raise with each Generator the problems it is anticipating due to low System NRAPM or Localised NRAPM and will discuss whether, in advance of Gate Closure:-

(i)	any change is possible in the Physical Notification of a BM Unit which has been notified to The Company; or

(ii)	any change is possible to the Physical Notification of a BM Unit within an Existing AGR Plant within the Existing AGR Plant Flexibility Limit;

in relation to periods of low System NRAPM or (as the case may be) low Localised NRAPM. The Company will also notify each Externally Interconnected System Operator of the anticipated low System NRAPM or Localised NRAPM and request assistance in obtaining changes to Physical Notifications from BM Units in that External System.

(d)	Following Gate Closure, the procedure of BC2.9.4 will apply. In this case The Company will also endeavor, where time allows, to issue a National Electricity Transmission System Warning – High Risk of Embedded Generation Reduction and/or a National Electricity Transmission System Warning  Embedded Generation Control Imminent as applicable.

BC1.6	SPECIAL PROVISIONS RELATING TO NETWORK OPERATORS

BC1.6.1	User System Data From Network Operators

(a)	By 1000 hours each day each Network Operator will submit to The Company in writing, confirmation or notification of the following in respect of the next Operational Day:

(i)	constraints on its User System which The Company may need to take into account in operating the National Electricity Transmission System. In this BC1.6.1 the term "constraints" shall include restrictions on the operation of Embedded Power Generating Modules, and/or Embedded CCGT Units, and/or Embedded Power Park Modules as a result of the User System to which the Power Generating Module and/or CCGT Unit and/or Power Park Module is connected at the User System Entry Point being operated or switched in a particular way, for example, splitting the relevant busbar. It is a matter for the Network Operator and the Generator to arrange the operation or switching, and to deal with any resulting consequences. The Generator, after consultation with the Network Operator, is responsible for ensuring that no BM Unit Data submitted to The Company can result in the violation of any such constraint on the User System.

(ii)	the requirements of voltage control and MVAr reserves which The Company may need to take into account for System security reasons.

(iii)	where applicable, updated best estimates of Maximum Export Capacity and Maximum Import Capacity and Interface Point Target Voltage/Power Factor for any Interface Point connected to its User System including any requirement for post-fault actions to be implemented on the relevant Offshore Transmission System by The Company.

(iv)  constraints on its User System which The Company may need to take into account when issuing Bid-Offer Acceptances to Additional BM units or Secondary BM units.

(b)	The form of the submission will be:

(i)	that of a BM Unit output or consumption (for MW and for MVAr, in each case a fixed value or an operating range, on the User System at the User System Entry Point, namely in the case of a BM Unit comprising a Generating Unit (as defined in the Glossary and Definitions and not limited by BC1.2) on the higher voltage side of the generator step-up transformer, and/or in the case of a Power Generating Module, at the point of connection and/or in the case of a Power Park Module, at the point of connection) required for particular BM Units (identified in the submission) connected to that User System for each Settlement Period of the next Operational Day;

(ii)	adjusted in each case for MW by the conversion factors applicable for those BM Units to provide output or consumption at the relevant Grid Supply Points.

(c)	At any time and from time to time, between 1000 hours each day and the expiry of the next Operational Day, each Network Operator must submit to The Company in writing any revisions to the information submitted under this BC1.6.1.

BC1.6.2	Notification Of Times To Network Operators

The Company will make available indicative Synchronising and De-Synchronising times to each Network Operator, but only relating to BM Units comprising a Generating Unit (as defined in the Glossary and Definitions and not limited by BC1.2) or a Power Park Module or a CCGT Module and/or a Power Generating Module, Embedded within that Network Operator’s User System and those Gensets directly connected to the National Electricity Transmission System which The Company has identified under OC2 as being those which may, in the reasonable opinion of The Company, affect the integrity of that User System. If in preparing for the operation of the Balancing Mechanism, The Company becomes aware that a BM Unit directly connected to the National Electricity Transmission System may, in its reasonable opinion, affect the integrity of that other User System which, in the case of a BM Unit comprising a Generating Unit (as defined in the Glossary and Definitions and not limited by BC1.2) and/or a Power Generating Module and/or a CCGT Module and/or a Power Park Module, it had not so identified under OC2, then The Company may make available details of its indicative Synchronising and De-Synchronising times to that other User and shall inform the relevant BM Participant that it has done so, identifying the BM Unit concerned.

BC1.7	SPECIAL ACTIONS

BC1.7.1	The Company may need to identify special actions (either pre- or post-fault) that need to be taken by specific Users in order to maintain the integrity of the National Electricity Transmission System in accordance with the Licence Standards and The Company Operational Strategy.

(a)	For a Generator special actions will generally involve a Load change or a change of required Notice to Deviate from Zero NDZ, in a specific timescale on individual or groups of Gensets.

(b)	For Network Operators these special actions will generally involve Load transfers between Grid Supply Points or arrangements for Demand reduction by manual or automatic means.

(c)	For Externally Interconnected System Operators (in their co-ordinating role for Interconnector Users using their External System) these special actions will generally involve an increase or decrease of net power flows across an External Interconnection by either manual or automatic means.

BC1.7.2	These special actions will be discussed and agreed with the relevant User as appropriate. The actual implementation of these special actions may be part of an “emergency circumstances” procedure described under BC2. If not agreed, generation or Demand may be restricted or may be at risk.

BC1.7.3	The Company will normally issue the list of special actions to the relevant Users by 1700 hours on the day prior to the day to which they are to apply.

BC1.8	PROVISION OF REACTIVE POWER CAPABILITY

BC1.8.1	Under certain operating conditions The Company may identify through its Operational Planning that an area of the National Electricity Transmission System may have insufficient Reactive Power capability available to ensure that the operating voltage can be maintained in accordance with The Company’s Licence Standards.

In respect of Onshore Synchronous Generating Unit(s) belonging to  GB Code Users

(i)	that have a Connection Entry Capacity in excess of Rated MW (or the Connection Entry Capacity of the CCGT Module exceeds the sum of Rated MW of the Generating Units comprising the CCGT Module); and

(ii)	that are not capable of continuous operation at any point between the limits 0.85 Power Factor lagging and 0.95 Power Factor leading at the Onshore Synchronous Generating Unit terminals at Active Power output levels higher than Rated MW; and

(iii)	that have either a Completion Date on or after 1st May 2009, or where its Connection Entry Capacity has been increased above Rated MW (or the Connection Entry Capacity of the CCGT Module has increased above the sum of Rated MW of the Generating Units comprising the CCGT Module) such increase takes effect on or after 1st May 2009 but only in respect of GB Generators that are classified as GB Code Users ; and

(iv)	that are in an area of potentially insufficient Reactive Power capability as described in this clause BC1.8.1,

The Company may instruct the Onshore Synchronous Generating Unit(s) to limit its submitted Physical Notifications to no higher than Rated MW (or the Active Power output at which it can operate continuously between the limits 0.85 Power Factor lagging to 0.95 Power Factor leading at its terminals if this is higher) for a period specified by The Company. Such an instruction must be made at least 1 hour prior to Gate Closure, although The Company will endeavour to give as much notice as possible. The instruction may require that a Physical Notification is re-submitted. The period covered by the instruction will not exceed the expected period for which the potential deficiency has been identified. Compliance with the instruction will not incur costs to The Company in the Balancing Mechanism.  The detailed provisions relating to such instructions will normally be set out in the relevant Bilateral Agreement.

BC1.8.2	BC1.8.1 shall not apply to EU Code Users where the obligations under CC.6.3.2(a) apply only to GB Generators. For the avoidance of doubt, EU Code User’s are only required to satisfy the requirements of the ECC’s and not the CC’s.

APPENDIX 1 - BM UNIT DATA

BC1.A.1	More detail about valid values required under the Grid Code for BM Unit Data and Generating Unit Data may be identified by referring to the Data Validation, Consistency and Defaulting Rules. In the case of Embedded BM Units and Generating Units the BM Unit Data and the Generating Unit Data shall represent the value at the relevant Grid Supply Point.  Where data is submitted on a Generating Unit basis, the provisions of this Appendix 1 shall in respect of such data submission apply as if references to BM Unit were replaced with Generating Unit.  Where The Company and the relevant User agree, submission on a Generating Unit basis (in whole or in part) may be otherwise than in accordance with the provisions of the Appendix 1.

BC1.A.1.1	Physical Notifications

For each BM Unit, the Physical Notification is a series of MW figures and associated times, making up a profile of intended input or output of Active Power at the Grid Entry Point or Grid Supply Point, as appropriate, except where a BM Unit is affected by a Stage 2 or higher Network Gas Supply Emergency load shedding event. For each Settlement Period, the first “from time” should be at the start of the Settlement Period and the last “to time” should be at the end of the Settlement Period.

The input or output reflected in the Physical Notification for a single BM Unit (or the aggregate Physical Notifications for a collection of BM Units at a Grid Entry Point or Grid Supply Point or to be transferred across an External Interconnection, owned or controlled by a single BM Participant) must comply with the following limits regarding maximum rates of change, either for a single change or a series of related changes :

| for a change of up to 300MW | no limit; |
| --- | --- |
| for a change greater than 300MW and less than 1000MW | 50MW per minute; |
| for a change of 1000MW or more | 40MW per minute, |

unless prior arrangements have been discussed and agreed with The Company. This limitation is not intended to limit the Run-Up or Run-Down Rates provided as Dynamic Parameters.

In the case where a BM Unit is affected by a Network Gas Supply Emergency load shedding event, once Stage 2 or higher has been declared, then their Physical Notifications shall represent the User's best estimate of the contracted power position of the affected BM Unit at the time of the event, taking into account any mitigating actions to reduce the difference between the contracted power position and the volume to be shed.

An example of the format of Physical Notification is shown below. The convention to be applied is that where it is proposed that the BM Unit will be importing, the Physical Notification is negative.

| Data Name |  |  |  | BMU name |  | Time From |  | From level (MW) |  | Time To |  | To Level MW) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PN | , | TAGENT | , | BMUNIT01 | , | 2001-11-03 06:30 | , | 77 | , | 2001-11-03 07:00 | , | 100 |
| PN | , | TAGENT | , | BMUNIT01 | , | 2001-11-03 07:00 | , | 100 | , | 2001-11-03 07:12 | , | 150 |
| PN | , | TAGENT | , | BMUNIT01 | , | 2001-11-03 07:12 | , | 150 | , | 2001-11-03 07:30 | , | 175 |

A linear interpolation will be assumed between the Physical Notification From and To levels specified for the BM Unit by the BM Participant.

BC1.A.1.2	 Not Used.

BC1.A.1.3	Export And Import Limits

BC1.A.1.3.1	Maximum Export Limit (MEL)

A series of MW figures and associated times, making up a profile of the maximum level at which the BM Unit may be exporting (in MW) to the National Electricity Transmission System at the Grid Entry Point or Grid Supply Point or GSP Group, as appropriate.

For a Power Park Module, the Maximum Export Limit should reflect the maximum possible Active Power output from each Power Park Module consistent with the data submitted within the Power Park Module Availability Matrix as defined under BC.1.A.1.8. For the avoidance of doubt, in the case of a Power Park Module this would equate to the Registered Capacity less the unavailable Power Park Units within the Power Park Module and not include weather corrected MW output from each Power Park Unit.

BC1.A.1.3.2	Maximum Import Limit (MIL)

A series of MW figures and associated times, making up a profile of the maximum level at which the BM Unit may be importing (in MW) from the National Electricity Transmission System at the Grid Entry Point or Grid Supply Point or GSP Group, as appropriate.

An example format of data is shown below. MEL must be positive or zero, and MIL must be negative or zero.

| Data Name |  |  |  | BMU name |  | Time From |  | From level (MW) |  | Time To |  | To level (MW) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MEL | , | TAGENT | , | BMUNIT01 | , | 2001-11-03 05:00 | , | 410 | , | 2001-11-03 09:35 | , | 410 |
| MEL | , | TAGENT | , | BMUNIT01 | , | 2001-11-03 09:35 | , | 450 | , | 2001-11-03 12:45 | , | 450 |
| MIL | , | TAGENT | , | BMUNIT04 | , | 2001-11-03 06:30 | , | -200 | , | 2001-11-03 07:00 | , | -220 |

BC1.A.1.4	Bid-Offer Data

| For each BM Unit for each Settlement Period: | Up to 10 Bid-Offer Pairs as defined in the BSC. |
| --- | --- |

An example of the format of data is shown below.

| Data |  | Name |  | BMU name |  | Time from |  | Time to |  | Pair ID |  | From Level (MW) |  | To Level (MW) |  | Offer (£/ MWh) |  | Bid (£/ MWh) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BOD | , | TAGENT | , | BMUNIT01 | , | 2000-10-28 12:00 | , | 2000-10-28 13:30 | , | 4 | , | 30 | , | 30 | , | 40 | , | 35 |
| BOD | , | TAGENT | , | BMUNIT01 | , | 2000-10-28 12:00 | , | 2000-10-28 13:30 | , | 3 | , | 20 | , | 20 | , | 35 | , | 30 |
| BOD | , | TAGENT | , | BMUNIT01 | , | 2000-10-28 12:00 | , | 2000-10-28 13:30 | , | 2 | , | 40 | , | 40 | , | 32 | , | 27 |
| BOD | , | TAGENT | , | BMUNIT01 | , | 2000-10-28 12:00 | , | 2000-10-28 13:30 | , | 1 | , | 50 | , | 50 | , | 30 | , | 25 |
| BOD | , | TAGENT | , | BMUNIT01 | , | 2000-10-28 12:00 | , | 2000-10-28 13:30 | , | -1 | , | -40 | , | -40 | , | 25 | , | 20 |
| BOD | , | TAGENT | , | BMUNIT01 | , | 2000-10-28 12:00 | , | 2000-10-28 13:30 | , | -2 | , | -30 | , | -30 | , | 23 | , | 17 |

This example of Bid-Offer data is illustrated graphically below:

Final Physical

Notification

Bid-Offer Pair No 1

Bid-Offer Pair No 2

Bid-Offer Pair No 3

Bid-Offer Pair No 4

Bid-Offer Pair No -1

Bid-Offer Pair No -2

50MW Offer £30 Bid £25

40MW Offer £32 Bid £27

20MW Offer £35 Bid £30

30MW Offer £40 Bid £35

-40MW Offer £25 Bid £20

-30MW Offer £23 Bid £17

BC1.A.1.5	Dynamic Parameters

The Dynamic Parameters comprise:

Up to three Run-Up Rate(s) and up to three Run-Down Rate(s), expressed in MW/minute and associated Run-Up Elbow(s) and Run-Down Elbow(s), expressed in MW for output and the same for input. It should be noted that Run-Up Rate(s) are applicable to a MW figure becoming more positive;

Notice to Deviate from Zero (NDZ) output or input, being the notification time required for a BM Unit to start importing or exporting energy, from a zero Physical Notification level as a result of a Bid-Offer Acceptance, expressed in minutes;

Notice to Deliver Offers (NTO) and Notice to Deliver Bids (NTB), expressed in minutes, indicating the notification time required for a BM Unit to start delivering Offers and Bids respectively from the time that the Bid-Offer Acceptance is issued. In the case of a BM Unit comprising a Genset, NTO and NTB will be set to a maximum period of two minutes;

Minimum Zero Time (MZT), being either the minimum time that a BM Unit which has been exporting must operate at zero or be importing, before returning to exporting or the minimum time that a BM Unit which has been importing must operate at zero or be exporting before returning to importing, as a result of a Bid-Offer Acceptance, expressed in minutes;

Minimum Non-Zero Time (MNZT), expressed in minutes, being the minimum time that a BM Unit can operate at a non-zero level as a result of a Bid-Offer Acceptance;

Stable Export Limit (SEL) expressed in MW at the Grid Entry Point or Grid Supply Point or GSP Group, as appropriate, being the minimum value at which the BM Unit can, under stable conditions, export to the National Electricity Transmission System;

Stable Import Limit (SIL) expressed in MW at the Grid Entry Point or Grid Supply Point or GSP Group, as appropriate, being the minimum value at which the BM Unit can, under stable conditions, import from the National Electricity Transmission System;

Maximum Delivery Volume (MDV), expressed in MWh, being the maximum number of MWh of Offer (or Bid if MDV is negative) that a particular BM Unit may deliver within the associated Maximum Delivery Period (MDP), expressed in minutes, being the maximum period over which the MDV applies.

Last Time to Cancel Synchronisation, expressed in minutes with an upper limit of 60 minutes, being the notification time required to cancel a BM Unit’s transition from operation at zero. This parameter is only applicable where the transition arises either from a Physical Notification or, in the case where the Physical Notification is zero, a Bid-Offer Acceptance. There can be up to three Last Time to Cancel Synchronisation(s) each applicable for a range of values of Notice to Deviate from Zero.

BC1.A.1.6	CCGT Module Matrix

BC1.A.1.6.1	CCGT Module Matrix showing the combination of CCGT Units running in relation to any given MW output, in the form of the diagram illustrated below. The CCGT Module Matrix is designed to achieve certainty in knowing the number of CCGT Units synchronised to meet the Physical Notification and to achieve a Bid-Offer Acceptance.

BC1.A.1.6.2	In the case of a Range CCGT Module, and if the Generator so wishes, a request for the single Grid Entry Point at which power is provided from the Range CCGT Module to be changed in accordance with the provisions of BC1.A.1.6.4 below:

CCGT Module Matrix example form

| CCGT MODULE ACTIVE POWER MW | CCGT GENERATING UNITS* AVAILABLE |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1st GT | 2nd GT | 3rd GT | 4th GT | 5th GT | 6th GT | 1st ST | 2nd ST | 3rd ST |
|  | ACTIVE POWER OUTPUT |  |  |  |  |  |  |  |  |
|  | 150 | 150 | 150 |  |  |  | 100 |  |  |
| 0MW to 150MW | / |  |  |  |  |  |  |  |  |
| 151MW to 250MW | / |  |  |  |  |  | / |  |  |
| 251MW to 300MW | / | / |  |  |  |  |  |  |  |
| 301MW to 400MW | / | / |  |  |  |  | / |  |  |
| 401MW to 450MW | / | / | / |  |  |  |  |  |  |
| 451MW to 550MW | / | / | / |  |  |  | / |  |  |

* as defined in the Glossary and Definitions and not limited by BC1.2

BC1.A.1.6.3	In the absence of the correct submission of a CCGT Module Matrix the last submitted (or deemed submitted) CCGT Module Matrix shall be taken to be the CCGT Module Matrix submitted hereunder.

BC1.A.1.6.4	The data may also include in the case of a Range CCGT Module, a request for the Grid Entry Point at which the power is provided from the Range CCGT Module to be changed with effect from the beginning of the following Operational Day to another specified single Grid Entry Point (there can be only one) to that being used for the current Operational Day. The Company will respond to this request by 1600 hours on the day of receipt of the request. If The Company agrees to the request (such agreement not to be unreasonably withheld), the Generator will operate the Range CCGT Module in accordance with the request. If The Company does not agree, the Generator will, if it produces power from that Range CCGT Module, continue to provide power from the Range CCGT Module to the Grid Entry Point being used at the time of the request. The request can only be made up to 1100 hours in respect of the following Operational Day. No subsequent request to change can be made after 1100 hours in respect of the following Operational Day. Nothing in this paragraph shall prevent the busbar at the Grid Entry Point being operated in separate sections.

BC1.A.1.6.5	The principles set out in PC.A.3.2.3 apply to the submission of a CCGT Module Matrix and accordingly the CCGT Module Matrix can only be amended as follows:

(a)	Normal CCGT Module

if the CCGT Module is a Normal CCGT Module, the CCGT Units within that CCGT Module can only be amended such that the CCGT Module comprises different CCGT Units if The Company gives its prior consent in writing. Notice of the wish to amend the CCGT Units within such a CCGT Module must be given at least 6 months before it is wished for the amendment to take effect;

(b)	Range CCGT Module

if the CCGT Module is a Range CCGT Module, the CCGT Units within that CCGT Module can only be amended such that the CCGT Module comprises different CCGT Units for a particular Operational Day if the relevant notification is given by 1100 hours on the day prior to the Operational Day in which the amendment is to take effect. No subsequent amendment may be made to the CCGT Units comprising the CCGT Module in respect of that particular Operational Day.

BC1.A.1.6.6	In the case of a CCGT Module Matrix submitted (or deemed to be submitted) as part of the other data for CCGT Modules, the output of the CCGT Module at any given instructed MW output must reflect the details given in the CCGT Module Matrix. It is accepted that in cases of change in MW in response to instructions issued by The Company there may be a transitional variance to the conditions reflected in the CCGT Module Matrix. In achieving an instruction the range of number of CCGT Units envisaged in moving from one MW output level to the other must not be departed from. Each Generator shall notify The Company as soon as practicable after the event of any such variance. It should be noted that there is a provision above for the Generator to revise the CCGT Module Matrix, subject always to the other provisions of this BC1;

BC1.A.1.6.7	Subject as provided above, The Company will rely on the CCGT Units specified in such CCGT Module Matrix running as indicated in the CCGT Module Matrix when it issues an instruction in respect of the CCGT Module;

BC1.A.1.6.8	Subject as provided in BC1.A.1.6.5 above, any changes to the CCGT Module Matrix must be notified immediately to The Company in accordance with the relevant provisions of BC1.

BC1.A.1.7	Cascade Hydro Scheme Matrix

BC1.A.1.7.1	A Cascade Hydro Scheme Matrix showing the performance of individual Generating Units forming part of a Cascade Hydro Scheme in response to Bid-Offer Acceptance.  An example table is shown below:

Cascade Hydro Scheme Matrix example form

| Plant | Synchronises when offer is greater than…….. |
| --- | --- |
| Generating Unit 1 | ......MW |
| Generating Unit 2 | ......MW |
| Generating Unit 3 | ......MW |
| Generating Unit 4 | ......MW |
| Generating Unit 5 | ......MW |

BC1.A.1.8	Power Park Module Availability Matrix

BC1.A.1.8.1	Power Park Module Availability Matrix showing the number of each type of Power Park Units expected to be available is illustrated in the example form below. The Power Park Module Availability Matrix is designed to achieve certainty in knowing the number of Power Park Units Synchronised to meet the Physical Notification and to achieve a Bid-Offer Acceptance by specifying which BM Unit each Power Park Module forms part of. The Power Park Module Availability Matrix may have as many columns as are required to provide information on the different make and model for each type of Power Park Unit in a Power Park Module and as many rows as are required to provide information on the Power Park Modules within each BM Unit. The description is required to assist identification of the Power Park Units within the Power Park Module and correlation with data provided under the Planning Code.

Power Park Module Availability Matrix example form

| BM Unit Name |  |  |  |  |
| --- | --- | --- | --- | --- |
| Power Park Module [unique identifier] |  |  |  |  |
| POWER PARK UNIT AVAILABILITY | POWER PARK UNITS |  |  |  |
|  | Type A | Type B | Type C | Type D |
| Description (Make/Model) |  |  |  |  |
| Number of units |  |  |  |  |
| Power Park Module [unique identifier] |  |  |  |  |
| POWER PARK UNIT AVAILABILITY | POWER PARK UNITS |  |  |  |
|  | Type A | Type B | Type C | Type D |
| Description (Make/Model) |  |  |  |  |
| Number of units |  |  |  |  |

BC1.A.1.8.2	In the absence of the correct submission of a Power Park Module Availability Matrix the last submitted (or deemed submitted) Power Park Module Availability Matrix shall be taken to be the Power Park Module Availability Matrix submitted hereunder.

BC1.A.1.8.3	The Company will rely on the Power Park Units, Power Park Modules and BM Units specified in such Power Park Module Availability Matrix running as indicated in the Power Park Module Availability Matrix when it issues an instruction in respect of the BM Unit.

BC1.A.1.8.4	Subject as provided in PC.A.3.2.4 any changes to Power Park Module or BM Unit configuration, or availability of Power Park Units which affects the information set out in the Power Park Module Availability Matrix must be notified immediately to The Company in accordance with the relevant provisions of BC1. Initial notification may be by telephone.  In some circumstances, such as a significant re-configuration of a Power Park Module due to an unplanned outage, a revised Power Park Module Availability Matrix must be supplied on The Company's request.

BC1.A.1.9	Synchronous Power Generating Module Matrix

BC1.A.1.9.1	Synchronous Power Generating Module Matrix showing the combination of Synchronous Power Generating Units running in relation to any given MW output, in the form of the table illustrated below. The Synchronous Power Generating Module Matrix is designed to achieve certainty in knowing the number of Synchronous Power Generating Units synchronised to meet the Physical Notification and to achieve a Bid-Offer Acceptance.

BC1.A.1.9.2	This data need not be provided where a submission has been made in respect of BC1.A.1.6, BC1.A.1.7 or BC1.A.1.8

Synchronous Power Generating Module Matrix example form

| SYNCHRONOUS POWER GENERATING MODULE MATRIX MW | SYNCHRONOUS POWER GENERATING UNITS* AVAILABLE |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1st GT | 2nd GT | 3rd GT | 4th GT | 5th GT | 6th GT | 1st ST | 2nd ST | 3rd ST |
|  | ACTIVE POWER OUTPUT |  |  |  |  |  |  |  |  |
|  | 150 | 150 | 150 |  |  |  | 100 |  |  |
| 0MW to 150MW | / |  |  |  |  |  |  |  |  |
| 151MW to 250MW | / |  |  |  |  |  | / |  |  |
| 251MW to 300MW | / | / |  |  |  |  |  |  |  |
| 301MW to 400MW | / | / |  |  |  |  | / |  |  |
| 401MW to 450MW | / | / | / |  |  |  |  |  |  |
| 451MW to 550MW | / | / | / |  |  |  | / |  |  |

* as defined in the Glossary and Definitions and not limited by BC1.2

BC1.A.1.9.3	In the absence of the correct submission of a Synchronous Power Generating Module Matrix the last submitted (or deemed submitted) Synchronous Power Generating Module Matrix shall be taken to be the Synchronous Power Generating Module Matrix submitted hereunder.

BC1.A.1.9.4	The principles set out in PC.A.3.2.5 apply to the submission of a Synchronous Power Generating Module Matrix and accordingly the Synchronous Power Generating Module Matrix can only be amended as if the Synchronous Power Generating Units within that Synchronous Power Generating Module can only be amended such that the Synchronous Power Generating Module comprises different Synchronous Power Generating Units if The Company gives its prior consent in writing. Notice of the wish to amend the Synchronous Power Generating Units within such a Synchronous Power Generating Module must be given at least 6 months before it is wished for the amendment to take effect;

BC1.A.1.9.5	In the case of a Synchronous Power Generating Module Matrix submitted (or deemed to be submitted) as part of the other data for Synchronous Power Generating Modules, the output of the Synchronous Power Generating Module at any given instructed MW output must reflect the details given in the  Synchronous Power Generating Module Matrix. It is accepted that in cases of change in MW in response to instructions issued by The Company there may be a transitional variance to the conditions reflected in the Synchronous Power Generating Module Matrix. In achieving an instruction the range of number of Synchronous Power Generating Units envisaged in moving from one MW output level to the other must not be departed from. Each Generator shall notify The Company as soon as practicable after the event of any such variance. It should be noted that there is a provision above for the Generator to revise the Synchronous Power Generating Module Matrix, subject always to the other provisions of this BC1;

BC1.A.1.9.6	Subject as provided above, The Company will rely on the Synchronous Power Generating Units specified in such Synchronous Power Generating Module Matrix running as indicated in the Synchronous Power Generating Module Matrix when it issues an instruction in respect of the Synchronous Power Generating Module;

BC1.A.1.9.7	Subject as provided in BC1.A.1.9.4 above, any changes to the Synchronous Power Generating Module Matrix must be notified immediately to The Company in accordance with the relevant provisions of BC1.

BC1.A.10			Aggregator Impact Matrix

BC1.A.10.1	For each Additional BM Unit and Secondary BM Unit the relevant BM Participant will submit data relating to the effect of a Bid-Off Acceptance on each Grid Supply Point within the GSP Group over which the Additional BM Unit or Secondary BM Unit was defined.

BC1.A.10.2	For each Additional BM Unit and Secondary BM Unit the relevant BM Participant will also provide the post-codes and MSIDs that make up the Additional BM Unit or Secondary BM Unit

Aggregator Impact Matrix example form

| BMU Name |  |  |  |
| --- | --- | --- | --- |
| Operational Day from which values apply |  |  |  |
| Grid Supply Point | % Impact | Grid Supply Point | % Impact |

APPENDIX 2 - DATA TO BE MADE AVAILABLE BY THE COMPANY

BC1.A.2.1	Initial Day Ahead Demand Forecast

Normally by 09:00 hours each day, values (in MW) for each Settlement Period of the next following Operational Day of the following data items:-

(i)	Initial forecast of National Demand;

(II)	Initial forecast of Demand for a number of predetermined constraint groups.

BC1.A.2.2	Initial Day Ahead Market Information

Normally by 12:00 hours each day, values (in MW) for each Settlement Period of the next following Operational Day of the following data items:-

(i)	Initial National Indicated Margin

This is the difference between the sum of BM Unit MELs and the forecast of National Electricity Transmission System Demand.

(ii)	Initial National Indicated Imbalance

This is the difference between the sum of Physical Notifications for BM Units comprising Generating Units (as defined in the Glossary and Definitions and not limited by BC1.2) and/or Power Generating Modules and/or CCGT Modules and/or Power Park Modules and the forecast of National Electricity Transmission System Demand.

(iii)	Forecast of National Electricity Transmission System Demand.

BC1.A.2.3	Current Day And Day Ahead Updated Market Information

Data will normally be made available by the times shown below for the associated periods of time:

| Target Data Release Time | Period Start Time | Period End Time |
| --- | --- | --- |
| 02:00 | 02:00 D0 | 05:00 D+1 |
| 10:00 | 10:00 D0 | 05:00 D+1 |
| 16:00 | 05:00 D+1 | 05:00 D+2 |
| 16:30 | 16:30 D0 | 05:00 D+1 |
| 22:00 | 22:00 D0 | 05:00 D+2 |

In this table, D0 refers to the current day, D+1 refers to the next day and D+2 refers to the day following D+1.

In all cases, data will be ½ hourly average MW values calculated by The Company. Information to be released includes:

National Information

(i)	National Indicated Margin;

(ii)	National Indicated Imbalance;

(iii)	Updated forecast of National Electricity Transmission System Demand.

Constraint Boundary Information (For Each Constraint Boundary)

(i)	Indicated Constraint Boundary Margin;

This is the difference between the Constraint Boundary Transfer limit and the difference between the sum of BM Unit MELs and the forecast of local Demand within the constraint boundary.

(ii)	Local Indicated Imbalance;

This is the difference between the sum of Physical Notifications for BM Units comprising Generating Units (as defined in the Glossary and Definitions and not limited by BC1.2) and/or Power Generating Modules and/or CCGT Modules and/or Power Park Modules and the forecast of local Demand within the constraint boundary.

(iii)	Updated forecast of the local Demand within the constraint boundary.

< END OF BALANCING CODE NO. 1 >