EUROPEAN CONNECTION CONDITIONS

(ECC)

CONTENTS

(This contents page does not form part of the Grid Code)

Paragraph No/Title	Page Number

ECC.1   INTRODUCTION	2

ECC.2   OBJECTIVE	3

ECC.3   SCOPE	3

ECC.4   PROCEDURE	5

ECC.5   CONNECTION	5

ECC.6   TECHNICAL, DESIGN AND OPERATIONAL CRITERIA	7

ECC.7   SITE RELATED CONDITIONS	90

ECC.8   ANCILLARY SERVICES	98

APPENDIX E1 - SITE RESPONSIBILITY SCHEDULES	100

PROFORMA FOR SITE RESPONSIBILITY SCHEDULE	103

APPENDIX E2 - OPERATION DIAGRAMS	108

PART 1A - PROCEDURES RELATING TO OPERATION DIAGRAMS	108

PART E1B - PROCEDURES RELATING TO GAS ZONE DIAGRAMS	111

PART E2 - NON-EXHAUSTIVE LIST OF APPARATUS TO BE INCLUDED ON OPERATION DIAGRAMS	112

APPENDIX E3 - MINIMUM FREQUENCY RESPONSE CAPABILITY REQUIREMENT PROFILE AND OPERATING RANGE FOR  POWER GENERATING MODULES AND HVDC EQUIPMENT	114

APPENDIX 4 - FAULT RIDE THROUGH REQUIREMENTS	120

APPENDIX E5 - TECHNICAL REQUIREMENTS LOW FREQUENCY RELAYS FOR THE AUTOMATIC DISCONNECTION OF SUPPLIES AT LOW FREQUENCY	126

APPENDIX E6 - PERFORMANCE REQUIREMENTS FOR CONTINUOUSLY ACTING AUTOMATIC EXCITATION CONTROL SYSTEMS FOR ONSHORE SYNCHRONOUS POWER GENERATING MODULES,	130

APPENDIX E7 - PERFORMANCE REQUIREMENTS FOR CONTINUOUSLY ACTING AUTOMATIC VOLTAGE CONTROL SYSTEMS FOR AC CONNECTED ONSHORE POWER PARK MODULES AND OTSDUW PLANT AND APPARATUS AT THE INTERFACE POINT HVDC SYSTEMS AND REMOTE END HVDC CONVERTER STATIONS	134

APPENDIX E8 - PERFORMANCE REQUIREMENTS FOR CONTINUOUSLY ACTING AUTOMATIC VOLTAGE CONTROL SYSTEMS FOR CONFIGURATION 2 AC CONNECTED OFFSHORE POWER PARK MODULES AND CONFIGURATION 2 DC CONNECTED POWER PARK MODULES	141

ECC.1	INTRODUCTION

ECC.1.1	The European Connection Conditions ("ECC") specify both:

(a)	the minimum technical, design and operational criteria which must be complied with by:

(i)	any EU Code User  connected to or seeking connection with the National Electricity Transmission System, or

(ii)	EU Generators  or HVDC System Owners connected to or seeking connection to a User's System which is located in Great Britain or Offshore, or

(iii)	Network Operators who are EU Code Users

(iv)	Network Operators who are GB Code Users but only in respect of:-

- Their obligations in respect of Embedded Medium Power Stations not subject to a Bilateral Agreement for whom the requirements of ECC.3.1(b)(iii) apply alone; and/or

- The requirements of this ECC only in relation to each EU Grid Supply Point.  Network Operators in respect of all other Grid Supply Points should continue to satisfy the requirements as specified in the CCs.

(v)	Non-Embedded Customers who are EU Code Users

(b)	the minimum technical, design and operational criteria with which The Company will comply in relation to the part of the National Electricity Transmission System at the Connection Site with Users.  In the case of any OTSDUW Plant and Apparatus, the ECC also specify the minimum technical, design and operational criteria which must be complied with by the User when undertaking OTSDUW.

(c )	The requirements of Retained EU Law (Commission Regulation (EU) 2016/631) shall not apply to

- Power Generating Modules that are installed to provide backup power and operate in parallel with the Total System for less than 5 minutes per calendar month while the System is in normal state.  Parallel operation during maintenance or commissioning of tests of that Power Generating Module shall not count towards that five minute limit.

- Power Generating Modules connected to the Transmission System or Network Operators System which are not operated in synchronism with a Synchronous Area.

- Power Generating Modules that do not have a permanent Connection Point or User System Entry Point and used by The Company to temporarily provide power when normal System capacity is partly or completely unavailable.

(iv)	       Electricity Storage Modules.

(d)     Storage Users are required to comply with the entirety of the ECC but are not subject to the requirements of Retained EU Law (Commission Regulation (EU) 2016/631, Commission Regulation (EU) 2016/1388 and Commission Regulation (EU) 2016/1485).  The requirements of the ECC shall therefore be enforceable against Storage Users under the Grid Code only (and not under any of the aforementioned Retained EU Law) and any derogation sought by a Storage User in respect of the ECC shall be deemed a derogation from the Grid Code only (and not from the aforementioned Retained EU Law).

ECC.2	OBJECTIVE

ECC.2.1	The objective of the ECC is to ensure that by specifying minimum technical, design and operational criteria the basic rules for connection to the National Electricity Transmission System and (for certain Users) to a User's System are similar for all Users of an equivalent category and will enable The Company to comply with its statutory and Transmission Licence obligations and the applicable Retained EU Law.

ECC.2.2	In the case of any OTSDUW the objective of the ECC is to ensure that by specifying the minimum technical, design and operational criteria the basic rules relating to an Offshore Transmission System designed and constructed by an Offshore Transmission Licensee and designed and/or constructed by a User under the OTSDUW Arrangements are equivalent.

ECC.2.3	Provisions of the ECC which apply in relation to OTSDUW and OTSUA, and/or a Transmission Interface Site, shall (in any particular case) apply up to the OTSUA Transfer Time, whereupon such provisions shall (without prejudice to any prior non-compliance) cease to apply, without prejudice to the continuing application of provisions of the ECC applying in relation to the relevant Offshore Transmission System and/or Connection Site.  It is the case therefore that in cases where the OTSUA becomes operational prior to the OTSUA Transfer Time that a EU Generator is required to comply with this ECC both as it applies to its Plant and Apparatus at a Connection Site\Connection Point and the OTSUA at the Transmission Interface Site/Transmission Interface Point until the OTSUA Transfer Time and this ECC shall be construed accordingly.

ECC.2.4	In relation to OTSDUW, provisions otherwise to be contained in a Bilateral Agreement may be contained in the Construction Agreement, and accordingly a reference in the ECC to a relevant Bilateral Agreement includes the relevant Construction Agreement.

ECC.3	SCOPE

ECC.3.1	The ECC applies to The Company and to Users, which in the ECC means:

- EU Generators (other than those which only have Embedded Small Power Stations), including those undertaking OTSDUW including Power Generating Modules, and DC Connected Power Park Modules. For the avoidance of doubt, Electricity Storage Modules are included within the definition of Power Generating Modules for which the requirements of the ECC would be equally applicable.

- Network Operators but only in respect of:-

(i) 	Network Operators who are EU Code Users

(ii) 	Network Operators who only have EU Grid Supply Points

(iii)	Embedded Medium Power Stations not subject to a Bilateral Agreement as provided for in ECC.3.2, ECC.3.3, EC3.4,  EC3.5,  ECC5.1, ECC.6.4.4 and ECA.3.4;

(iv)	Notwithstanding the requirements of ECC3.1(b)(i)(ii) and (iii), Network Operators who own and/or operate EU Grid Supply Points, are only required to satisfy the requirements of this ECC in relation to each EU Grid Supply Point.  Network Operators in respect of all other Grid Supply Points should continue to satisfy the requirements as specified in the CCs.

(c)	Non-Embedded Customers who are also EU Code Users;

(d)	HVDC System Owners who are also EU Code Users;

(e)	BM Participants and Externally Interconnected System Operators who are also EU Code Users in respect of ECC.6.5, ECC.7.9, ECC.7.10 and ECC.7.11 only; and.

(f)	In relation to Distribution Restoration Zones, Restoration Contractors who are Non- CUSC Parties and whose Embedded Plant needs to comply with the requirements of EREC G99, other than those  included in (a) to (e) above, shall only be required to satisfy ECC.6.1.2, ECC.6.2.2.2.1.2, ECC.6.2.2.7, ECC.6.3, ECC.6.6, ECC.7.10, ECC.7.11 and ECC.8.1 unless additional technical requirements are provided for in the Anchor Restoration Contract or Top Up Restoration Contract.  Restoration Contractors who are Non-CUSC Parties and whose Embedded Plant needs to comply with EREC G59 are not included in the scope of the ECC and should refer to the CC.

ECC.3.2	The above categories of User will become bound by the applicable sections of the ECC prior to them generating, distributing, storing, supplying or consuming, as the case may be, and references to the various categories should, therefore, be taken as referring to them in that prospective role.

ECC.3.3	Embedded Medium Power Stations not subject to a Bilateral Agreement and Embedded HVDC Systems not subject to a Bilateral Agreement Provisions.

The following provisions apply in respect of Embedded Medium Power Stations not subject to a Bilateral Agreement and Embedded HVDC Systems not subject to a Bilateral Agreement.

ECC.3.3.1	The obligations within the ECC that are expressed to be applicable to EU Generators in respect of Embedded Medium Power Stations not subject to a Bilateral Agreement and HVDC System Owners in respect of Embedded HVDC Systems not subject to a Bilateral Agreement (where the obligations are in each case listed in ECC.3.3.2) shall be read and construed as obligations that the Network Operator within whose System any such Medium Power Station or HVDC System is Embedded must ensure are performed and discharged by the EU Generator or the HVDC  Owner.  Embedded Medium Power Stations not subject to a Bilateral Agreement and Embedded HVDC Systems not subject to a Bilateral Agreement which are located Offshore and which are connected to an Onshore User System will be required to meet the applicable requirements of the Grid Code as though they are an Onshore Generator or Onshore HVDC System Owner connected to an Onshore User System Entry Point.

ECC.3.3.2	The Network Operator within whose System a Medium Power Station not subject to a Bilateral Agreement is Embedded or a HVDC System not subject to a Bilateral Agreement is Embedded must ensure that the following obligations in the ECC are performed and discharged by the EU Generator  in respect of each such Embedded Medium Power Station or the HVDC System Owner in the case of an Embedded HVDC System:

ECC.5.1

ECC.5.2.2

ECC.5.3

ECC.6.1.3

ECC.6.1.5 (b)

ECC.6.3.2, ECC.6.3.3, ECC.6.3.4, ECC.6.3.6, ECC.6.3.7, ECC.6.3.8, ECC.6.3.9, ECC.6.3.10, ECC.6.3.12, ECC.6.3.13, ECC.6.3.15, ECC.6.3.16

ECC.6.4.4

ECC.6.5.6 (where required by ECC.6.4.4)

In respect of ECC.6.2.2.2, ECC.6.2.2.3, ECC.6.2.2.5, ECC.6.1.5(a), ECC.6.1.5(b) and ECC.6.3.11 equivalent provisions as co-ordinated and agreed with the Network Operator and EU Generator or HVDC System Owner may be required.  Details of any such requirements will be notified to the Network Operator in accordance with ECC.3.5.

ECC.3.3.3	In the case of Embedded Medium Power Stations not subject to a Bilateral Agreement and Embedded HVDC Systems not subject to a Bilateral Agreement the requirements in:

ECC.6.1.6

ECC.6.3.8

ECC.6.3.12

ECC.6.3.15

ECC.6.3.16

ECC.6.3.17

that would otherwise have been specified in a Bilateral Agreement will be notified to the relevant Network Operator in writing in accordance with the provisions of the CUSC and the Network Operator must ensure such requirements are performed and discharged by the Generator or the HVDC System owner.

ECC.3.4	In the case of Offshore Embedded Power Generating Modules connected to an Offshore User’s System which  directly connects to an Offshore Transmission System, any additional requirements in respect of such Offshore Embedded Power Generating Modules may be specified in the relevant Bilateral Agreement with the Network Operator or in any Bilateral Agreement between The Company and such Offshore Generator.

ECC.3.5	In the case of a Generator undertaking OTSDUW connecting to an Onshore Network Operator’s System, any additional requirements in respect of such OTSDUW Plant and Apparatus will be specified in the relevant Bilateral Agreement with the EU Generator. For the avoidance of doubt, requirements applicable to EU Generators undertaking OTSDUW and connecting to a Network Operator’s User System, shall be consistent with those applicable requirements of Generators undertaking OTSDUW and connecting to a Transmission Interface Point.

ECC.3.6	The requirements of this ECC shall apply to EU Code Users in respect of Power Generating Modules (including DC Connected Power Park Modules and Electricity Storage Modules) and HVDC Systems.

ECC.4	PROCEDURE

ECC.4.1	The CUSC contains certain provisions relating to the procedure for connection to the National Electricity Transmission System or, in the case of Embedded Power Stations or Embedded HVDC Systems, becoming operational and includes provisions relating to certain conditions to be complied with by  EU Code Users prior to and during the course of The Company notifying the User that it has the right to become operational.  The procedure for an EU Code User  to become connected is set out in the Compliance Processes.

ECC.5	CONNECTION

ECC.5.1	The provisions relating to connecting to the National Electricity Transmission System (or to a User's System in the case of a connection of an Embedded Large Power Station or Embedded Medium Power Stations or Embedded HVDC System) are contained in:

(a)	the CUSC and/or CUSC Contract (or in the relevant application form or offer for a CUSC Contract);

(b)	or, in the case of an Embedded Development, the relevant Distribution Code and/or the Embedded Development Agreement for the connection (or in the relevant application form or offer for an Embedded Development Agreement),

and include provisions relating to both the submission of information and reports relating to compliance with the relevant European Connection Conditions for that EU Code User, Safety Rules, commissioning programmes, Operation Diagrams and approval to connect (and their equivalents in the case of Embedded Medium Power Stations not subject to a Bilateral Agreement or Embedded HVDC Systems not subject to a Bilateral Agreement).  References in the ECC to the "Bilateral Agreement” and/or “Construction Agreement" and/or “Embedded Development Agreement” shall be deemed to include references to the application form or offer therefor.

ECC.5.2	Items For Submission

ECC.5.2.1	Prior to the Completion Date (or, where the EU Generator  is undertaking OTSDUW, any later date specified) under the Bilateral Agreement and/or Construction Agreement, the following is submitted pursuant to the terms of the Bilateral Agreement and/or Construction Agreement:

(a)	updated Planning Code data (both Standard Planning Data and Detailed Planning Data), with any estimated values assumed for planning purposes confirmed or, where practical, replaced by validated actual values and by updated estimates for the future and by updated forecasts for Forecast Data items such as Demand, pursuant to the requirements of the Planning Code;

(b)	details of the Protection arrangements and settings referred to in ECC.6;

(c)	copies of all Safety Rules and Local Safety Instructions applicable at Users' Sites which will be used at the Transmission/User interface (which, for the purpose of OC8, must be to The Company’s satisfaction regarding the procedures for Isolation and Earthing. The Company will consult the Relevant Transmission Licensee when determining whether the procedures for Isolation and Earthing are satisfactory);

(d)	information to enable the preparation of the Site Responsibility Schedules on the basis of the provisions set out in Appendix 1;

(e)	an Operation Diagram for all HV Apparatus on the User side of the Connection Point as described in ECC.7;

(f)	the proposed name of the User Site (which shall not be the same as, or confusingly similar to, the name of any Transmission Site or of any other User Site);

(g)	written confirmation that Safety Co-ordinators acting on behalf of the User are authorised and competent pursuant to the requirements of OC8;

(h)	Such RISSP prefixes pursuant to the requirements of OC8. Such RISSP prefixes shall be circulated utilising a proforma in accordance with OC8;

(i)	a list of the telephone numbers for Joint System Incidents at which senior management representatives nominated for the purpose can be contacted and confirmation that they are fully authorised to make binding decisions on behalf of the User, pursuant to OC9;

(j)	a list of managers who have been duly authorised to sign Site Responsibility Schedules on behalf of the User;

(k)	information to enable the preparation of the Site Common Drawings as described in ECC.7;

(l)	a list of the telephone numbers for the Users facsimile machines referred to in ECC.6.5.9; and

(m)	for Sites in Scotland and Offshore a list of persons appointed by the User to undertake operational duties on the User’s System (including any  OTSDUW prior to the OTSUA Transfer Time) and to issue and receive operational messages and instructions in relation to the User’s System (including any  OTSDUW prior to the OTSUA Transfer Time); and an appointed person or persons responsible for the maintenance and testing of User’s Plant and Apparatus.

ECC.5.2.2	Prior to the Completion Date the following must be submitted to The Company by the Network Operator in respect of an Embedded Development:

(a)	updated Planning Code data (both Standard Planning Data and Detailed Planning Data), with any estimated values assumed for planning purposes confirmed or, where practical, replaced by validated actual values and by updated estimates for the future and by updated forecasts for Forecast Data items such as Demand, pursuant to the requirements of the Planning Code;

(b)	details of the Protection arrangements and settings referred to in ECC.6;

(c) 	the proposed name of the Embedded Medium Power Station or Embedded HVDC System (which shall be agreed with The Company unless it is the same as, or confusingly similar to, the name of other Transmission Site or User Site);

ECC.5.2.3	Prior to the Completion Date contained within an Offshore Transmission Distribution Connection Agreement the following must be submitted to The Company by the Network Operator in respect of a proposed new Interface Point within its User System:

(a)	updated Planning Code data (both Standard Planning Data and Detailed Planning Data), with any estimated values assumed for planning purposes confirmed or, where practical, replaced by validated actual values and by updated estimates for the future and by updated forecasts for Forecast Data items such as Demand, pursuant to the requirements of the Planning Code;

(b)	details of the Protection arrangements and settings referred to in ECC.6;

(c) 	the proposed name of the Interface Point (which shall not be the same as, or confusingly similar to, the name of any Transmission Site or of any other User Site);

ECC.5.2.4	In the case of OTSDUW Plant and Apparatus (in addition to items under ECC.5.2.1 in respect of the Connection Site), prior to the Completion Date (or any later date specified)  under the Construction Agreement the following must be submitted to The Company by the User in respect of the proposed new Connection Point and Interface Point:

(a)	updated Planning Code data (Standard Planning Data, Detailed Planning Data and OTSDUW Data and Information), with any estimated values assumed for planning purposes confirmed or, where practical, replaced by validated actual values and by updated estimates for the future and by updated forecasts for Forecast Data items such as Demand, pursuant to the requirements of the Planning Code;

(b)	details of the Protection arrangements and settings referred to in ECC.6;

(c)	information to enable preparation of the Site Responsibility Schedules at the Transmission Interface Site on the basis of the provisions set out in Appendix E1.

(d) 	the proposed name of the Interface Point (which shall not be the same as, or confusingly similar to, the name of any Transmission Site or of any other User Site);

ECC.5.3	(a)	Of the items ECC.5.2.1 (c), (e), (g), (h), (k) and (m) need not be supplied in respect of Embedded Power Stations or Embedded HVDC Systems,

(b)	item ECC.5.2.1(i) need not be supplied in respect of Embedded Small Power Stations and Embedded Medium Power Stations or Embedded HVDC Systems with a Registered Capacity of less than 100MW, and

(c) 	items ECC.5.2.1(d) and (j) are only needed in the case where the Embedded Power Station or the Embedded HVDC System is within a Connection Site with another User.

ECC.6	TECHNICAL, DESIGN AND OPERATIONAL CRITERIA

ECC.6.1	National Electricity Transmission System Performance Characteristics

ECC.6.1.1	The Company shall ensure that, subject as provided in the Grid Code, the National Electricity Transmission System complies with the following technical, design and operational criteria in relation to the part of the National Electricity Transmission System at the Connection Site with a User and in the case of OTSDUW Plant and Apparatus, a Transmission Interface Point (unless otherwise specified in ECC.6) although in relation to operational criteria The Company may be unable (and will not be required) to comply with this obligation to the extent that there are insufficient Power Stations or User Systems are not available or Users do not comply with The Company's instructions or otherwise do not comply with the Grid Code and each User shall ensure that its Plant and Apparatus complies with the criteria set out in ECC.6.1.5.

ECC.6.1.2	Grid Frequency Variations

ECC.6.1.2.1	Grid Frequency Variations

ECC.6.1.2.1.1	The Frequency of the National Electricity Transmission System shall be nominally 50Hz and shall be controlled within the limits of 49.5 - 50.5Hz unless exceptional circumstances prevail, for example but not limited to, situations such as during System Restoration.

ECC.6.1.2.1.2	The System Frequency could rise to 52Hz or fall to 47Hz in exceptional circumstances. Design of User's Plant and Apparatus and OTSDUW Plant and Apparatus must enable operation of that Plant and Apparatus within that range in accordance with the following:

| Frequency Range | Requirement |
| --- | --- |
| 51.5Hz - 52Hz | Operation for a period of at least 15 minutes is required each time the Frequency is above 51.5Hz. |
| 51Hz - 51.5Hz | Operation for a period of at least 90 minutes is required each time the Frequency is above 51Hz. |
| 49.0Hz - 51Hz | Continuous operation is required |
| 47.5Hz - 49.0Hz | Operation for a period of at least 90 minutes is required each time the Frequency is below 49.0Hz. |
| 47Hz - 47.5Hz | Operation for a period of at least 20 seconds is required each time the Frequency is below 47.5Hz. |

ECC.6.1.2.1.3	For the avoidance of doubt, disconnection, by frequency or speed based relays is not permitted within the frequency range 47.5Hz to 51.5Hz. EU Generators should however be aware of the combined voltage and frequency operating ranges as defined in ECC.6.3.12 and ECC.6.3.13.

ECC.6.1.2.1.4	The Company in co-ordination with the Relevant Transmission Licensee and/or Network Operator and a User may agree on wider variations in frequency or longer minimum operating times to those set out in ECC.6.1.2.1.2 or specific requirements for combined frequency and voltage deviations, for example but not limited to, situations such as during System Restoration.  Any such requirements in relation to Power Generating Modules shall be in accordance with ECC.6.3.12 and ECC.6.3.13.  A User shall not unreasonably withhold consent to apply wider frequency ranges or longer minimum times for operation taking account of their economic and technical feasibility.

ECC.6.1.2.2	Grid Frequency variations for HVDC Systems  and Remote End HVDC Converter Stations

ECC.6.1.2.2.1	HVDC Systems and Remote End HVDC Converter Stations shall be capable of staying connected to the System and remaining operable within the frequency ranges and time periods specified in Table ECC.6.1.2.2 below.  This requirement shall continue to apply during the Fault Ride Through conditions defined in ECC.6.3.15

| Frequency Range (Hz) | Time Period for Operation (s) |
| --- | --- |
| 47.0 – 47.5Hz | 60 seconds |
| 47.5 – 49.0Hz | 90 minutes and 30 seconds |
| 49.0 – 51.0Hz | Unlimited |
| 51.0 – 51.5Hz | 90 minutes and 30 seconds |
| 51.5Hz – 52 Hz | 20 minutes |

Table ECC.6.1.2.2 – Minimum time periods HVDC Systems  and Remote End HVDC Converter Stations shall be able to operate for different frequencies deviating from a nominal value without disconnecting from the National Electricity Transmission System

ECC.6.1.2.2.2	The Company in coordination with the Relevant Transmission Licensee and a HVDC System Owner may agree wider frequency ranges or longer minimum operating times if required to preserve or restore system security, for example but not limited to, situations such as during System Restoration.    If wider frequency ranges or longer minimum times for operation are economically and technically feasible, the HVDC System Owner shall not unreasonably withhold consent.

ECC.6.1.2.2.3	Not withstanding the requirements of ECC.6.1.2.2.1, an HVDC System or Remote End HVDC Converter Station shall be capable of automatic disconnection at frequencies specified by The Company and/or Relevant Network Operator.

ECC.6.1.2.2.4	In the case of Remote End HVDC Converter Stations where the Remote End HVDC Converter Station is operating at either nominal frequency other than 50Hz or a variable frequency, the requirements defined in ECC6.1.2.2.1 to ECC.6.1.2.2.3 shall apply to the Remote End HVDC Converter Station other than in respect of the frequency ranges and time periods.

ECC.6.1.2.3	Grid Frequency Variations for DC Connected Power Park Modules

ECC.6.1.2.3.1	DC Connected Power Park Modules shall be capable of staying connected to the Remote End DC Converter network at the HVDC Interface Point and operating within the Frequency ranges and time periods specified in Table ECC.6.1.2.3 below.  Where a nominal frequency other than 50Hz, or a Frequency variable by design is used as agreed with The Company and the Relevant Transmission Licensee the applicable Frequency ranges and time periods shall be specified in the Bilateral Agreement which shall (where applicable) reflect the requirements in Table ECC.6.1.2.3 .

| Frequency Range (Hz) | Time Period for Operation (s) |
| --- | --- |
| 47.0 – 47.5Hz | 20 seconds |
| 47.5 – 49.0Hz | 90 minutes |
| 49.0 – 51.0Hz | Unlimited |
| 51.0 – 51.5Hz | 90 minutes |
| 51.5Hz – 52 Hz | 15 minutes |

Table ECC.6.1.2.3 – Minimum time periods a DC Connected Power Park Module  shall be able to operate for different frequencies deviating from a nominal value without disconnecting from the System

ECC.6.1.2.3.2	The Company in coordination with the Relevant Transmission Licensee and a Generator may agree wider frequency ranges or longer minimum operating times  if required to preserve or restore system security and to ensure the optimum capability of the DC Connected Power Park Module, for example but not limited to, situations such as during System Restoration.   If wider frequency ranges or longer minimum times for operation are economically and technically feasible, the EU Generator  shall not unreasonably withhold consent.

ECC.6.1.3	Not used

ECC.6.1.4	Grid Voltage Variations

ECC.6.1.4.1	Grid Voltage Variations for Users excluding DC Connected Power Park Modules and Remote End HVDC Converters

The voltage on part of the National Electricity Transmission System operating at nominal voltages of greater than 300kV at each Connection Site with a User (and in the case of OTSDUW Plant and Apparatus, a Transmission Interface Point, excluding DC Connected Power Park Modules and Remote End HVDC Converters) will normally remain within 5% of the nominal value unless abnormal conditions prevail. The minimum voltage is -10% and the maximum voltage is +10% unless abnormal conditions prevail, for example, but not limited to, situations such as during System Restoration, but voltages between +5% and +10% will not last longer than 15 minutes unless abnormal conditions prevail. For nominal voltages of 110kV and up to and including 300kV voltages on the parts of the National Electricity Transmission System at each Connection Point (and in the case of OTSDUW Plant and Apparatus, a Transmission Interface Point) will normally remain within the limits 10% of the nominal value unless abnormal conditions prevail for example, but not limited to, situations such as during System Restoration.  At nominal System voltages below 110kV the voltage of the National Electricity Transmission System at each Connection Site with a User (and in the case of OTSDUW Plant and Apparatus, a Transmission Interface Point), excluding Connection Sites for DC Connected Power Park Modules and Remote End HVDC Converters) will normally remain within the limits 6% of the nominal value unless abnormal conditions prevail for example but not limited to, situations such as during System Restoration.  Under fault conditions, the voltage may collapse transiently to zero at the point of fault until the fault is cleared.  The normal operating ranges of the National Electricity Transmission System are summarised below:

| National Electricity Transmission System Nominal Voltage | Normal Operating Range |  | Time period for Operation |
| --- | --- | --- | --- |
|  | Voltage (percentage of Nominal Voltage) | Pu (1pu relates to the Nominal Voltage) |  |
| Greater than 300kV | V -10% to +5% V +5% to +10% | 0.90pu- 1.05pu 1.05pu- 1.10pu | Unlimited 15 minutes |
| 110kV up to 300kV | V 10% | 0.90- 1.10pu | Unlimited |
| Below 110kV | ±6% | 0.94pu- 1.06pu | Unlimited |

The Company and a User may agree greater variations or longer minimum time periods of operation in voltage to those set out above in relation to a particular Connection Site, and insofar as a greater variation is agreed, the relevant figure set out above shall, in relation to that User at the particular Connection Site, be replaced by the figure agreed.

ECC.6.1.4.2	Grid Voltage Variations for all DC Connected Power Park Modules

ECC.6.1.4.2.1	All DC Connected Power Park Modules shall be capable of staying connected to the Remote End HVDC Converter Station at the HVDC Interface Point  and operating within the voltage ranges and time periods specified in Tables ECC.6.1.4.2(a) and ECC.6.1.4.2(b) below. The applicable voltage range and time periods specified are selected based on the reference 1pu voltage.

| Voltage Range (pu) | Time Period for Operation (s) |
| --- | --- |
| 0.85pu – 0.9pu | 60 minutes |
| 0.9pu – 1.1pu | Unlimited |
| 1.1pu – 1.15pu | 15 minutes |

Table ECC.6.1.4.2(a) – Minimum time periods for which DC Connected Power Park Modules shall be capable of operating for different voltages deviating from reference 1pu without disconnecting from the network where the nominal voltage base is 110kV or above and less than 300kV.

| Voltage Range (pu) | Time Period for Operation (s) |
| --- | --- |
| 0.85pu – 0.9pu | 60 minutes |
| 0.9pu – 1.05pu | Unlimited |
| 1.05pu – 1.15pu | 15 minutes |

Table ECC.6.1.4.2(b) – Minimum time periods for which DC Connected Power Park Modules shall be capable of operating for different voltages deviating from reference 1pu without disconnecting from the network where the nominal voltage base is from 300kV up to and including 400kV.

ECC.6.1.4.2.2	The Company and a EU Generator in respect of a DC Connected Power Park Module may agree greater voltage ranges or longer minimum operating times.   If  greater voltage ranges or longer minimum times for operation are economically and technically feasible, the EU Generator shall not unreasonably withhold any agreement .

ECC.6.1.4.2.3	For DC Connected Power Park Modules which have an HVDC Interface Point to the Remote End HVDC Converter Station, The Company in coordination with the Relevant Transmission Licensee may specify voltage limits at the HVDC Interface Point at which the DC Connected Power Park Module is capable of automatic disconnection.

ECC.6.1.4.2.4	For HVDC Interface Points which fall outside the scope of  ECC.6.1.4.2.1, ECC.6.1.4.2.2 and ECC.6.1.4.2.3, The Company in coordination with the Relevant Transmission Licensee shall specify any applicable requirements at the Grid Entry Point or User System Entry Point.

ECC.6.1.4.2.5	Where the nominal frequency of the AC collector System which is connected to an HVDC Interface Point is at a value other than 50Hz, the voltage ranges and time periods specified by The Company in coordination with the Relevant Transmission Licensee shall be proportional to the values specified in Table ECC.6.1.4.2(a) and Table ECC.6.1.4.2(b)

ECC.6.1.4.3	Grid Voltage Variations for all Remote End HVDC Converters

ECC.6.1.4.3.1	All Remote End HVDC Converter Stations shall be capable of staying connected to the HVDC Interface Point and operating within the voltage ranges and time periods specified in Tables ECC.6.1.4.3(a) and ECC.6.1.4.3(b) below. The applicable voltage range and time periods specified are selected based on the reference 1pu voltage.

| Voltage Range (pu) | Time Period for Operation (s) |
| --- | --- |
| 0.85pu – 0.9pu | 60 minutes |
| 0.9pu – 1.1pu | Unlimited |
| 1.1pu – 1.15pu | 15 minutes |

Table ECC.6.1.4.3(a) – Minimum time periods for which a Remote End HVDC Converter shall be capable of operating for different voltages deviating from reference 1pu without disconnecting from the network where the nominal voltage base is 110kV or above and less than 300kV.

| Voltage Range (pu) | Time Period for Operation (s) |
| --- | --- |
| 0.85pu – 0.9pu | 60 minutes |
| 0.9pu – 1.05pu | Unlimited |
| 1.05pu – 1.15pu | 15 minutes |

Table ECC.6.1.4.3(b) – Minimum time periods for which a Remote End HVDC Converter shall be capable of operating for different voltages deviating from reference 1pu without disconnecting from the network where the nominal voltage base is from 300kV up to and including 400kV.

ECC.6.1.4.3.2	The Company and a HVDC System Owner may agree greater voltage ranges or longer minimum operating times which shall be in accordance with the requirements of ECC.6.1.4.2.

ECC.6.1.4.3.4	For HVDC Interface Points which fall outside the scope of ECC.6.1.4.3.1 The Company in coordination with the Relevant Transmission Licensee shall specify any applicable requirements at the Grid Entry Point or User System Entry Point.

ECC.6.1.4.3.5	Where the nominal frequency of the AC collector System which is connected to an HVDC Interface Point is at a value other than 50Hz, the voltage ranges and time periods specified by The Company in coordination with the Relevant Transmission Licensee shall be proportional to the values specified in Table ECC.6.1.4.3(a) and Table ECC.6.1.4.3(b)

Voltage Waveform Quality

ECC.6.1.5	All Plant and Apparatus connected to the National Electricity Transmission System, and that part of the National Electricity Transmission System at each Connection Site or, in the case of OTSDUW Plant and Apparatus, at each Interface Point, should be capable of withstanding the following distortions of the voltage waveform in respect of harmonic content and phase unbalance:

(a)	Harmonic Content

The Electromagnetic Compatibility Levels for harmonic distortion on the Onshore Transmission System from all sources under both Planned Outage and fault outage conditions, (unless abnormal conditions prevail) shall comply with  Engineering Recommendation G5. The Electromagnetic Compatibility Levels for harmonic distortion on an Offshore Transmission System will be defined in relevant Bilateral Agreements.

Engineering Recommendation G5 contains planning criteria which The Company will apply to the connection of non-linear Load to the National Electricity Transmission System, which may result in harmonic emission limits being specified for these Loads in the relevant Bilateral Agreement.  The application of the planning criteria will take into account the position of existing GB Code User’s and EU Code Users’ Plant and Apparatus (and OTSDUW Plant and Apparatus) in relation to harmonic emissions.  EU Code Users must ensure that connection of distorting loads to their User Systems do not cause any harmonic emission limits specified in the Bilateral Agreement, or where no such limits are specified, the relevant planning levels specified in Engineering Recommendation G5 to be exceeded.

(b)	Phase Unbalance

Under Planned Outage conditions, the weekly 95 percentile of Phase (Voltage) Unbalance, calculated in accordance with IEC 61000-4-30 and IEC 61000-3-13, on the National Electricity Transmission System for voltages above 150kV should remain, in England and Wales, below 1.5%, and in Scotland, below 2%, and for voltages of 150kV and below, across GB below 2%, unless abnormal conditions prevail and Offshore (or in the case of OTSDUW, OTSDUW Plant and Apparatus) will be defined in relevant Bilateral Agreements.

The Phase Unbalance is calculated from the ratio of root mean square (rms) of negative phase sequence voltage to rms of positive phase sequence voltage, based on 10-minute average values, in accordance with IEC 61000-4-30.

ECC.6.1.6	Across GB, under the Planned Outage conditions stated in ECC.6.1.5(b) infrequent short duration peaks with a maximum value of 2% are permitted for Phase (Voltage) Unbalance, for voltages above 150kV, subject to the prior agreement of The Company under the Bilateral Agreement and in relation to OTSDUW, the Construction Agreement.  The Company will only agree following a specific assessment of the impact of these levels on Transmission Apparatus and other Users Apparatus with which it is satisfied.

Voltage Fluctuations

ECC.6.1.7	Voltage changes at a Point of Common Coupling on the Onshore Transmission System shall not exceed:

- The limits specified in Table ECC.6.1.7(a) with the stated frequency of occurrence, where:

## (i)

| %Vsteadystate = │100 x | Vsteadystate | │ |
| --- | --- | --- |
|  | Vn |  |

and

| %Vmax =100 x | Vmax | ; |
| --- | --- | --- |
|  | Vn |  |

## (ii)	Vn is the nominal system voltage;

(iii)	Vsteadystate is the voltage at the end of a period of 1 s during which the rate of change of system voltage over time is ≤ 0.5%;

(iv)	Vsteadystate is the difference in voltage between the initial steady state voltage prior to the RVC (V0) and the final steady state voltage after the RVC (V0’);

(v)	Vmax is the absolute change in the system voltage relative to the initial steady state system voltage (V0);

(vi)	All voltages are the r.m.s. of the voltage measured over one cycle refreshed every half a cycle as per BS EN 61000-4-30; and

(vii)   The applications in the ‘Example Applicability’ column are examples only and are not definitive.

| Cat-egory | Title | Maximum number of occurrence | Limits %Vmax & %Vsteadystate | Example Applicability |
| --- | --- | --- | --- | --- |
| 1 | Frequent events | (see NOTE 1) | As per Figure ECC.6.1.7 (1) | Any single or repetitive RVC that falls inside Figure ECC.6.1.7 (1) |
| 2 | Infrequent events | 4 events in 1 calendar month (see NOTE 2) | As per Figure ECC.6.1.7 (2) │%Vsteadystate │≤ 3% For decrease in voltage: │%Vmax │≤ 10% (see NOTE 3) For increase in voltage: │%Vmax │≤ 6% (see NOTE 4) | Infrequent motor starting, transformer energisation, re-energisation (see NOTE 7) |
| 3 | Very infrequent events | 1 event in 3 calendar months (see NOTE 2) | As per Figure ECC.6.1.7 (3) │%Vsteadystate │≤ 3% For decrease in voltage: │%Vmax │≤ 12% (see NOTE 5) For increase in voltage: │%Vmax │≤ 6% (see NOTE 6) | Commissioning, maintenance & post fault switching (see NOTE 7) |
| NOTE 1: 6% is permissible for 100 ms reduced to 3% thereafter as per Figure ECC.6.1.7 (1) . If the profile of repetitive voltage change(s) falls within the envelope given in Figure ECC.6.1.7 (1) , the assessment of such voltage change(s) shall be undertaken according to the recommendations for assessment of flicker and shall conform to the planning levels provided for flicker. If any part of the voltage change(s) falls outside the envelope given in Figure ECC.6.1.7(1), the assessment of such voltage changes, repetitive or not, shall be done according to the guidance and limits for RVCs. NOTE 2: No more than 1 event is permitted per day, consisting of up to 4 RVCs, each separated by at least 10 minutes with all switching completed within a two-hour window. NOTE 3: −10% is permissible for 100 ms reduced to -6% until 2 s then reduced to -3% thereafter as per Figure ECC.6.1.7 (2). NOTE 4: +6% is permissible for 0.8 s from the instant the event begins then reduced to +3% thereafter as per Figure ECC.6.1.7 (2). NOTE 5: −12% is permissible for 100 ms reduced to −10% until 2 s then reduced to -3% thereafter as per Figure ECC.6.1.7 (3). NOTE 6: +6% is permissible for 0.8 s from the instant the event begins then reduced to +3% thereafter as per Figure ECC.6.1.7 (3). NOTE 7: These are examples only. Customers may opt to conform to the limits of another category providing the frequency of occurrence is not expected to exceed the ‘Maximum number of occurrence’ for the chosen category. |  |  |  |  |

Table ECC.6.1.7 (a) – Planning levels for RVC

- The voltage change limit is the absolute maximum allowed of either the phase-to-earth voltage change or the phase-to-phase voltage change, whichever is the highest. The limits do not apply to single phasor equivalent voltages, e.g. positive phase sequence (PPS) voltages. For high impedance earthed systems, the maximum phase-to-phase, i.e. line voltage, should be used for assessment.

- The RVCs in Category 2 and 3 should not exceed the limits depicted in the time dependent characteristic shown in Figure ECC.6.1.7 (2) and Figure ECC.6.1.7 (3)   respectively. These limits do not apply to: 1) fault clearance operations; or 2) immediate operations in response to fault conditions; or 3) operations relating to post fault system restoration (for the avoidance of doubt this third exception pertains to a fault that is external to the Users plant and apparatus).

- Any RVCs permitted in Category 2 and Category 3 should be at least 10 minutes apart.

- The value of Vsteadystate should be established immediately prior to the start of a RVC. Following a RVC, the voltage should remain within the relevant envelope, as shown in Figures ECC.6.1.7 (1), ECC.6.1.7 (2), ECC.6.1.7 (3), until a Vsteadystate condition has been satisfied.

Figure ECC.6.1.7 (1) — Voltage characteristic for frequent events

t

V0

V0+6%

V0+3%

V0−3%

V0−6%

100 ms

t=0

0.8 s

2 s

V0−10%

Figure ECC.6.1.7 (2) — Voltage characteristic for infrequent events

t

V0

V0+6%

100 ms

t=0

0.8 s

2 s

V0+3%

V0−3%

V0−10%

V0−12%

Figure ECC.6.1.7 (3) — Voltage characteristic for very infrequent events

- The voltage change between two steady state voltage conditions should not exceed 3%. (The limit is based on 3% of the nominal voltage of the system (Vn) as measured at the PCC. The step voltage change as measured at the customer’s supply terminals or equipment terminals could be greater. For example: The step voltage change limit stated in BS EN 61000-3-3 and BS EN 61000-3-11 is 3.3% when measured at the equipment terminals.)

- The limits apply to voltage changes measured at the Point of Common Coupling.

- Category 3 events that are planned should be notified to the Company in advance.

- For connections where voltage changes would constitute a risk to the National Electricity Transmission System or, in The Company’s view, the System of any GB Code User, Bilateral Agreements may include provision for The Company to reasonably limit the number of voltage changes in Category 2 or 3 to a lower number than specified in Table ECC.6.1.7(a) to ensure that the total number of voltage changes at the Point of Common Coupling across multiple Users remains within the limits of Table ECC.6.1.7(a).

- The planning levels applicable to Flicker Severity Short Term (Pst) and Flicker Severity Long Term (Plt) are set out in Table ECC.6.1.7(b).

| Supply system Nominal voltage | Planning level |  |
| --- | --- | --- |
|  | Flicker Severity Short Term (Pst) | Flicker Severity Long Term (Plt) |
| Up to and including 33 kV | 0.9 | 0.7 |
| 66kV and greater | 0.8 | 0.6 |
| NOTE 1: The magnitude of Pst is linear with respect to the magnitude of the voltage changes giving rise to it. NOTE 2: Extreme caution is advised in allowing any excursions of Pst and Plt above the planning level. |  |  |

Table ECC.6.7.1(b) — Planning levels for flicker

The values and figures referred to in this paragraph ECC.6.1.7 are derived from Engineering Recommendation  P28 Issue 2.

ECC.6.1.8	Voltage fluctuations at a Point of Common Coupling with a fluctuating Load directly connected to an Offshore Transmission System (or in the case of OTSDUW, OTSDUW Plant and Apparatus) shall not exceed the limits set out in the Bilateral Agreement.

Sub-Synchronous Resonance and Sub-Synchronous Torsional Interaction (SSTI)

ECC.6.1.9	The Company shall ensure that Users' Plant and Apparatus will not be subject to unacceptable Sub-Synchronous Oscillation conditions as specified in the relevant License Standards.

ECC.6.1.10	The Company shall ensure where necessary, and in consultation with Relevant Transmission Licensees where required, that any relevant site specific conditions applicable at a User's Connection Site, including a description of the Sub-Synchronous Oscillation conditions considered in the application of the relevant License Standards, are set out in the User's Bilateral Agreement.

.

ECC.6.2	Plant and Apparatus relating to Connection Sites and Interface Points and HVDC Interface Points

The following requirements apply to Plant and Apparatus relating to the Connection Point and OTSDUW Plant and Apparatus relating to the Interface Point (until the OTSUA Transfer Time), HVDC Interface Points relating to Remote End HVDC Converters and Connection Points which (except as otherwise provided in the relevant paragraph) each EU Code User must ensure are complied with in relation to its Plant and Apparatus and which in the case of ECC.6.2.2.2.2, ECC.6.2.3.1.1 and ECC.6.2.1.1(b) only, The Company must ensure are complied with in relation to Transmission  Plant and Apparatus, as provided in those paragraphs.

ECC.6.2.1	General Requirements

ECC.6.2.1.1	(a)	The design of connections between the National Electricity Transmission System and:

(i)	any Power Generating Module Generating Unit (other than a CCGT Unit or Power Park Unit) HVDC Equipment, Power Park Module or CCGT Module, or

(ii)	any Network Operator’s User System, or

(iii) 	Non-Embedded Customers equipment;

will be consistent with the Licence Standards.

In the case of OTSDUW, the design of the OTSUA’s connections at the Interface Point and Connection Point will be consistent with Licence Standards.

(b)	The National Electricity Transmission System (and any OTSDUW Plant and Apparatus) at nominal System voltages of 132kV and above is/shall be designed to be earthed with an Earth Fault Factor of, in England and Wales or Offshore, below 1.4 and in Scotland, below 1.5. Under fault conditions the rated Frequency component of voltage could fall transiently to zero on one or more phases or, in England and Wales, rise to 140% phase-to-earth voltage, or in Scotland, rise to 150% phase-to-earth voltage.  The voltage rise would last only for the time that the fault conditions exist.  The fault conditions referred to here are those existing when the type of fault is single or two phase-to-earth.

(c)	For connections to the National Electricity Transmission System at nominal System voltages of below 132kV the earthing requirements and voltage rise conditions will be advised by The Company as soon as practicable prior to connection and in the case of OTSDUW Plant and Apparatus shall be advised to The Company by the EU Code User.

ECC.6.2.1.2	Substation Plant and Apparatus

(a)	The following provisions shall apply to all Plant and Apparatus which is connected at the voltage of the Connection Point (and OTSDUW Plant and Apparatus at the Interface Point ) and which is contained in equipment bays that are within the Transmission busbar Protection zone at the Connection Point.  This includes circuit breakers, switch disconnectors, disconnectors, Earthing Devices, power transformers, voltage transformers, reactors, current transformers, surge arresters, bushings, neutral equipment, capacitors, line traps, coupling devices, external insulation and insulation co-ordination devices.  Where necessary, this is as more precisely defined in the Bilateral Agreement.

(i)	Plant and/or Apparatus in respect of EU Code Users connecting to a new Connection Point (including OTSDUW Plant and Apparatus at the Interface Point )

Each item of such Plant and/or Apparatus installed in relation to a new Connection Point (or OTSDUW Plant and Apparatus at the Interface Point or Remote End HVDC Converter Station at the HVDC Interface Point)  shall comply with the relevant Technical Specifications and any further requirements identified by The Company, acting reasonably, to reflect the options to be followed within the Technical Specifications and/or to complement if necessary the Technical Specifications so as to enable The Company to comply with its obligations in relation to the National Electricity Transmission System or the Relevant Transmission Licensee to comply with its obligations in relation to its Transmission System. This information, including the application dates of the relevant Technical Specifications, will be as specified in the Bilateral Agreement.

(ii)	EU Code User’s Plant and/or Apparatus connecting to an existing Connection Point (including OTSDUW Plant and Apparatus at the Interface Point )

Each new additional and/or replacement item of such Plant and/or Apparatus installed in relation to a change to an existing Connection Point (or OTSDUW Plant and Apparatus at the Interface Point  and Connection Point or Remote End HVDC Converter Stations at the HVDC Interface Point) shall comply with the standards/specifications applicable when the change was designed, or such other standards/specifications as necessary to ensure that the item of Plant and/or Apparatus is reasonably fit for its intended purpose having due regard to the obligations of The Company, the relevant User the Relevant Transmission Licensee under their respective Licences.  Where appropriate this information, including the application dates of the relevant standards/specifications, will be as specified in the varied Bilateral Agreement.

(iii)	Used Plant and/or Apparatus being moved, re-used or modified

If, after its installation, any such item of Plant and/or Apparatus is subsequently:

moved to a new location; or

used for a different purpose; or

otherwise modified;

then the standards/specifications as described in (i) or (ii) above as applicable will apply as appropriate to such Plant and/or Apparatus, which must be reasonably fit for its intended purpose having due regard to the obligations of The Company, the relevant User and the Relevant Transmission Licensee under their respective Licences.

(b)	The Company shall at all times maintain a list of those Technical Specifications and additional requirements which might be applicable under this ECC.6.2.1.2 and which may be referenced by The Company in the Bilateral Agreement. The Company shall provide a copy of the list upon request to any  EU Code User. The Company shall also provide a copy of the list to any EU Code User  upon receipt of an application form for a Bilateral Agreement for a new Connection Point.

(c)	Where the EU Code User  provides The Company with information and/or test reports in respect of Plant and/or Apparatus which the EU Code User  reasonably believes demonstrate the compliance of such items with the provisions of a Technical Specification then The Company shall promptly and without unreasonable delay give due and proper consideration to such information.

(d)	Plant and Apparatus shall be designed, manufactured and tested in premises with an accredited certificate in accordance with the quality assurance requirements of the relevant standard in the BS EN ISO 9000 series (or equivalent as reasonably approved by The Company) or in respect of test premises which do not include a manufacturing facility premises with an accredited certificate in accordance with BS EN 45001.

(e)	Each connection between a  User  and the National Electricity Transmission System must be controlled by a circuit-breaker (or circuit breakers) capable of interrupting the maximum short circuit current at the point of connection.  The Seven Year Statement gives values of short circuit current and the rating of Transmission circuit breakers at existing and committed Connection Points for future years.

(f)	Each connection between a Generator undertaking OTSDUW or an Onshore Transmission Licensee, must be controlled by a circuit breaker (or circuit breakers) capable of interrupting the maximum short circuit current at the Transmission Interface Point.  The Seven Year Statement gives values of short circuit current and the rating of Transmission circuit breakers at existing and committed Transmission Interface Points for future years.

ECC.6.2.2	Requirements at Connection Points or, in the case of OTSDUW at Interface Points that relate to Generators or OTSDUW Plant and Apparatus

ECC.6.2.2.1	Not Used.

ECC.6.2.2.2	Power Generating Module, OTSDUW Plant and Apparatus, HVDC Equipment and Power Station Protection Arrangements

ECC.6.2.2.2.1	Minimum Requirements

ECC.6.2.2.2.1.1	Protection of Power Generating Modules (other than Power Park Units), HVDC Equipment, OTSDUW Plant and Apparatus and their connections to the National Electricity Transmission System shall meet the requirements given below. These are necessary to reduce the impact on the National Electricity Transmission System of faults on OTSDUW Plant and Apparatus circuits or circuits owned by Generators (including DC Connected Power Park Modules) or HVDC System Owners.

ECC.6.2.2.2.1.2 Restoration Contractors shall, if required by a Restoration Plan, have the ability to switch:-

- From the normal to the alternative Protection settings on their Plant and Apparatus and:-

- From the alternative to the normal Protection settings whilst their Plant remains in service.

Any alternative Protection settings shall be included in the Restoration Plan.  Normal and alternative Protection settings shall be agreed between The Company and/or Relevant Transmission Licensee and/or Network Operator as part of developing a Restoration Plan.

ECC.6.2.2.2.2	Fault Clearance Times

(a)	The required fault clearance time for faults on the Generator's (including DC Connected Power Park Modules) or HVDC System Owner’s equipment directly connected to the National Electricity Transmission System or OTSDUW Plant and Apparatus and for faults on the National Electricity Transmission System directly connected to the EU Generator (including DC Connected Power Park Modules) or HVDC System Owner's equipment or OTSDUW Plant and Apparatus, from fault inception to the circuit breaker arc extinction, shall be set out in the Bilateral Agreement.  The fault clearance time specified in the Bilateral Agreement shall not be shorter than the durations specified in (i), (ii) and (iii) below:

(i)	80ms for connections operating at a nominal voltage of greater than 300kV

(ii)	100ms for connections operating at a nominal voltage of greater than 132kV and up to 300kV

(iii)	120ms for connections operating at a nominal voltage of 132kV and below

but this shall not prevent the User or The Company or the Relevant Transmission Licensee or the EU Generator (including in respect of OTSDUW Plant and Apparatus and DC Connected Power Park Modules) from selecting a shorter fault clearance time on their own Plant and Apparatus provided Discrimination is achieved.

A longer fault clearance time may be specified in the Bilateral Agreement for faults on the National Electricity Transmission System. A longer fault clearance time for faults on the EU Generator or HVDC System Owner's equipment or OTSDUW Plant and Apparatus may be agreed with The Company in accordance with the terms of the Bilateral Agreement but only if System requirements, in The Company's view, permit.  The probability that the fault clearance time stated in the Bilateral Agreement will be exceeded by any given fault, must be less than 2%.

(b)	In the event that the required fault clearance time is not met as a result of failure to operate on the Main Protection System(s) provided, the Generators or HVDC System Owners or Generators in the case of OTSDUW Plant and Apparatus shall, except as specified below provide Independent Back-Up Protection.  The Relevant Transmission Licensee will also provide Back-Up Protection and the Relevant Transmission Licensee’s and the User’s Back-Up Protections will be co-ordinated so as to provide Discrimination.

On a Power Generating Module (other than a Power Park Unit), HVDC Equipment or OTSDUW Plant and Apparatus and connected to the National Electricity Transmission System operating at a nominal voltage of greater than 132kV and where two Independent Main Protections are provided to clear faults on the HV Connections within the required fault clearance time, the Back-Up Protection provided by EU Generators (including in respect of OTSDUW Plant and Apparatus and DC Connected Power Park Modules) and HVDC  System Owners shall operate to give a fault clearance time of no longer than 300ms at the minimum infeed for normal operation for faults on the HV Connections.  Where two Independent Main Protections are installed the Back-Up Protection may be integrated into one (or both) of the Independent Main Protection relays.

On a Power Generating Module (other than a Power Park Unit), HVDC Equipment or OTSDUW Plant and Apparatus and connected to the National Electricity Transmission System at 132 kV and below and where only one Main Protection is provided to clear faults on the HV Connections within the required fault clearance time, the Independent Back-Up Protection provided by the Generator (including in respect of OTSDUW Plant and Apparatus and DC Connected Power Park Modules) and the HVDC System Owner shall operate to give a fault clearance time of no longer than 300ms at the minimum infeed for normal operation for faults on the HV Connections.

A Power Generating Module (other than a Power Park Unit), HVDC Equipment or OTSDUW Plant and Apparatus) with Back-Up Protection or Independent Back-Up Protection will also be required to withstand, without tripping, the loading incurred during the clearance of a fault on the National Electricity Transmission System by breaker fail Protection at a nominal voltage of greater than 132kV or of a fault cleared by Back-Up Protection where the EU Generator (including in the case of OTSDUW Plant and Apparatus or DC Connected Power Park Module) or HVDC System is connected at 132kV and below.  This will permit Discrimination between the Generator in respect of OTSDUW Plant and Apparatus or DC Connected Power Park Modules or HVDC System Owners’ Back-Up Protection or Independent Back-Up Protection and the Back-Up Protection provided on the National Electricity Transmission System and other Users' Systems.

(c)	When the Power Generating Module (other than Power Park Units), or the HVDC Equipment or OTSDUW Plant and Apparatus is connected to the National Electricity Transmission System operating at a nominal voltage of greater than 132kV, and in Scotland and Offshore also at 132kV, and a circuit breaker is provided by the Generator (including in respect of OTSDUW Plant and Apparatus or DC Connected Power Park Modules) or the HVDC System owner, or the Relevant Transmission Licensee, as the case may be, to interrupt fault current interchange with the National Electricity Transmission System, or Generator's System, or HVDC System Owner’s System, as the case may be, circuit breaker fail Protection shall be provided by the Generator (including in respect of OTSDUW Plant and Apparatus or DC Connected Power Park Modules) or HVDC System Owner, or the Relevant Transmission Licensee, as the case may be, on this circuit breaker.  In the event, following operation of a Protection system, of a failure to interrupt fault current by these circuit-breakers within the Fault Current Interruption Time, the circuit breaker fail Protection is required to initiate tripping of all the necessary electrically adjacent circuit-breakers so as to interrupt the fault current within the next 200ms.

(d)	The target performance for the System Fault Dependability Index shall be not less than 99%.  This is a measure of the ability of Protection to initiate successful tripping of circuit breakers which are associated with the faulty item of Apparatus.

ECC.6.2.2.3	Equipment including Protection equipment to be provided

The Relevant Transmission Licensee shall specify the Protection schemes and settings necessary to protect the National Electricity Transmission System, taking into account the characteristics of the Power Generating Module or HVDC Equipment.

The protection schemes needed for the Power Generating Module or HVDC Equipment and the National Electricity Transmission System as well as the settings relevant to the Power Generating Module and/or HVDC Equipment shall be coordinated and agreed between The Company and the EU Generator or HVDC System Owner.  The agreed Protection schemes and settings will be specified in the Bilateral Agreement.

The protection schemes and settings for internal electrical faults must not prevent the Power Generating Module or HVDC Equipment from satisfying the requirements of the Grid Code although EU Generators should be aware of the requirements of ECC.6.3.13.1. ;

electrical Protection of the Power Generating Module or HVDC Equipment shall take precedence over operational controls, taking into account the security of the National Electricity Transmission System and the health and safety of personnel, as well as mitigating any damage to the Power Generating Module or HVDC Equipment.

ECC.6.2.2.3.1	Protection of Interconnecting Connections

The requirements for the provision of Protection equipment for interconnecting connections will be specified in the Bilateral Agreement.  In this ECC the term "interconnecting connections" means the primary conductors from the current transformer accommodation on the circuit side of the circuit breaker to the Connection Point or the primary conductors from the current transformer accommodation on the circuit side of the OTSDUW Plant and Apparatus of the circuit breaker to the Transmission Interface Point.

ECC.6.2.2.3.2	Circuit-breaker fail Protection

The EU Generator or HVDC System Owner will install circuit breaker fail Protection equipment in accordance with the requirements of the Bilateral Agreement.  The EU Generator or HVDC System Owner will also provide a back-trip signal in the event of loss of air from its pressurised head circuit breakers, during the Power Generating Module (other than a CCGT Unit or Power Park Unit) or HVDC Equipment run-up sequence, where these circuit breakers are installed.

ECC.6.2.2.3.3	Loss of Excitation

The EU Generator must provide Protection to detect loss of excitation in respect of each of its Generating Units within a Synchronous Power Generating Module to initiate a Generating Unit trip.

ECC.6.2.2.3.4	Pole-Slipping Protection

Where, in The Company's reasonable opinion, System requirements dictate, The Company will specify in the Bilateral Agreement a requirement for EU Generators to fit pole-slipping Protection on their Generating Units within each Synchronous Power Generating Module.

ECC.6.2.2.3.5	Signals for Tariff Metering

EU Generators and HVDC System Owners will install current and voltage transformers supplying all tariff meters at a voltage to be specified in, and in accordance with, the Bilateral Agreement.

ECC.6.2.2.3.6	Commissioning of Protection Systems

No EU Generator or HVDC System Owner equipment shall be energised until the Protection settings have been finalised. The EU Generator or HVDC System Owner  shall agree with The Company (in coordination with the Relevant Transmission Licensee) and carry out a combined commissioning programme for the Protection systems, and generally, to a minimum standard as specified in the Bilateral Agreement.

ECC.6.2.2.4	Work on Protection Equipment

No busbar Protection, mesh corner Protection, circuit-breaker fail Protection relays, AC or DC wiring (other than power supplies or DC tripping associated with the Power Generating Module, HVDC Equipment itself) may be worked upon or altered by the EU Generator or HVDC System Owner personnel in the absence of a representative of the Relevant Transmission Licensee or written authority from the Relevant Transmission Licensee to perform such work or alterations in the absence of a representative of the Relevant Transmission Licensee.

ECC.6.2.2.5	Relay Settings

Protection and relay settings will be co-ordinated (both on connection and subsequently) across the Connection Point in accordance with the Bilateral Agreement and in relation to OTSDUW Plant and Apparatus, across the Interface Point  in accordance with the Bilateral Agreement to ensure effective disconnection of faulty Apparatus.

ECC.6.2.2.6	Changes to Protection Schemes and HVDC System Control Modes

ECC.6.2.2.6.1	Any subsequent alterations to the protection settings (whether by The Company, the Relevant Transmission Licensee, the EU Generator, or the HVDC System Owner) shall be agreed between The Company (in co-ordination with the Relevant Transmission Licensee) and the EU Generator or HVDC System Owner in accordance with the Grid Code (ECC.6.2.2.5).  No alterations are to be made to any protection schemes unless agreement has been reached between The Company, the Relevant Transmission Licensee, the EU Generator or HVDC System Owner.

ECC.6.2.2.6.2	 The parameters of different control modes of the HVDC System shall be able to be changed in the HVDC Converter Station, if required by The Company  in coordination with the Relevant Transmission Licensee and in accordance with ECC.6.2.2.6.4.

ECC.6.2.2.6.3	Any change to the schemes or settings of parameters of the different control modes and protection of the HVDC System including the procedure shall be agreed with The Company in coordination with the Relevant Transmission Licensee and the HVDC System Owner.

ECC.6.2.2.6.4	The control modes and associated set points shall be capable of being changed remotely, as specified by The Company in coordination with the Relevant Transmission Licensee.

ECC.6.2.2.7	Control Schemes and Settings

ECC.6.2.2.7.1	The schemes and settings of the different control devices on the Power Generating Module  and HVDC Equipment that are necessary for Transmission System stability and for taking emergency action shall be agreed with The Company in coordination with the Relevant Transmission Licensee and the EU Generator or HVDC System Owner.  Restoration Contractors shall have the ability to switch from alternative control schemes and settings on their Plant and Apparatus whilst remaining in service if they are required to satisfy their obligations in a Restoration Plan. Changes to any control schemes and settings shall be agreed between The Company and/or Relevant Transmission Licensee and/or Network Operator as part of developing a Restoration Plan which shall be in accordance with the requirements of ECC.6.2.2.6.

ECC.6.2.2.7.2	Subject to the requirements of ECC.6.2.2.7.1 any changes to the schemes and settings, defined in ECC.6.2.2.7.1, of the different control devices of the Power Generating Module or Restoration Contractor or HVDC Equipment shall be coordinated and agreed between the Relevant Transmission Licensee, the EU Generator, Restoration Contractor and HVDC System Owner.

ECC.6.2.2.8	Ranking of Protection and Control

ECC.6.2.2.8.1	The Company in coordination with Relevant Transmission Licensees, shall agree and coordinate the  protection and control devices  of EU Generators Plant and Apparatus in accordance with the following general priority ranking (from highest to lowest):

- The interface between the National Electricity Transmission System and  the Power Generating Module or HVDC Equipment Protection equipment;

- frequency control (active power adjustment);

- power restriction; and

- power gradient constraint;

ECC.6.2.2.8.2	A control scheme, specified by the HVDC System Owner consisting of different control modes, including the settings of the specific parameters, shall be coordinated and agreed between The Company in coordination with the Relevant Transmission Licensee and the HVDC System Owner.  These details would be specified in the Bilateral Agreement.

ECC.6.2.2.8.3	The Company in coordination with Relevant Transmission Licensees, shall agree and coordinate the protection and control devices of HVDC System Owners Plant and Apparatus in accordance with the following general priority ranking (from highest to lowest)

- The interface between the National Electricity Transmission System and HVDC System Protection equipment;

- Active Power control for emergency assistance

- automatic remedial actions as specified in ECC.6.3.6.1.2.5

- Limited Frequency Sensitive Mode (LFSM) of operation;

- Frequency Sensitive Mode of operation and Frequency control; and

- power gradient constraint.

ECC.6.2.2.9	Synchronising

ECC.6.2.2.9.1	For any Power Generating Module directly connected to the National Electricity Transmission System or Type D Power Generating Module, synchronisation shall be performed by the EU Generator only after instruction by The Company in accordance with the requirements of BC.2.5.2.

ECC.6.2.2.9.2	Each Power Generating Module directly connected to the National Electricity Transmission System or Type D Power Generating Module shall be equipped with the necessary synchronisation facilities. Synchronisation shall be possible within the range of frequencies specified in ECC.6.1.2.

ECC.6.2.2.9.3	The requirements for synchronising equipment  shall be specified in accordance with the requirements in the Electrical Standards listed in the annex to the General Conditions.  The synchronisation settings shall include the following elements below.  Any variation to these requirements shall be pursuant to the terms of the Bilateral Agreement.

- voltage

- Frequency

- phase angle range

- phase sequence

- deviation of voltage and Frequency

ECC.6.2.2.9.4	HVDC Equipment shall be required to satisfy the requirements of ECC.6.2.2.9.1 – ECC.6.2.2.9.3.  In addition, unless otherwise specified by The Company, during the synchronisation of a DC Connected Power Park Module to the National Electricity Transmission System, any HVDC Equipment shall have the capability to limit any steady state voltage changes to the limits specified within ECC.6.1.7 or ECC.6.1.8 (as applicable) which shall not exceed 5% of the pre-synchronisation voltage.  The Company in coordination with the Relevant Transmission Licensee shall specify any additional requirements for the maximum magnitude, duration and measurement of the voltage transients over and above those defined in ECC.6.1.7 and ECC.6.1.8 in the Bilateral Agreement.

ECC.6.2.2.9.5	EU Generators in respect of DC Connected Power Park Modules shall also provide output synchronisation signals specified by The Company in co-ordination with the Relevant Transmission Licensee.

ECC.6.2.2.9.6	In addition to the requirements of ECC.6.2.2.9.1 to ECC.6.2.2.9.5, EU Generators and HVDC System Owners should also be aware of the requirements of ECC.6.5.10 relating to busbar voltage

ECC.6.2.2.9.10	HVDC Parameters and Settings

ECC.6.2.2.9.10.1	The parameters and settings of the main control functions of an HVDC System shall be agreed between the HVDC System owner and The Company , in coordination with the Relevant Transmission Licensee. The parameters and settings shall be implemented within such a control hierarchy that makes their modification possible if necessary. Those main control functions are at least:

(b) Frequency Sensitive Modes (FSM, LFSM-O, LFSM-U);

(c) Frequency control, if applicable;

(d) Reactive Power control mode, if applicable;

(e) power oscillation damping capability;

(f) subsynchronous torsional interaction damping capability,.

ECC.6.2.2.11	Automatic Reconnection

ECC.6.2.2.11.1	EU Generators in respect of Type A, Type B,  Type C and Type D Power Generating Modules (including DC Connected Power Park Modules) which have signed a CUSC Contract with The Company are not permitted to automatically reconnect to the Total System without instruction from The Company.  The Company will issue instructions for re-connection or re-synchronisation in accordance with the requirements of BC2.5.2.  Where synchronising is permitted in accordance with BC2.5.2, the voltage and frequency at the Grid Entry Point or User System Entry Point shall be within the limits defined in ECC.6.1.2 and ECC.6.1.4 and the ramp rate limits pursuant to BC1.A.1.1.  For the avoidance of doubt this requirement does not apply to EU Generators who are not required to satisfy the requirements of the Balancing Codes.

ECC.6.2.2.12	Automatic Disconnection

ECC.6.2.2.12.1 No Power Generating Module or HVDC Equipment shall disconnect within the frequency range or voltage range defined in ECC.6.1.2 and ECC.6.1.4.

ECC.6.2.2.13	Special Provisions relating to Power Generating Modules embedded within Industrial Sites which supply electricity as a bi-product of their industrial process

ECC.6.2.2.13.1	Generators in respect of Power Generating Modules which form part of an industrial network, where the Power Generating Module is used to supply critical loads within the industrial process shall be permitted to operate isolated from the Total System if agreed with The Company in the Bilateral Agreement.

ECC.6.2.2.13.2	Except for the requirements of ECC.6.3.3 and ECC.6.3.7.1, Power Generating Modules which are embedded within industrial sites are not required to satisfy the requirements of ECC.6.3.6.2.1 and ECC.6.3.9.  In this case this exception would only apply to Power Generating Modules on industrial sites used for combined heat and power production which are embedded in the network of an industrial site where all the following criteria are met.

- The primary purpose of these sites is to produce heat for production processes of the industrial site concerned,

- Heat and power generation is inextricably interlinked, that is to say any change to heat generation results inadvertently in a change of active power generating and vica versa.

- The Power Generating Modules are of Type A, Type B or Type C.

- Combined heat and power generating facilities shall be assessed on the basis of their electrical Maximum Capacity.

ECC.6.2.3	Requirements at EU Grid Supply Points relating to Network Operators and Non-Embedded Customers

ECC.6.2.3.1	Protection Arrangements for EU Code Users in respect of Network Operators and Non-Embedded Customers

ECC.6.2.3.1.1	Protection arrangements for EU Code Users in respect of Network Operators and Non-Embedded Customers User Systems directly connected to the National Electricity Transmission System, shall meet the requirements given below:

Fault Clearance Times

(a)	The required fault clearance time for faults on Network Operator and Non-Embedded Customer equipment directly connected to the National Electricity Transmission System, and for faults on the National Electricity Transmission System directly connected to the Network Operator’s or Non-Embedded Customer's equipment, from fault inception to the circuit breaker arc extinction, shall be set out in each Bilateral Agreement.  The fault clearance time specified in the Bilateral Agreement shall not be shorter than the durations specified in (i), (ii) and (iii) below:

(i)	 80ms for connections operating at a nominal voltage of greater than 300kV

(ii)	100ms for connections operating at a nominal voltage of greater than 132kV and up to 300kV

(iii)	120ms for connections operating at a nominal voltage of greater than 132kV and below

but this shall not prevent the User or The Company or Relevant Transmission Licensee from selecting a shorter fault clearance time on its own Plant and Apparatus provided Discrimination is achieved.

For the purpose of establishing the Protection requirements in accordance with ECC.6.2.3.1.1 only, the point of connection of the Network Operator or Non-Embedded Customer equipment to the National Electricity Transmission System shall be deemed to be the low voltage busbars at an EU Grid Supply Point, irrespective of the ownership of the equipment at the EU Grid Supply Point.

A longer fault clearance time may be specified in the Bilateral Agreement for faults on the National Electricity Transmission System.  A longer fault clearance time for faults on the Network Operator and Non-Embedded Customers equipment may be agreed with The Company in accordance with the terms of the Bilateral Agreement but only if System requirements in The Company's view permit. The probability that the fault clearance time stated in the Bilateral Agreement will be exceeded by any given fault must be less than 2%.

(b)	(i)	For the event of failure of the Protection systems provided to meet the above fault clearance time requirements, Back-Up Protection shall be provided by the Network Operator or Non-Embedded Customer as the case may be.

(ii)	The Relevant Transmission Licensee will also provide Back-Up Protection, which will result in a fault clearance time longer than that specified for the Network Operator or Non-Embedded Customer Back-Up Protection so as to provide Discrimination.

(iii)	For connections with the National Electricity Transmission System at 132kV and below, it is normally required that the Back-Up Protection on the National Electricity Transmission System shall discriminate with the Network Operator or Non-Embedded Customer's Back-Up Protection.

(iv)	For connections with the National Electricity Transmission System operating at a nominal voltage greater than 132kV, the Back-Up Protection will be provided by the Network Operator or Non-Embedded Customer, as the case may be, with a fault clearance time not longer than 300ms for faults on the Network Operator’s or Non-Embedded Customer's Apparatus.

(v)	Such Protection will also be required to withstand, without tripping, the loading incurred during the clearance of a fault on the National Electricity Transmission System by breaker fail Protection operating at a nominal voltage of greater than 132kV. This will permit Discrimination between Network Operator’s Back-Up Protection or Non-Embedded Customer’s Back-Up Protection, as the case may be, and Back-Up Protection provided on the National Electricity Transmission System and other User Systems. The requirement for and level of Discrimination required will be specified in the Bilateral Agreement.

(c)	(i)	Where the Network Operator or Non-Embedded Customer is connected to part of the National Electricity Transmission System operating at a nominal voltage greater than 132kV and in Scotland also at 132kV, and a circuit breaker is provided by the Network Operator or Non-Embedded Customer, or the Relevant Transmission Licensee, as the case may be, to interrupt the interchange of fault current with the National Electricity Transmission System or the System of the Network Operator or Non-Embedded Customer, as the case may be, circuit breaker fail Protection will be provided by the Network Operator or Non-Embedded Customer, or the Relevant Transmission Licensee, as the case may be, on this circuit breaker.

(ii)	In the event, following operation of a Protection system, of a failure to interrupt fault current by these circuit-breakers within the Fault Current Interruption Time, the circuit breaker fail Protection is required to initiate tripping of all the necessary electrically adjacent circuit-breakers so as to interrupt the fault current within the next 200ms.

(d)	The target performance for the System Fault Dependability Index shall be not less than 99%.  This is a measure of the ability of Protection to initiate successful tripping of circuit breakers which are associated with the faulty items of Apparatus.

ECC.6.2.3.2	Fault Disconnection Facilities

(a)	Where no Transmission circuit breaker is provided at the User's connection voltage, the User must provide The Company with the means of tripping all the User's circuit breakers necessary to isolate faults or System abnormalities on the National Electricity Transmission System.  In these circumstances, for faults on the User's System, the User's Protection should also trip higher voltage Transmission circuit breakers.  These tripping facilities shall be in accordance with the requirements specified in the Bilateral Agreement.

(b)	The Company may require the installation of a System to Generator Operational Intertripping Scheme in order to enable the timely restoration of circuits following power System fault(s).  These requirements shall be set out in the relevant Bilateral Agreement.

ECC.6.2.3.3	Automatic Switching Equipment

Where automatic reclosure of Transmission circuit breakers is required following faults on the User's System, automatic switching equipment shall be provided in accordance with the requirements specified in the Bilateral Agreement.

ECC.6.2.3.4	Relay Settings

Protection and relay settings will be co-ordinated (both on connection and subsequently) across the Connection Point in accordance with the Bilateral Agreement to ensure effective disconnection of faulty Apparatus.

ECC.6.2.3.5	Work on Protection equipment

Where a Transmission Licensee owns the busbar at the Connection Point, no busbar Protection, mesh corner Protection relays, AC or DC wiring (other than power supplies or DC tripping associated with the Network Operator or Non-Embedded Customer’s Apparatus itself) may be worked upon or altered by the Network Operator or Non-Embedded Customer personnel in the absence of a representative of the Relevant Transmission Licensee or written authority from the Relevant Transmission Licensee to perform such work or alterations in the absence of a representative of the Relevant Transmission Licensee.

ECC.6.2.3.6		Equipment including Protection equipment to be provided

The Company in coordination with the Relevant Transmission Licensee shall specify and agree the Protection schemes and settings at each EU Grid Supply Point required to protect the National Electricity Transmission System in accordance with the characteristics of the Network Operator’s or Non Embedded Customer’s System. The Company in coordination with the Relevant Transmission Licensee and the Network Operator or Non Embedded Customer shall agree on the protection schemes and settings in respect of the busbar protection zone in respect of each EU Grid Supply Point.

Protection of the Network Operator’s or Non Embedded Customer’s System shall take precedence over operational controls whilst respecting the security of the National Electricity Transmission System and the health and safety of staff and the public.

ECC.6.2.3.6.1	Protection of Interconnecting Connections

The requirements for the provision of Protection equipment for interconnecting connections will be specified in the Bilateral Agreement.

ECC.6.2.3.7	Changes to Protection Schemes

ECC.6.2.3.7.1	At EU Grid Supply Points

Any alterations to the busbar protection settings at the EU Grid Supply Point (whether by The Company, the Relevant Transmission Licensee, the Network Operator or the Non Embedded Customer) shall be agreed between The Company (in co-ordination with the Relevant Transmission Licensee) and the Network Operator or Non Embedded Customer in accordance with the Grid Code (ECC.6.2.3.4).  No alterations are to be made to any busbar protection schemes unless agreement has been reached between The Company, the Relevant Transmission Licensee, the Network Operator or Non Embedded Customer.

No Network Operator or Non-Embedded Customer equipment shall be energised until the Protection settings have been agreed prior to commissioning. The Network Operator or Non-Embedded Customer shall agree with The Company (in coordination with the Relevant Transmission Licensee) and carry out a combined commissioning programme for the Protection systems, and generally, to a minimum standard as specified in the Bilateral Agreement.

ECC.6.2.3.7.2	Network Operators Systems

Network Operators shall, if required in a Restoration Plan, have the ability to switch:-

- From the normal to the alternative Protection settings on their Plant and Apparatus; and:-

- From the alternative to the normal Protection settings whilst their Plant remains in service,

Any alternative Protection settings shall be included in the Restoration Plan.  Normal and alternative Protection settings shall be agreed between The Company and the Network Operator as part of developing a Restoration Plan.

ECC.6.2.3.8	Control Requirements

ECC.6.2.3.8.1	The Company in coordination with the Relevant Transmission Licensee and the Network Operator or Non Embedded Customer shall agree on the control schemes and settings at each EU Grid Supply Point of the different control devices of the Network Operator’s or Non Embedded Customer’s System relevant for security of the National Electricity Transmission System. Such requirements would be pursuant to the terms of the Bilateral Agreement which shall also cover at least the following elements:

- Isolated (National Electricity Transmission System) operation;

- Damping of oscillations;

- Disturbances to the National Electricity Transmission System;

- Automatic switching to emergency supply and restoration to normal topology;

- Automatic circuit breaker re-closure (on 1-phase faults).

ECC.6.2.3.8.2	Subject to the requirements of ECC.6.2.3.8.1, any changes to the schemes and settings, defined in ECC.6.2.3.8.1 of the different control devices of the Network Operator’s or Non-Embedded Customer’s System at the EU Grid Supply Point shall be coordinated and agreed between The Company, the Relevant Transmission Licensee, the Network Operator or Non Embedded Customer.  Network Operators shall have the ability to switch between alternative control settings on their Plant and Apparatus if they are required to do so to be able to satisfy their obligations of a Restoration Plan.  Any alternative control settings shall be included in the Restoration Plan.

ECC.6.2.3.9	Ranking of Protection and Control

ECC.6.2.3.9.1	The Network Operator or the Non Embedded Customer who owns or operates an EU Grid Supply Point shall set the Protection and control devices of its System, in compliance with the following priority ranking, organised in decreasing order of importance:

(a) National Electricity Transmission System Protection;

(b)  Protection equipment at each EU Grid Supply Point;

(c) Frequency control (Active Power adjustment);

(d) Power restriction.

ECC.6.2.3.10	Synchronising

ECC.6.2.3.10.1	Each Network Operator or Non Embedded Customer at each EU Grid Supply Point shall be capable of synchronisation within the range of frequencies specified in ECC.6.1.2 unless otherwise agreed with The Company.

ECC.6.2.3.10.2	The Company and the Network Operator or Non Embedded Customer shall agree on the settings of the synchronisation equipment at each EU Grid Supply Point prior to the Completion Date. The Company and the relevant Network Operator or Non-Embedded Customer shall agree the synchronisation settings which shall include the following elements.

- Voltage;

- Frequency;

- phase angle range;

- deviation of voltage and Frequency.

ECC.6.3	GENERAL POWER GENERATING MODULE, OTSDUW  AND HVDC EQUIPMENT REQUIREMENTS

ECC.6.3.1	This section sets out the technical and design criteria and performance requirements for Power Generating Modules (which includes Electricity Storage Modules) and HVDC Equipment (whether directly connected to the National Electricity Transmission System or Embedded) and (where provided in this section) OTSDUW Plant and Apparatus  which each Generator or HVDC System Owner must ensure are complied with in relation to its Power Generating Modules, HVDC Equipment  and OTSDUW Plant and Apparatus.  References to Power Generating Modules, HVDC Equipment  in this ECC.6.3 should be read accordingly. For the avoidance of doubt, the requirements applicable to Synchronous Power Generating Modules also apply to Synchronous Electricity Storage Modules and the requirements applicable to Power Park Modules apply to Non-Synchronous Electricity Storage Modules.  In addition, the requirements applicable to Electricity Storage Modules also apply irrespective of whether the Electricity Storage Module operates in such a mode as to import or export power from the Total System.

Plant Performance Requirements

ECC.6.3.2	REACTIVE CAPABILITY

ECC.6.3.2.1	Reactive Capability for Type B Synchronous Power Generating Modules

ECC.6.3.2.1.1	When operating at Maximum Capacity, all Type B Synchronous Power Generating Modules must be capable of continuous operation at any points between the limits of 0.95 Power Factor lagging and 0.95 Power Factor leading at the Grid Entry Point or User System Entry Point unless otherwise agreed with The Company or relevant Network Operator. At Active Power output levels other than Maximum Capacity, all Generating Units within a Type B Synchronous Power Generating Module must be capable of continuous operation at any point between the Reactive Power capability limits identified on the HV Generator Performance Chart unless otherwise agreed with The Company or relevant Network Operator.

ECC.6.3.2.2 	Reactive Capability for Type B Power Park Modules

ECC.6.3.2.2.1	When operating at  Maximum Capacity all Type B Power Park Modules must be capable of continuous operation at any points between the limits of 0.95 Power Factor lagging and 0.95 Power Factor leading at the Grid Entry Point or User System Entry Point unless otherwise agreed with The Company or relevant Network Operator.    At Active Power output levels other than Maximum Capacity, each Power Park Module  must be capable of continuous operation at any point between the Reactive Power capability limits identified on the HV Generator Performance Chart unless otherwise agreed with The Company or Network Operator.

ECC.6.3.2.3	Reactive Capability for Type C and D Synchronous Power Generating Modules

ECC.6.3.2.3.1	In addition to meeting the requirements of ECC.6.3.2.3.2 – ECC.6.3.2.3.5, EU Generators which connect a Type C or Type D Synchronous Power Generating Module(s) to a Non Embedded Customers System or private network, may be required to meet additional reactive compensation requirements at the point of connection between the System and the Non Embedded Customer or private network where this is required for System reasons.

ECC.6.3.2.3.2	All Type C and Type D Synchronous Power Generating Modules shall be capable of satisfying the Reactive Power capability requirements at the Grid Entry Point or User System Entry Point as defined in Figure ECC.6.3.2.3 when operating at Maximum Capacity.

ECC.6.3.2.3.3	At Active Power output levels other than Maximum Capacity, all Generating Units within a Synchronous Power Generating Module must be capable of continuous operation at any point between the Reactive Power capability limit identified on the HV Generator Performance Chart at least down to the  Minimum Stable Operating Level.  At reduced Active Power output, Reactive Power supplied at the Grid Entry Point (or User System Entry Point if Embedded) shall correspond to the HV Generator Performance Chart of the Synchronous Power Generating Module, taking the auxiliary supplies and the Active Power and Reactive Power losses of the Generating Unit transformer or Station Transformer into account.

Figure ECC.6.3.2.3

ECC.6.3.2.3.4	In addition, to the requirements of ECC.6.3.2.3.1 – ECC.6.3.2.3.3 the short circuit ratio of all Onshore Synchronous Generating Units with an Apparent Power rating of less than 1600MVA shall not be less than 0.5.  The short circuit ratio of Onshore Synchronous Generating Units with a rated Apparent Power of 1600MVA or above shall be not less than 0.4.

ECC.6.3.2.4	Reactive Capability for Type C and D Power Park Modules, HVDC Equipment and OTSDUW Plant and Apparatus at the Interface Point

ECC.6.3.2.4.1	EU Generators or HVDC System Owners which connect an Onshore Type C or Onshore Type D Power Park Module or HVDC Equipment to a Non Embedded Customers System or private network, may be required to meet additional reactive compensation requirements at the point of connection between the System and the Non Embedded Customer or private network where this is required for System reasons.

ECC.6.3.2.4.2	All Onshore Type C Power Park Modules and Onshore Type D Power Park Modules  or HVDC Converters at an HVDC Converter Station with a Grid Entry Point or User System Entry Point  voltage above 33kV, or Remote End HVDC Converters with an HVDC Interface Point voltage above 33kV, or OTSDUW Plant and Apparatus with an Interface Point voltage above 33kV shall be capable of satisfying the Reactive Power capability requirements at the Grid Entry Point or User System Entry Point  (or Interface Point in the case of OTSDUW Plant and Apparatus, or HVDC Interface Point in the case of a Remote End HVDC Converter Station) as defined in Figure ECC.6.3.2.4(a) when operating at Maximum Capacity (or Interface Point Capacity in the case of OTSUW Plant and Apparatus). In the case of Remote End HVDC Converters and DC Connected Power Park Modules, The Company in co-ordination with the Relevant Transmission Licensee may agree to alternative reactive capability requirements to those specified in Figure ECC.6.3.2.4(a), where it is demonstrated that it is uneconomic and inefficient to do so, for example in the case of new technologies or advanced control strategies.  For the avoidance of doubt, the requirements for Offshore Power Park Modules and DC Connected Power Park Modules are defined in ECC.6.3.2.5 and ECC.6.3.2.6.

Figure ECC.6.3.2.4(a)

ECC.6.3.2.4.3	All Onshore Type C or Type D Power Park Modules or HVDC Converters at a HVDC Converter Station with a Grid Entry Point or User System Entry Point voltage at or below 33kV or Remote End HVDC Converter Station with an HVDC Interface Point Voltage at or below 33kV shall be capable of satisfying the Reactive Power capability requirements at the Grid Entry Point or User System Entry Point as defined in Figure ECC.6.3.2.4(b) when operating at Maximum Capacity. In the case of Remote End HVDC Converters The Company in co-ordination with the Relevant Transmission Licensee may agree to alternative reactive capability requirements to those specified in Figure ECC.6.3.2.4(b), where it is demonstrated that it is uneconomic and inefficient to do so, for example in the case of new technologies or advanced control strategies. For the avoidance of doubt, the requirements for Offshore Power Park Modules and DC Connected Power Park Modules are defined in ECC.6.3.2.5 and ECC.6.3.2.6.

Figure ECC.6.3.2.4(b)

ECC.6.3.2.4.4	All Type C and Type D Power Park Modules, HVDC Converters at a HVDC Converter Station including Remote End HVDC Converters or OTSDUW Plant and Apparatus, shall be capable of satisfying the Reactive Power capability requirements at the Grid Entry Point or User System Entry Point (or Interface Point Capacity in the case of OTSUW Plant and Apparatus or HVDC Interface Point in the case of Remote End HVDC Converter Stations) as defined in Figure ECC.6.3.2.4(c) when operating below Maximum Capacity. With all Plant in service, the Reactive Power limits will reduce linearly below 50% Active Power output as shown in Figure ECC.6.3.2.4(c) unless the requirement to maintain the Reactive Power limits defined at Maximum Capacity (or Interface Point Capacity in the case of OTSDUW Plant and Apparatus) under absorbing Reactive Power conditions down to 20% Active Power output has been specified by The Company.  These Reactive Power limits will be reduced pro rata to the amount of Plant in service. In the case of Remote End HVDC Converters, The Company in co-ordination with the Relevant Transmission Licensee may agree to alternative reactive capability requirements to those specified in Figure ECC.6.3.2.4(a), where it is demonstrated that it is uneconomic and inefficient to do so, for example in the case of new technologies or advanced control strategies.   For the avoidance of doubt, the requirements for Offshore Power Park Modules and DC Connected Power Park Modules are defined in ECC.6.3.2.5 and ECC.6.3.2.6.

Figure ECC.6.3.2.4(c)

ECC.6.3.2.5	Reactive Capability for Offshore Synchronous Power Generating Modules, Configuration 1 AC connected Offshore Power Park Modules and Configuration 1 DC Connected Power Park Modules.

ECC.6.3.2.5.1	The short circuit ratio of any Offshore Synchronous Generating Units within a Synchronous Power Generating Module shall not be less than 0.5.  Notwithstanding the requirements of ECC.6.3.2.5.2 and ECC.6.3.2.5.3, all Offshore Synchronous Generating Units, Configuration 1 AC Connected Offshore Power Park Modules or Configuration 1 DC Connected Power Park Modules must be capable of maintaining zero transfer of Reactive Power at the Offshore Grid Entry Point. The steady state tolerance on Reactive Power transfer to and from an Offshore Transmission System expressed in MVAr shall be no greater than 5% of the Maximum Capacity.

ECC.6.3.2.5.2	If an EU Generator  (including those in respect of DC Connected Power Park Modules or those which are Restoration Contractors), wish to provide a Reactive Power capability in excess of the minimum requirements defined in ECC.6.3.2.5.1, then such  capability (including steady state tolerance) shall be agreed between the Generator, Offshore Transmission Licensee and The Company and/or the relevant Network Operator.

ECC.6.3.2.5.3	In the case of EU Code Users and Restoration Contractors who own and operate Anchor Plant and/or Top Up Restoration Plant or EU Code Users who own and operate Plant and Apparatus which is operating with a Grid Forming Capability in service, the Reactive Power capability requirements (including steady state tolerance) at the Offshore Grid Entry Point shall be agreed between the Restoration Contractor or EU Code User, the Offshore Transmission Licensee and The Company in order to facilitate the operation of an Offshore Local Joint Restoration Plan.

ECC.6.3.2.6	Reactive Capability for Configuration 2 AC Connected Offshore Power Park Modules and Configuration 2 DC Connected Power Park Modules.

ECC.6.3.2.6.1	All Configuration 2 AC connected Offshore Power Park Modules and Configuration 2 DC Connected Power Park Modules shall be capable of satisfying the minimum Reactive Power capability requirements at the Offshore Grid Entry Point as defined in Figure ECC.6.3.2.6(a) when operating at Maximum Capacity. The Company in co-ordination with the Relevant Transmission Licensee may agree to alternative reactive capability requirements to those specified in Figure ECC.6.3.2.6(a), where it is demonstrated that it is uneconomic and inefficient to do so, for example in the case of new technologies or advanced control strategies.

Figure ECC.6.3.2.6(a)

ECC.6.3.2.6.2	All AC Connected Configuration 2 Offshore Power Park Modules and Configuration 2 DC Connected Power Park Modules shall be capable of satisfying the Reactive Power capability requirements at the Offshore Grid Entry Point as defined in Figure ECC.6.3.2.6(b) when operating below Maximum Capacity. With all Plant in service, the Reactive Power limits will reduce linearly below 50% Active Power output as shown in Figure ECC.6.3.2.6(b) unless the requirement to maintain the Reactive Power limits defined at Maximum Capacity (or Interface Point Capacity in the case of OTSDUW Plant and Apparatus) under absorbing Reactive Power conditions down to 20% Active Power output has been specified with The Company. These Reactive Power limits will be reduced pro rata to the amount of Plant in service. The Company in co-ordination with the Relevant Transmission Licensee may agree to alternative reactive capability requirements to those specified in Figure ECC.6.3.2.6(b), where it is demonstrated that it is uneconomic and inefficient to do so, for example in the case of new technologies or advanced control strategies.

Figure ECC.6.3.2.6(b)

ECC.6.3.2.6.3	For the avoidance of doubt, if an EU Generator  (including Generators in respect of DC Connected Power Park Modules or those which are Restoration Contractors referred to in ECC.6.3.2.6.2) wishes to provide a Reactive Power capability in excess of the minimum requirements defined in ECC.6.3.2.6.1, then such capability (including any steady state tolerance) shall be agreed between the EU Generator, Offshore Transmission Licensee and The Company and/or the relevant Network Operator.

ECC.6.3.2.6.4	In addition to the requirements of ECC.6.3.2.6.2, EU Generators and HVDC System Owners and Restoration Contractors who own and operate Anchor Plant and/or Top Up Restoration Plant, then the Reactive Power capability requirements (including steady state tolerance) at the Offshore Grid Entry Point shall be agreed between the Generator, Offshore Transmission Licensee and The Company in order to facilitate the operation of an Offshore Local Joint Restoration Plan.

ECC.6.3.3	OUTPUT POWER WITH FALLING FREQUENCY

ECC.6.3.3.1	Output power with falling frequency for Power Generating Modules and HVDC Equipment

ECC.6.3.3.1.1	Each Power Generating Module and HVDC Equipment must be capable of:

(a)	continuously maintaining constant Active Power output for System Frequency changes within the range 50.5 to 49.5 Hz; and

(b)	(subject to the provisions of ECC.6.1.2) maintaining its Active Power output at a level not lower than the figure determined by the linear relationship shown in Figure ECC.6.3.3(a) for System Frequency changes within the range 49.5 to 47 Hz for all ambient temperatures up to and including 25⁰C, such that if the System Frequency drops to 47 Hz the Active Power output does not decrease by more than 5%. In the case of a CCGT Module, the above requirement shall be retained down to the Low Frequency Relay trip setting of 48.8 Hz, which reflects the first stage of the Automatic Low Frequency Demand Disconnection scheme notified to Network Operators under OC6.6.2.  For System Frequency below that setting, the existing requirement shall be retained for a minimum period of 5 minutes while System Frequency remains below that setting, and special measure(s) that may be required to meet this requirement shall be kept in service during this period. After that 5 minutes period, if System Frequency remains below that setting, the special measure(s) must be discontinued if there is a materially increased risk of the Gas Turbine tripping. The need for special measure(s) is linked to the inherent Gas Turbine Active Power output reduction caused by reduced shaft speed due to falling System Frequency. Where the need for special measures is identified in order to maintain output in line with the level identified in Figure ECC.6.3.3(a) these measures should be still continued at ambient temperatures above 25⁰C maintaining as much of the Active Power achievable within the capability of the plant. For the avoidance of doubt, Generators in respect of Pumped Storage shall also be required to satisfy the requirements of OC6.6.6.

Figure ECC.6.3.3(a) Active Power Output with falling frequency for Power Generating Modules and HVDC Systems and Electricity Storage Modules when operating in an exporting mode of operation

(c)	For the avoidance of doubt, in the case of a Power Generating Module including a DC Connected Power Park Module using an Intermittent Power Source where the mechanical power input will not be constant over time, the requirement is that the Active Power output shall be independent of System Frequency under (a) above and should not drop with System Frequency by greater than the amount specified in (b) above.

(d)	An HVDC System must be capable of maintaining its Active Power input (i.e. when operating in a mode analogous to Demand) from the National Electricity Transmission System (or User System in the case of an Embedded HVDC System) at a level not greater than the figure determined by the linear relationship shown in Figure ECC.6.3.3(b) for System Frequency changes within the range 49.5 to 47 Hz, such that if the System Frequency drops to 47.8 Hz the Active Power input decreases by more than 60%.

Figure ECC.6.3.3(b) Active Power input with falling frequency for HVDC Systems

(e)	In the case of an Offshore Generating Unit or Offshore Power Park Module or DC Connected Power Park Module or Remote End HVDC Converter or Transmission DC Converter, the EU Generator shall comply with the requirements of ECC.6.3.3.  EU Generators should be aware that Section K of the STC places requirements on Offshore Transmission Licensees which utilise a Transmission DC Converter as part of their Offshore Transmission System to make appropriate provisions to enable EU Generators to fulfil their obligations.

(f)	Transmission DC Converters and Remote End HVDC Converters shall provide a continuous signal indicating the real time frequency measured at the Interface Point to the Offshore Grid Entry Point or HVDC Interface Point for the purpose of Offshore Generators or DC Connected Power Park Modules to respond to changes in System Frequency on the Main Interconnected Transmission System.  A DC Connected Power Park Module or Offshore Power Generating Module shall be capable of receiving and processing this signal within 100ms.

(g)	For HVDC Systems with a Completion Date on or after 31 December 2026, HVDC System Owners shall ensure that each HVDC System has the capability to provide a continuous signal indicating the real time frequency measured at the  Grid Entry Point and HVDC Interface Point and other signals as agreed with The Company for the purpose of participating in a Local Joint Restoration Plan or wider System Restoration event. The frequency signal at the Interface Point shall be capable of being received and processed within 100ms.

(h)	For Transmission DC Converters with a Completion Date on or after 31 December 2026, Offshore Transmission Licensees shall ensure that each Transmission DC Converter has the capability to provide a continuous signal indicating the real time frequency measured at the Offshore Grid Entry Point and HVDC Interface Point to the Interface Point for the purpose of participating in an Offshore Local Joint Restoration Plan or wider System Restoration event. The frequency signal at the Interface Point shall be capable of being received and processed within 100ms. This requirement shall be necessary where one or more Offshore Generators  are part of an Offshore Local Joint Restoration Zone Plan.

ECC.6.3.4	ACTIVE POWER OUTPUT UNDER SYSTEM VOLTAGE VARIATIONS

ECC.6.3.4.1	At the Grid Entry Point or User System Entry Point , the Active Power output under steady state conditions of any Power Generating Module or HVDC Equipment directly connected to the National Electricity Transmission System or in the case of OTSDUW, the Active Power transfer at the Interface Point, under steady state conditions of any OTSDUW Plant and Apparatus should not be affected by voltage changes in the normal operating range specified in paragraph ECC.6.1.4 by more than the change in Active Power losses at reduced or increased voltage.

ECC.6.3.5	SYSTEM RESTORATION

ECC.6.3.5.1		It is not a mandatory requirement for Generators, or HVDC System Owners to provide an Anchor Plant Capability or Top Up Restoration Capability, however EU Code Users may wish to notify The Company of their ability to provide such a facility and the cost of the service. The Company will then consider whether it wishes to contract with the EU Code User for the provision of such a service which would be specified via an Anchor Restoration Contract or Top Up Restoration Contract. Where an EU Code User does not offer to provide a cost for the provision of an Anchor Plant Capability, The Company may make such a request if it considers System security to be at risk due to a lack of Anchor Plant capability.

ECC.6.3.5.2	It is an essential requirement that The Company has a means of implementing System Restoration in accordance with the requirements of the Electricity System Restoration Standard. This is facilitated by agreeing contracts with Restoration Contractors who have Plant  at a number of strategically located sites.  In the case of Restoration Contractors who are party to a Distribution Restoration Zone Plan, The Company shall agree the requirements with the relevant Network Operator and Restoration Contractors.

ECC.6.3.5.3	The following requirements shall apply in respect of each Type C Power Generating Module, Type D Power Generating Module and DC Connected Power Park Module which have an Anchor Restoration Contract.

- The Power-Generating Module or DC Connected Power Park Module shall be capable of starting from a Total Shutdown or Partial Shutdown without any external electrical energy supply within either 2 hours of receiving an instruction from The Company in the case of Local Joint Restoration Plan or alternatively 8 hours of receiving an instruction from a Network Operator in the case of a Distribution Restoration Zone Plan;

- Each Power Generating Module or DC Connected Power Park Module  shall  be able to synchronise within the frequency limits defined in ECC.6.1.2 and, where applicable, voltage limits specified in ECC.6.1.4;

- The Power Generating Module or DC Connected Power Park Module shall be capable of energising an unenergised part of the System;

- The Power-Generating Module or DC Connected Power Park Module  shall be capable of automatically regulating dips in voltage caused by connection of demand;

- The Power Generating Module or DC Connected Power Park Module shall;

be capable of a Block Load Capability,

be capable of operating in LFSM-O and LFSM-U, as specified in ECC.6.3.7.1 and ECC.6.3.7.2,

control Frequency in case of overfrequency and underfrequency within the whole Active Power output range between the Minimum Regulating Level and Maximum Capacity as well as at Houseload Operation levels, and

be capable of parallel operation together with other Power Generating Modules including DC Connected Power Park Modules within an isolated part of the Total System that is still supplying Customers, and controlling voltage automatically during the system restoration phase;

- Power Park Modules (including DC Connected Power Park Modules) and HVDC Equipment which provide an Anchor Plant Capability, shall also be capable of satisfying the relevant Grid Forming Capability requirements defined in ECC.6.3.19 as agreed with The Company.

ECC.6.3.5.4	Each HVDC System or Remote End HVDC Converter Station which has Anchor Plant  Capability and an Anchor Restoration Contract shall be capable of energising the busbar of an AC substation to which another HVDC Converter Station is connected.  The timeframe after shutdown of the HVDC System prior to energisation of the AC substation shall be pursuant to the terms of the Anchor Restoration Contract. The HVDC System shall be able to synchronise within the Frequency limits defined in ECC.6.1.2.1.2 and voltage limits defined in ECC.6.1.4.1 unless otherwise specified in the Anchor Restoration Contract. Wider Frequency and voltage ranges can be specified in the Anchor Restoration Contract in order to restore System security.

ECC.6.3.5.5	With regard to the capability to take part in operation of an isolated part of the Total System that is still supplying Customers:

i	Power Generating Modules including DC Connected Power Park Modules shall be capable of taking part in island operation if specified in the Anchor Restoration Contract or Top Up Restoration Contract  and:

ii	the Frequency limits for island operation shall be those specified in ECC.6.1.2;

iii	the voltage limits for island operation shall be those defined in ECC.6.1.4;

iv	Power Generating Modules including DC Connected Power Park Modules shall be able to operate in Frequency Sensitive Mode during island operation, as specified in ECC.6.3.7.3. In the event of a power surplus, Power Generating Modules including DC Connected Power Park Modules shall be capable of reducing the Active Power output from a previous operating point to any new operating point within the Power Generating Module Performance Chart. Power Generating Modules including DC Connected Power Park Modules shall be capable of reducing Active Power output as much as inherently technically feasible, but to at least 55 % of Maximum Capacity;

v	The method for detecting a change from interconnected system operation to island operation shall be agreed between the EU Generator, The Company and the Relevant Transmission Licensee. The agreed method of detection must not rely solely on The Company, Relevant Transmission Licensee’s or Network Operators switchgear position signals;

vi	Power Generating Modules including DC Connected Power Park Modules shall be able to operate in LFSM-O and LFSM-U during island operation, as specified in ECC.6.3.7.1 and ECC.6.3.7.2;

ECC.6.3.5.6	 	With regard to quick re-synchronisation capability:

- In case of disconnection of the Power Generating Module including DC Connected Power Park Modules from the System, the Power Generating Module shall be capable of quick re-synchronisation in line with the Protection strategy agreed between The Company and/or Network Operator  in co-ordination with the Relevant Transmission Licensee and the Generator;

- A Power Generating Module including a DC Connected Power Park Module with a minimum re-synchronisation time greater than 15 minutes after its disconnection from any external power supply must be capable of Houseload Operation from any operating point on its Power Generating Module  Performance Chart. In this case, the identification of Houseload Operation must not be based solely on the Total System’s switchgear position signals;

- Power Generating Modules including DC Connected Power Park Modules shall be capable of  Houseload Operation, irrespective of any auxiliary connection to the Total System. The minimum operation time shall be specified by The Company, taking into consideration the specific characteristics of prime mover technology.

ECC.6.3.5.7	Restoration Contractors who are Offshore Generators and Transmission DC Converter owners who are part of an Offshore Local Joint Restoration Plan shall ensure their Plant and Apparatus is designed to satisfy the requirements of ECC.7.10 and ECC.7.11.

R

ECC.6.3.6	CONTROL ARRANGEMENTS

ECC.6.3.6.1	ACTIVE POWER CONTROL

ECC.6.3.6.1.1	Active Power control in respect of Power Generating  Modules including DC Connected Power Park Modules

ECC.6.3.6.1.1.1	Type A Power Generating Modules shall be equipped with a logic interface (input port) in order to cease Active Power output within five seconds following receipt of a signal from The Company.  The Company shall specify the  requirements for such facilities, including the need for remote operation, in the Bilateral Agreement where they are necessary for System reasons .

ECC.6.3.6.1.1.2	Type B Power Generating Modules shall be equipped with an interface (input port) in order to be able to reduce Active Power output following receipt of a signal from The Company.   The Company shall specify the  requirements for such facilities, including the need for remote operation, in the Bilateral Agreement where they are necessary for System reasons.

ECC.6.3.6.1.1.3	Type C and Type D Power Generating Modules and DC Connected Power Park Modules shall be capable of adjusting the Active Power setpoint in accordance with instructions issued by The Company.

ECC.6.3.6.1.2	Active Power control in respect of HVDC Systems  and Remote End HVDC Converter Stations

ECC.6.3.6.1.2.1	HVDC Systems shall be capable of adjusting the transmitted Active Power upon receipt of an instruction from The Company which shall be in accordance with the requirements of BC2.6.1.

ECC.6.3.6.1.2.2	The requirements for fast Active Power reversal (if required) shall be specified by The Company. Where Active Power reversal is specified in the Bilateral Agreement, each HVDC System  and Remote End HVDC Converter Station shall be capable of operating from maximum import to maximum export in a time which is as fast as technically feasible or in a time that is no greater than 2 seconds except where a HVDC Converter Station Owner has justified to The Company that a longer reversal time is required.

ECC.6.3.6.1.2.3	Where an HVDC System connects various Control Areas or Synchronous Areas, each HVDC System or Remote End HVDC Converter Station shall be capable of responding to instructions issued by The Company under the Balancing Code to modify the transmitted Active Power for the purposes of cross-border balancing.

ECC.6.3.6.1.2.4	An HVDC System shall be capable of adjusting the ramping rate of Active Power variations within its technical capabilities in accordance with instructions issued by The Company . In case of modification of Active Power according to ECC.6.3.15 and ECC.6.3.6.1.2.2, there shall be no adjustment of ramping rate.

ECC.6.3.6.1.2.5	If specified by The Company, in coordination with the Relevant Transmission Licensees, the control functions of an HVDC System shall be capable of taking automatic remedial actions including, but not limited to, stopping the ramping and blocking FSM, LFSM-O, LFSM-U and Frequency control. The triggering and blocking criteria shall be specified by The Company.

ECC.6.3.6.2	MODULATION OF ACTIVE POWER

ECC.6.3.6.2.1		Each Power Generating Module (including DC Connected Power Park Modules) and Onshore HVDC Converters at an Onshore HVDC Converter Station  must be capable of contributing to Frequency control by continuous modulation of Active Power supplied to the National Electricity Transmission System.  For the avoidance of doubt each Onshore HVDC Converter at an Onshore HVDC Converter Station  and/or OTSDUW DC Converter shall provide each EU Code User in respect of its Offshore Power Stations connected to and/or using an Offshore Transmission System a continuous signal indicating the real time Frequency measured at the Transmission Interface Point. A DC Connected Power Park Module or Offshore Power Generating Module shall be capable of receiving and processing this signal within 100ms.

ECC.6.3.6.3	MODULATION OF REACTIVE POWER

ECC.6.3.6.3.1	Notwithstanding the requirements of ECC.6.3.2, each Power Generating Module or HVDC Equipment (and OTSDUW Plant and Apparatus at a Transmission Interface Point and Remote End HVDC Converter at an HVDC Interface Point) (as applicable) must be capable of contributing to voltage control by continuous changes to the Reactive Power supplied to the National Electricity Transmission System or the User System in which it is Embedded.

ECC.6.3.7	FREQUENCY RESPONSE

ECC.6.3.7.1	Limited Frequency Sensitive Mode – Overfrequency (LFSM-O)

ECC.6.3.7.1.1	Each Power Generating Module (including DC Connected Power Park Modules) and HVDC Systems shall be capable of reducing Active Power output in response to Frequency on the Total System when this rises above 50.4Hz.  For the avoidance of doubt, the provision of this reduction in Active Power output is not an Ancillary Service. Such provision is known as Limited High Frequency Response. The Power Generating Module (including DC Connected Power Park Modules) or HVDC Systems  shall be capable of operating stably during LFSM-O operation.  However for a Power Generating Module (including DC Connected Power Park Modules) or HVDC Systems operating in Frequency Sensitive Mode the requirements of LFSM-O shall apply when the frequency exceeds 50.5Hz.

ECC.6.3.7.1.2	(i)	The rate of change of Active Power output must be at a minimum a rate of 2 percent of output per 0.1 Hz deviation of System Frequency above 50.4Hz (ie a Droop of 10%) as shown in Figure ECC.6.3.7.1 below. This would not preclude a EU Generator or HVDC System Owner from designing their Power Generating Module with a Droop of less than 10% but in all cases the Droop should be 2% or greater.

(ii)	The reduction in Active Power output must be continuously and linearly proportional, as far as is practicable, to the excess of Frequency above 50.4 Hz and must be provided increasingly with time over the period specified in (iii) below.

(iii)	As much as possible of the proportional reduction in Active Power output must result from the frequency control device (or speed governor) action and must be achieved within 10 seconds of the time of the Frequency increase above 50.4 Hz.  The Power Generating Module (including DC Connected Power Park Modules) or HVDC Systems shall be capable of initiating a power Frequency response with an initial delay that is as short as possible. If the delay exceeds 2 seconds the EU Generator or HVDC System Owner shall justify the variation, providing technical evidence to The Company.

(iv)	The residue of the proportional reduction in Active Power output which results from automatic action of the Power Generating Module (including DC Connected Power Park Modules) or HVDC System output control devices other than the frequency control devices (or speed governors) must be achieved within 3 minutes for the time of the Frequency increase above 50.4Hz.

(v)	For the avoidance of doubt, the LFSM-O response must be reduced when the Frequency falls again and, when to a value less than 50.4Hz, as much as possible of the increase in Active Power must be achieved within 10 seconds.

(vi)	For Type A  and  Type B Power Generating Modules which are not required to have Frequency Sensitive Mode (FSM) as described in ECC.6.3.7.3 for deviations in Frequency up to 50.9Hz at least half of the proportional reduction in Active Power  output must be achieved in 10 seconds of the time of the Frequency increase above 50.4Hz.  For deviations in Frequency beyond 50.9Hz the measured rate of change of Active Power reduction must exceed 0.5%/sec of the initial output.  The LFSM-O response must be reduced when the Frequency subsequently falls again and when to a value less than 50.4Hz, at least half the increase in  Active Power must be achieved in 10 seconds.  For a  Frequency  excursion returning from beyond 50.9Hz the measured rate of change of Active Power increase must exceed 0.5%/second.

Figure ECC.6.3.7.1 – Pref is the reference Active Power to which ΔP is related and  ΔP is the change in Active Power output from the Power Generating Module (including DC Connected Power Park Modules) or HVDC System.  The Power Generating Module (including DC Connected Power Park Modules or HVDC Systems) has to provide a negative Active Power output change with a droop of 10% or less based on Pref.

ECC.6.3.7.1.3	Each Power Generating Module (including DC Connected Power Park Modules) or HVDC Systems which is providing Limited High Frequency Response (LFSM-O) must continue to provide it until the Frequency has returned to or below 50.4Hz or until otherwise instructed by The Company.  EU Generators in respect of Gensets and HVDC Converter Station Owners in respect of an HVDC System  should also be aware of the requirements in BC.3.7.2.2.

ECC.6.3.7.1.4	Steady state operation below the Minimum Stable Operating Level in the case of Power Generating Modules including DC Connected Power Park Modules or Minimum Active Power Transmission Capacity in the case of HVDC Systems is not expected but if System operating conditions cause operation below the Minimum Stable Operating Level or Minimum Active Power Transmission Capacity which could give rise to operational difficulties for the Power Generating Module including a DC Connected Power Park Module or HVDC Systems then the EU Generator or HVDC System Owner shall be able to return the output of the Power Generating Module including a DC Connected Power Park Module to an output of not less than the Minimum Stable Operating Level  or HVDC System to an output of not less than the Minimum Active Power Transmission Capacity.

ECC.6.3.7.1.5	All reasonable efforts should in the event be made by the EU Generator or HVDC System Owner to avoid such tripping provided that the System Frequency is below 52Hz in accordance with the requirements of ECC.6.1.2.  If the System Frequency is at or above 52Hz, the requirement to make all reasonable efforts to avoid tripping does not apply and the EU Generator or HVDC System Owner is required to take action to protect its Power Generating Modules including DC Connected Power Park Modules or HVDC Converter Stations.

ECC.6.3.7.2	Limited Frequency Sensitive Mode – Underfrequency (LFSM-U)

ECC.6.3.7.2.1	Each Type C Power Generating Module and Type D Power Generating Module (including DC Connected Power Park Modules) or HVDC Systems operating in Limited Frequency Sensitive Mode shall be capable of increasing Active Power output in response to System Frequency when this falls below 49.5Hz. For the avoidance of doubt, the provision of this increase in Active Power output is not a mandatory Ancillary Service and it is not anticipated Power Generating Modules (including DC Connected Power Park Modules) or HVDC Systems are operated in an inefficient mode to facilitate delivery of LFSM-U response, but any inherent capability (where available) should be made without undue delay. The Power Generating Module (including DC Connected Power Park Modules) or HVDC Systems shall be capable of stable operation during LFSM-U Mode.  For example, an EU Generator which is operating with no headroom (eg it is operating at maximum output or is de-loading as part of a run down sequence and has no headroom) would not be required to provide LFSM-U.

ECC.6.3.7.2.2	(i)	The rate of change of Active Power output must be at a minimum a rate of 2 percent of output per 0.1 Hz deviation of System Frequency below 49.5Hz (ie a Droop of 10%) as shown in Figure ECC.6.3.7.2.2 below. This requirement only applies if the Power Generating Module has headroom and the ability to increase Active Power output.  In the case of a Power Park Module or DC Connected Power Park Module the requirements of Figure ECC.6.3.7.2.2 shall be reduced pro-rata to the amount of Power Park Units in service and available to generate.  For the avoidance of doubt, this would not preclude an EU Generator or HVDC System Owner from designing their Power Generating Module with a lower Droop setting, for example between 3 – 5%.

- As much as possible of the proportional increase in Active Power output must result from the Frequency control device (or speed governor) action and must be achieved  for Frequencies below 49.5 Hz.  The Power Generating Module (including DC Connected Power Park Modules) or HVDC Systems shall be capable of initiating a power Frequency response with minimal delay. If the delay exceeds 2 seconds the EU Generator or HVDC System  Owner shall justify the delay, providing technical evidence to The Company).

- The actual delivery of Active Power Frequency Response in LFSM-U mode shall take into account

The ambient conditions when the response is to be triggered

The operating conditions of the Power Generating Module (including DC Connected Power Park Modules) or HVDC Systems in particular limitations on operation near  Maximum Capacity or Maximum HVDC Active Power Transmission Capacity at low frequencies and the respective impact of ambient conditions as detailed in ECC.6.3.3.

The availability of primary energy sources.

- In LFSM_U Mode, the Power Generating Module (including DC Connected Power Park Modules) and HVDC Systems, shall be capable of providing a power increase up to its  Maximum Capacity or Maximum HVDC Active Power Transmission Capacity (as applicable).

Figure ECC.6.3.7.2.2 – Pref is the reference Active Power to which ΔP is related and  ΔP is the change in Active Power output from the Power Generating Module (including DC Connected Power Park Modules) or HVDC System.  The Power Generating Module (including DC Connected Power Park Modules or HVDC Systems) has to provide a positive Active Power output change with a droop of 10% or less based on Pref.

ECC.6.3.7.2.3	Limited Frequency Sensitive Mode Electricity Storage Modules when operating in an importing mode of operation

ECC.6.3.7.2.3.1	Each Generator or Defence Service Provider or Restoration Contractor or Non-Embedded Customer in respect of an Electricity Storage Module is required to meet the requirements of ECC.6.3.7.2.3.1 (a) – (f) except where it has been agreed with The Company that such an Electricity Storage Module is unable to meet these requirements in which case the requirements of OC6.6.6 shall apply:-

- Be capable of automatically maintaining its Active Power output within the shaded operating region shown in Figure ECC.6.3.7.2.3(a) until the stored energy has been depleted, except in the case of a  Restoration Contractor which shall not deplete its stored energy below the level required to meet its contractual obligations.  The Electricity Storage Module could initially be operating at any level of import between zero Active Power and the Maximum Import Power within a System Frequency range of 50Hz and 49.5Hz as shown in Figure ECC.6.3.7.2.3(a).  For the avoidance of doubt, the Electricity Storage Module would only be required to reach its Maximum Capacity if the Electricity Storage Module has headroom and the ability to increase Active Power output.  A typical value of the Droop would be 0.6% where this does not result in control system instability or plant difficulties.  In all cases the Droop shall be between 0.6% and 1.2% and shall be agreed with The Company.

- Automatically respond in accordance with the characteristic of Figure ECC.6.3.7.2.3(a) when the System Frequency falls to 49.5Hz and below.

- The reduction in Active Power import (during an import mode of operation), and the transition to the final value of Active Power output shall be continuously and linearly proportional, as far as is practicable, to the reduction in Frequency below 49.5 Hz.  Active Power output must be provided increasingly with time as required by ECC.6.3.7.2.3.1 (d) below.

- As much as possible of the proportional reduction in Active Power import (when the Electricity Storage Module is in a mode analogous to Demand) must result from the Frequency control device (or speed governor) action and must be achieved within 10 seconds of the time of the Frequency decreases below 49.5 Hz.  The Electricity Storage Module shall be capable of initiating a power Frequency response with an initial delay that is as short as possible.  Delays that exceed 2 seconds shall be justified by the Generator or Defence Service Provider or Restoration Contractor or Non-Embedded Customer providing technical evidence to The Company and in any event as much as possible of the proportional reduction in Active Power import shall be achieved within 10 seconds.  This performance requirement is to be maintained when the Electricity Storage Module makes the transition to an Active Power export mode of operation unless the energy store is depleted, in which case it shall be required to operate at zero Active Power output.

- Where the Electricity Storage Module is not capable of making a transition from import operation to export operation within 20 seconds of the System Frequency falling to 49.2Hz, then it shall then immediately reduce its Active Power import to zero.

- If the Electricity Storage Module has not achieved at least a zero Active Power import when the System Frequency has reached 48.9Hz, it shall be instantaneously tripped.  Where a Electricity Storage Module trips, it shall not be permitted to reconnect to the System until instructed by The Company in accordance with BC2.5.2 and as provided for in ECC.6.2.2.11.

Figure ECC.6.3.7.2.3(a) Active Power performance with falling frequency

ECC.6.3.7.2.3.2	Where an Electricity Storage Module has been importing and has responded in accordance with the requirements of ECC.6.3.7.2.3.1, its performance, once the System Frequency starts to rise above the minimum reached, shall be in accordance with Figure ECC.6.3.7.2.3(b) in respect of the Active Power output and Active Power import.  For example, Figure ECC.6.3.7.2.3(b), illustrates the four operating points W, X, Y and Z.  If points W, X, Y and Z denotes the minimum frequency that the Total System reached during a particular low System Frequency event, as the System Frequency starts to rise, the Active Power output of the Electricity Storage Module should remain at a constant level (where the energy source has not been depleted) until 49.5Hz is reached as denoted by the dashed black lines.  Once the System Frequency has risen above 49.5Hz the Electricity Storage Module is permitted to reduce Active Power output so long as it is operates within the shaded area above 49.5Hz shown in Figure ECC.6.3.7.2.3(b), unless the Electricity Storage Module has insufficient capability in which case it shall operate at zero Active Power.

Figure ECC.6.3.7.2.3(b) Active Power performance with increasing frequency

ECC.6.3.7.2.3.3 Where an Electricity Storage Module is exporting Active Power to the Total System (including zero) and the System Frequency falls below 49.5Hz the requirements of ECC.6.3.7.2.1 and ECC.6.3.7.2.2 shall apply.

ECC.6.3.7.3	Frequency Sensitive Mode – (FSM)

ECC.6.3.7.3.1	In addition to the requirements of ECC.6.3.7.1 and ECC.6.3.7.2 each Type C Power Generating  Module and Type D Power Generating Module (including DC Connected Power Park Modules) or HVDC Systems must be fitted with a fast acting proportional Frequency control device (or turbine speed governor) and unit load controller or equivalent control device to provide Frequency response under normal operational conditions in accordance with Balancing Code 3 (BC3). In the case of a Power Park Module including a DC Connected Power Park Module, the Frequency or speed control device(s) may be on the Power Park Module (including a DC Connected Power Park Module) or on each individual Power Park Unit (including a Power Park Unit within a DC Connected Power Park Module) or be a combination of both. The Frequency control  device(s) (or speed governor(s)) must be designed and operated to the appropriate:

- European Specification: or

- in the absence of a relevant European Specification, such other standard which is in common use within the European Community (which may include a manufacturer specification);

as at the time when the installation of which it forms part was designed or (in the case of modification or alteration to the Frequency control device (or turbine speed governor)) when the modification or alteration was designed.

The European Specification or other standard utilised in accordance with sub paragraph ECC.6.3.7.3.1 (a) (ii) will be notified to The Company by the EU Generator or HVDC System Owner:

(i)	as part of the application for a Bilateral Agreement; or

(ii)	as part of the application for a varied Bilateral Agreement; or

(iii) 	in the case of an Embedded Development, within 28 days of entry into the Embedded Development Agreement (or such later time as agreed with The Company) or

(iv) as soon as possible prior to any modification or alteration to the Frequency control device (or governor); and

ECC.6.3.7.3.2	The Frequency control device (or speed governor) in co-ordination with other control devices must control each Type C Power Generating Module and Type D Power Generating Module (including DC Connected Power Park Modules) or HVDC Systems Active Power Output or Active Power transfer capability with stability over the entire operating range of the Power Generating Module (including DC Connected Power Park Modules) or HVDC Systems ; and

ECC.6.3.7.3.3	Type C and Type D Power Generating Modules and DC Connected Power Park Modules shall also meet the following minimum requirements:

- capable of providing Active Power Frequency response in accordance with the performance characteristic shown in Figure 6.3.7.3.3(a) and parameters in Table 6.3.7.3.3(a)

Figure 6.3.7.3.3(a) – Frequency Sensitive Mode capability of Power Generating Modules and DC Connected Power Park Modules

| Parameter | Setting |
| --- | --- |
| Nominal System Frequency | 50Hz |
| Active Power as a percentage of Maximum Capacity (ǀΔP1ǀPmax) | 10% |
| Frequency Response Insensitivity in mHz (ǀΔfiǀ) | ±15mHz |
| Frequency Response Insensitivity as a percentage of nominal frequency (ǀΔfiǀfn) | ±0.03% |
| Frequency Response Deadband in mHz | 0 (mHz) |
| Droop (%) | 3 – 5% |

Table 6.3.7.3.3(a) – Parameters for Active Power Frequency response in Frequency Sensitive Mode including the mathematical expressions in Figure 6.3.7.3.3(a).

- In satisfying the performance requirements specified in ECC.6.3.7.3(i) EU Generators in respect of each Type C and Type D Power Generating Modules and DC Connected Power Park Module should be aware:-

in the case of overfrequency, the Active Power Frequency response is limited by the Minimum Regulating Level,

in the case of underfrequency, the Active Power Frequency response is limited by the  Maximum Capacity,

the actual delivery of Active Power frequency response depends on the operating and ambient conditions of the Power Generating Module (including DC Connected Power Park Modules) when this response is triggered, in particular limitations on operation near Maximum Capacity at low Frequencies as specified in ECC.6.3.3 and available primary energy sources.

The frequency control device (or speed governor) must also be capable of being set so that it operates with an overall speed Droop of between 3 – 5%.  The Frequency Response Deadband and Droop must be able to be reselected repeatedly.  For the avoidance of doubt, in the case of a Power Park Module (including DC Connected Power Park Modules) the speed Droop should be equivalent of a fixed setting between 3% and 5% applied to each Power Park Unit in service.

- In the event of a Frequency step change, each Type C and Type D Power Generating Module and DC Connected Power Park Module shall be capable of activating full and stable Active Power Frequency response (without undue power oscillations), in accordance with the performance characteristic shown in Figure 6.3.7.3.3(b) and parameters in Table 6.3.7.3.3(b).

Figure 6.3.7.3.3(b) Active Power Frequency Response capability.

| Parameter | Setting |
| --- | --- |
| Active Power as a percentage of Maximum Capacity (frequency response range) (ǀΔP1ǀPmax) | 10% |
| Maximum admissible initial delay t1 for Power Generating Modules (including DC Connected Power Park Modules) with inertia unless justified as specified in ECC.6.3.7.3.3 (iv) | 2 seconds |
| Maximum admissible initial delay t1 for Power Generating Modules (including DC Connected Power Park Modules) which do not contribute to System inertia unless justified as specified in ECC.6.3.7.3.3 (iv) | 1 second |
| Activation time t2 | 10 seconds |

Table 6.3.7.3.3(b) – Parameters for full activation of Active Power Frequency response resulting from a Frequency step change. Table 6.3.7.3.3(b) also includes the mathematical expressions used in Figure 6.3.7.3.3(b).

- The initial activation of Active Power Primary Frequency response  shall not be unduly delayed.  For Type C and Type D Power Generating Modules (including DC Connected Power Park Modules) with inertia the delay in initial Active Power Frequency response shall not be greater than 2 seconds. For Type C and Type D Power Generating Modules (including DC Connected Power Park Modules) without inertia, the delay in initial Active Power Frequency response shall not be greater than 1 second.  If the Generator cannot meet this requirement they shall provide technical evidence to The Company demonstrating why a longer time is needed for the initial activation of Active Power Frequency response.

- in the case of Type C and Type D Power Generating Modules (including DC Connected Power Park Modules) other than the Steam Unit within a CCGT Module the combined effect of the Frequency Response Insensitivity and Frequency Response Deadband  of the Frequency control device (or speed governor) should be no greater than 0.03Hz (for the avoidance of doubt, ±0.015Hz).  In the case of the Steam Unit within a CCGT Module, the Frequency Response Deadband  should be set to an appropriate value consistent with the requirements of ECC.6.3.7.3.5(ii) and the requirements of BC3.7.2.2 for the provision of LFSM-O taking account of any Frequency Response Insensitivity of the Frequency control device (or speed governor);

ECC.6.3.7.3.4	HVDC Systems shall also meet the following minimum requirements:

- HVDC Systems shall be capable of responding to Frequency deviations in each connected AC System  by adjusting their Active Power import or export as shown in Figure 6.3.7.3.4(a) with the corresponding parameters in Table 6.3.7.3.4(a).

Figure 6.3.7.3.4(a) – Active Power frequency response capability of a HVDC  System operating in Frequency Sensitive Mode (FSM). ΔΡ is the change in active power output from the HVDC System..

| Parameter | Setting |
| --- | --- |
| Frequency Response Deadband | 0 |
| Droop S1 and S2 (upward and downward regulation) where S1=S2. | 3 – 5% |
| Frequency Response Insensitivity | ±15mHz |

Table 6.3.7.3.4(a) – Parameters for Active Power Frequency response in FSM including the mathematical expressions in Figure 6.3.7.3.4.

- Each HVDC System  shall be capable of adjusting the Droop for both upward and downward regulation and the Active Power range over which Frequency Sensitive Mode of operation is available as defined in ECC.6.3.7.3.4.

- In addition to the requirements in ECC.6.3.7.4(i) and ECC.6.3.7.4(ii) each HVDC System shall be capable of:-

delivering the response as soon as technically feasible

delivering the response on or above the solid line in Figure 6.3.7.3.4(b) in accordance with the parameters shown in Table 6.3.7.3.4(b)

initiating the delivery of Primary Response in no less than 0.5 seconds unless otherwise agreed with The Company.  Where the initial delay time (t1 – as shown in Figure 6.3.7.3.4(b)) is longer than 0.5 seconds the HVDC Converter Station Owner shall reasonably justify it to The Company.

Figure 6.3.7.3.4(b) Active Power Frequency Response capability of a HVDC System.  ΔP is the change in Active Power triggered by the step change in frequency

| Parameter | Setting |
| --- | --- |
| Active Power as a percentage of Maximum Capacity (frequency response range) (ǀΔP1ǀPmax) | 10% |
| Maximum admissible delay t1 | 0.5 seconds |
| Maximum admissible time for full activation t2, unless longer activation times are agreed with The Company | 10 seconds |

Table 6.3.7.3.4(b) – Parameters for full activation of Active Power Frequency response resulting from a Frequency step change.

- For HVDC Systems connecting various Synchronous Areas, each HVDC System shall be capable of adjusting the full Active Power Frequency Response when operating in Frequency Sensitive Mode at any time and for a continuous time period.   In addition, the Active Power controller of each HVDC System shall not have any adverse impact on the delivery of frequency response.

ECC.6.3.7.3.5	For HVDC Systems and  Type C and Type D Power Generating Modules (including DC Connected Power Park Modules),  other than the Steam Unit within a CCGT Module the combined effect of the Frequency Response Insensitivity and Frequency Response Deadband of the Frequency control device (or speed governor) should be no greater than 0.03Hz (for the avoidance of doubt, ±0.015Hz).  In the case of the Steam Unit within a CCGT Module, the Frequency Response Deadband  should be set to an appropriate value consistent with the requirements of ECC.6.3.7.3.5(ii) and the requirements of BC3.7.2.2 for the provision of LFSM-O taking account of any Frequency Response Insensitivity of the Frequency control device (or speed governor);

(i)	With regard to disconnection due to underfrequency, EU Generators responsible for Type C and Type D Power Generating Modules (including DC Connected Power Park Modules) capable of acting as a load, including but not limited to Pumped Storage and tidal  Power Generating Modules, HVDC Systems  and  Remote End HVDC Converter Stations  , shall be capable of disconnecting their load in case of underfrequency which will be agreed with The Company. For the avoidance of doubt this requirement does not apply to station auxiliary supplies;  EU Generators in respect of Type C and Type D Pumped Storage Power Generating Modules should also be aware of the requirements in OC.6.6.6.

- Where a Type C or Type D Power Generating Module, DC Connected Power Park Module or HVDC System becomes isolated from the rest of the Total System but is still supplying Customers, the Frequency control device (or speed governor) must also be able to control System Frequency below 52Hz unless this causes the Type C or Type D Power Generating Module or DC Connected Power Park Module to operate below its Minimum Regulating Level or Minimum Active Power Transmission Capacity when it is possible that it may, as detailed in BC 3.7.3, trip after a time. For the avoidance of doubt Power Generating Modules (including DC Connected Power Park Modules) and HVDC Systems  are only required to operate within the System Frequency range 47 - 52 Hz as defined in ECC.6.1.2 and for converter based technologies, the remaining island contains sufficient fault level for effective commutation;

- Each Type C and Type D Power Generating Module and HVDC Systems shall have the facility to modify the Target Frequency setting either continuously or in a maximum of 0.05Hz steps over at least the range 50 ±0.1Hz should be provided in the unit load controller or equivalent device.

ECC.6.3.7.3.6	In addition to the requirements of ECC.6.3.7.3 each Type C and Type D Power Generating Module  and HVDC System shall be capable of meeting the minimum Frequency response requirement profile subject to and in accordance with the provisions of Appendix A3.

ECC.6.3.7.3.7	For the avoidance of doubt, the requirements of Appendix A3 do not apply to Type A and Type B Power Generating Modules.

ECC.6.3.7.3.8	Frequency control device (or speed governor) requirements during System Restoration

ECC.6.3.7.3.8.1		Restoration Contractors shall be capable of operating their Generating Units or Power Generating Modules or HVDC Systems such that the Frequency control device (or turbine speed governor) and unit load controller or equivalent control device can be switched to Frequency control only with no load influence, during the early stages of a System Restoration whilst in island operation.

ECC.6.3.7.8.3.2	Generators and HVDC System Owners shall advise The Company of the capability of operating their Generating Units or Power Generating Modules or HVDC Systems such that the Frequency control device (or turbine speed governor) and unit load controller or equivalent control device can be switched to Frequency control only with no load influence during the early stages of System Restoration whilst in island operation. If there is a suitable capability, The Company and the User shall agree on how it shall be used and kept available.

ECC.6.3.7.8.3.3 		In addition to the requirements of ECC.6.3.7.8.3.1 and ECC.6.3.7.8.3.2 the following shall 	apply:-

(i) 	Changes to any control schemes and settings identified from ECC.6.3.7.8.3.1, and ECC.6.3.7.8.3.2 shall be agreed between The Company and/or Relevant Transmission Licensee and/or Network Operator as recorded in the Restoration Plan.

(ii)	During System Restoration, any changes to the schemes and settings defined in ECC.6.3.7.8.3.1 and ECC.6.3.7.8.3.2, of the different control devices of the Generating Unit or Power Generating Module or Restoration Contractor’s Plant or HVDC System shall be coordinated and agreed between the Relevant Transmission Licensee, the EU Generator, Restoration Contractor and HVDC System Owner as part of a Restoration Plan.

ECC.6.3.8		EXCITATION AND VOLTAGE CONTROL PERFORMANCE REQUIREMENTS

ECC.6.3.8.1		Excitation Performance Requirements for Type B Synchronous Power Generating Modules

ECC.6.3.8.1.1	Each Synchronous Generating Unit within a Type B Synchronous Power Generating Module shall be equipped with a permanent automatic excitation control system that shall have the capability to provide constant terminal voltage control at a selectable setpoint without instability over the entire operating range of the Type B Synchronous Power Generating Module.

ECC.6.3.8.1.2	In addition to the requirements of ECC.6.3.8.1.1, The Company or the relevant Network Operator will specify if the control system of the Type B Synchronous Power Generating Module shall contribute to voltage control or Reactive Power control or Power Factor control at the Grid Entry Point or User System Entry Point (or other defined busbar).  The performance requirements of the control system including slope (where applicable) shall be agreed between The Company and/or the relevant Network Operator and the EU Generator.

ECC.6.3.8.2	Voltage Control Requirements for Type B Power Park Modules

ECC.6.3.8.2.1	The Company or the relevant Network Operator will specify if the control system of the Type B Power Park Module shall contribute to voltage control or Reactive Power control or Power Factor control at the Grid Entry Point or User System Entry Point (or other defined busbar).  The performance requirements of the control system including slope  (where applicable) shall be agreed between The Company and/or the relevant Network Operator and the EU Generator.

ECC.6.3.8.3		Excitation Performance Requirements for Type C and Type D Onshore Synchronous Power Generating Modules

ECC.6.3.8.3.1	Each Synchronous Generating Unit within a Type C and Type D Onshore Synchronous Power Generating Modules shall be equipped with a permanent automatic excitation control system that shall have the capability to  provide constant terminal voltage control at a selectable setpoint without instability over the entire operating range of the Synchronous Power Generating Module.

ECC.6.3.8.3.2	The requirements for excitation control facilities are specified in ECC.A.6. Any site specific requirements shall be specified by The Company or the relevant Network Operator.

ECC.6.3.8.3.3	Unless otherwise required for testing in accordance with OC5.A.2, the automatic excitation control system of an Onshore Synchronous Power Generating Module shall always be operated such that it controls the Onshore Synchronous Generating Unit terminal voltage to a value that is

- equal to its rated value: or

- only where provisions have been made in the Bilateral Agreement, greater than its rated value.

ECC.6.3.8.3.4	In particular, other control facilities including constant Reactive Power output control modes and constant Power Factor control modes (but excluding VAR limiters) are not required. However if present in the excitation or voltage control system they will be disabled unless otherwise agreed with The Company or the relevant Network Operator.  Operation of such control facilities will be in accordance with the provisions contained in BC2.

ECC.6.3.8.3.5	The excitation performance requirements for Offshore Synchronous Power Generating Modules with an Offshore Grid Entry Point shall be specified by The Company.

ECC.6.3.8.4		Voltage Control Performance Requirements for Type C and Type D Onshore Power Park Modules, Onshore HVDC Converters  and OTSUW Plant and Apparatus at the Interface Point

ECC.6.3.8.4.1		Each Type C and Type D Onshore Power Park Module, Onshore HVDC Converter and OTSDUW Plant and Apparatus shall be fitted with a continuously acting automatic control system to provide control of the voltage at the Grid Entry Point or User System Entry Point  (or Interface Point in the case of OTSDUW Plant and Apparatus) without instability over the entire operating range of the Onshore Power Park Module, or Onshore HVDC Converter or OTSDUW Plant and Apparatus. Any Plant or Apparatus used in the provisions of such voltage control within an Onshore Power Park Module may be located at the Power Park Unit terminals, an appropriate intermediate busbar or the Grid Entry Point or User System Entry Point. In the case of an Onshore HVDC Converter at a HVDC Converter Station any Plant or Apparatus used in the provisions of such voltage control may be located at any point within the User’s Plant and Apparatus including the Grid Entry Point or User System Entry Point. OTSDUW Plant and Apparatus used in the provision of such voltage control may be located at the Offshore Grid Entry Point an appropriate intermediate busbar or at the Interface Point. When operating below 20% Maximum Capacity the automatic control system may continue to provide voltage control using any available reactive capability. If voltage control is not being provided, the automatic control system shall be designed to ensure a smooth transition between the shaded area below 20% of Active Power output and the non-shaded area above 20% of Active Power output in Figure ECC.6.3.2.4(c) and Figure ECC.6.3.2.6(b) The performance requirements for a continuously acting automatic voltage control system that shall be complied with by the User in respect of Onshore Power Park Modules, Onshore HVDC Converters at an Onshore HVDC Converter Station, OTSDUW Plant and Apparatus at the Interface Point are defined in ECC.A.7.

ECC.6.3.8.4.3	In particular, other control facilities, including constant Reactive Power output control modes and constant Power Factor control modes (but excluding VAR limiters) are not required. However if present in the voltage control system they will be disabled unless otherwise agreed with The Company or the relevant Network Operator. Operation of such control facilities will be in accordance with the provisions contained in BC2. Where Reactive Power output control modes and constant Power Factor control modes have been fitted within the voltage control system they shall be required to satisfy the requirements of ECC.A.7.3 and ECC.A.7.4.

ECC.6.3.8.5	Excitation Control Performance requirements applicable to AC Connected Offshore Synchronous Power Generating Modules and voltage control performance requirements applicable to AC connected Offshore Power Park Modules, DC Connected Power Park Modules and Remote End HVDC Converters

ECC.6.3.8.5.1	A continuously acting automatic control system is required to provide control of Reactive Power (as specified in ECC.6.3.2.5 and ECC.6.3.2.6) at the Offshore Grid Entry  Point (or HVDC Interface  Point in the case of Configuration 1 DC Connected Power Park Modules and Remote End HVDC Converters) without instability over the entire operating range of the AC connected Offshore Synchronous Power Generating Module or Configuration 1 AC connected Offshore Power Park Module or Configuration 1 DC Connected Power Park Modules or Remote End HVDC Converter.  The performance requirements for this automatic control system will be specified by The Company which would be consistent with the requirements of ECC.6.3.2.5 and ECC.6.3.2.6.

ECC.6.3.8.5.2	A continuously acting automatic control system is required to provide control of Reactive Power (as specified in ECC.6.3.2.8) at the Offshore Grid Entry Point (or HVDC Interface  Point in the case of Configuration 2 DC Connected Power Park Modules) without instability over the entire operating range of the Configuration 2 AC connected Offshore Power Park Module or Configuration 2 DC Connected Power Park Modules. otherwise the requirements of ECC.6.3.2.6 shall apply.  The performance requirements for this automatic control system are specified in ECC.A.8

ECC.6.3.8.5.3	In addition to ECC.6.3.8.5.1 and ECC.6.3.8.5.2 the requirements for excitation or voltage control facilities, including Power System Stabilisers, where these are necessary for system reasons, will be specified by The Company.  Reference is made to on-load commissioning witnessed by The Company in BC2.11.2.

ECC.6.3.9	STEADY STATE LOAD INACCURACIES

ECC.6.3.9.1	The standard deviation of Load error at steady state Load over a 30 minute period must not exceed 2.5 per cent of a Type C or Type D Power Generating Modules (including a DC Connected Power Park Module) Maximum Capacity.  Where a Type C or Type D Power Generating Module (including a DC Connected Power Park Module)  is instructed to Frequency sensitive operation, allowance will be made in determining whether there has been an error according to the governor droop characteristic registered under the PC.

For the avoidance of doubt in the case of a Power Park Module (excluding a Non-Synchronous Electricity Storage Module) an allowance will be made for the full variation of mechanical power output.

In the case of an Electricity Storage Module, an allowance will be made for the storage reserve capability of the Electricity Storage Module.

ECC.6.3.10	NEGATIVE PHASE SEQUENCE LOADINGS

ECC.6.3.10.1	In addition to meeting the conditions specified in ECC.6.1.5(b), each Synchronous Power Generating Module will be required to withstand, without tripping, the negative phase sequence loading incurred by clearance of a close-up phase-to-phase fault, by System Back-Up Protection on the National Electricity Transmission System or User System located Onshore in which it is Embedded.

ECC.6.3.11	NEUTRAL EARTHING

ECC.6.3.11	At nominal System voltages of 110kV and above the higher voltage windings of a transformer of a Power Generating Module or HVDC Equipment  or transformer resulting from OTSDUW must be star connected with the star point suitable for connection to earth.  The earthing and lower voltage winding arrangement shall be such as to ensure that the Earth Fault Factor requirement of paragraph ECC.6.2.1.1 (b) will be met on the National Electricity Transmission System at nominal System voltages of 110kV and above.

ECC.6.3.12	FREQUENCY AND VOLTAGE DEVIATIONS

ECC.6.3.12.1	As stated in ECC.6.1.2, the System Frequency could rise to 52Hz or fall to 47Hz. Each Power Generating Module (including DC Connected Power Park Modules) must continue to operate within this Frequency range for at least the periods of time given in ECC.6.1.2 unless The Company has specified  any  requirements for combined Frequency and voltage deviations  which are required to ensure the best use of technical capabilities of Power Generating Modules (including DC Connected Power Park Modules) if required to preserve or restore system security.  Notwithstanding this requirement, EU Generators should also be aware of the requirements of ECC.6.3.13.

ECC.6.3.13	 FREQUENCY, RATE OF CHANGE OF FREQUENCY AND VOLATGE PROTECTION SETTING ARRANGEMENTS

ECC.6.3.13.1	EU Generators (including in respect of OTSDUW Plant and Apparatus) and HVDC System Owners will be responsible for protecting all their Power Generating Modules (and OTSDUW Plant and Apparatus) or HVDC Equipment against damage should Frequency excursions outside the range 52Hz to 47Hz ever occur. Should such excursions occur, it is up to the EU Generator or HVDC System Owner to decide whether to disconnect their Apparatus for reasons of safety of Apparatus, Plant and/or personnel.

ECC.6.3.13.2	Each Power Park Module with a Grid Forming Capability as provided for in ECC.6.3.19, when connected and synchronised to the System, is required to be capable of withstanding without tripping a rate of change of Frequency up to and including 2 Hz per second as measured over a rolling 500 milliseconds period.  All other Power Generating Modules when connected and synchronised to the System, shall be capable of withstanding without tripping a rate of change of Frequency up to and including 1 Hz per second as measured over a rolling 500 milliseconds period.  Voltage dips may cause localised rate of change of Frequency values in excess of 1 Hz per second (or 2Hz/s in the case of Power Park Modules with a Grid Forming Capability) for short periods, and in these cases, the requirements under ECC.6.3.15 (fault ride through) supersedes this clause. For the avoidance of doubt, this requirement relates to the capabilities of Power Generating Modules only and does not impose the need for rate of change of Frequency protection nor does it impose a specific setting for anti-islanding or loss-of-mains protection relays.

ECC.6.3.13.3	Each HVDC System and Remote End HVDC Converter Station when connected and synchronised to the System, shall be capable of withstanding without tripping a rate of change of Frequency up to and including ±2.5Hz per second as measured over the previous 1 second period.  Voltage dips may cause localised rate of change of Frequency values in excess of ±2.5 Hz per second for short periods, and in these cases, the requirements under ECC.6.3.15 (fault ride through) supersedes this clause. For the avoidance of doubt, this requirement relates to the capabilities of HVDC Systems  and Remote End HVDC Converter Stations only and does not impose the need for rate of change of Frequency protection nor does it impose a specific setting for anti-islanding or loss-of-mains protection relays.

ECC.6.3.13.4	Each  DC Connected  Power Park Module when connected to the System, shall be capable of withstanding without tripping a rate of change of Frequency up to and including ±2.0Hz per second as measured over the previous 1 second period.  Voltage dips may cause localised rate of change of Frequency values in excess of ±2.0 Hz per second for short periods, and in these cases, the requirements under ECC.6.3.15 (fault ride through) supersedes this clause. For the avoidance of doubt, this requirement relates to the capabilities of DC Connected Power Park Modules only and does not impose the need for rate of change of Frequency protection nor does it impose a specific setting for anti-islanding or loss-of-mains protection relays.

ECC.6.3.13.5		As stated in ECC.6.1.2, the System Frequency could rise to 52Hz or fall to 47Hz and the System voltage at the Grid Entry Point or User System Entry Point could rise or fall within the values outlined in ECC.6.1.4. Each Type C and Type D Power Generating Module (including DC Connected Power Park Modules) or any constituent element must continue to operate within this Frequency range for at least the periods of time given in ECC.6.1.2 and voltage range as defined in ECC.6.1.4  unless The Company has agreed to any simultaneous overvoltage and underfrequency relays and/or simultaneous undervoltage and over frequency relays which will trip such Power Generating Module (including DC Connected Power Park Modules), and any constituent element within this Frequency or voltage range. In the case of Grid Forming Plant, Grid Forming Plant Owners are also required to satisfy the System Frequency and System voltage requirements as defined in ECC.6.3.19.

ECC.6.3.14	FAST START CAPABILITY

ECC.6.3.14.1	It may be agreed in the Bilateral Agreement that a Genset shall have a Fast-Start Capability.  Such Gensets may be used for Operating Reserve and their Start-Up may be initiated by Frequency-level relays with settings in the range 49Hz to 50Hz as specified pursuant to OC2.

ECC.6.3.15	FAULT RIDE THROUGH

ECC.6.3.15.1	General Fault Ride Through requirements, principles and concepts applicable to Type B, Type C and Type D Power Generating Modules and OTSDUW Plant and Apparatus subject to faults up to 140ms in duration

ECC.6.3.15.1.1	ECC.6.3.15.1 – ECC.6.3.15.8 section sets out the Fault Ride Through requirements on Type B, Type C and Type D Power Generating Modules, OTSDUW Plant and Apparatus and HVDC Equipment  that shall apply in the event of a fault lasting up to 140ms in duration.

ECC.6.3.15.1.2		Each Power Generating Module, Power Park Module, HVDC Equipment and OTSDUW Plant and Apparatus is required to remain connected and stable for any balanced and unbalanced fault where the voltage at the Grid Entry Point or User System Entry Point  or (HVDC Interface Point in the case of Remote End DC Converter Stations  or Interface Point in the case of OTSDUW Plant and Apparatus) remains on or above the heavy black line defined in sections ECC.6.3.15.2 – ECC.6.3.15.7 below. For up to 30 minutes following such a fault event each Power Generating Module, Power Park Module, HVDC Equipment and OTSDUW Plant and Apparatus is required to remain connected and stable provided System operating conditions have returned within those specified in ECC.6.1.

ECC.6.3.15.1.3	The voltage against time curves defined in ECC.6.3.15.2 – ECC.6.3.15.7 expresses the lower limit (expressed as the ratio of its actual value and its reference 1pu) of the actual course of the phase to phase voltage (or phase to earth voltage in the case of asymmetrical/unbalanced faults) on the System voltage level at the Grid Entry Point or User System Entry Point (or HVDC Interface Point in the case of Remote End HVDC Converter Stations or Interface Point in the case of OTSDUW Plant and Apparatus) during a symmetrical or asymmetrical/unbalanced fault, as a function of time before, during and after the fault.

ECC.6.3.15.2	Voltage against time curve and parameters applicable to Type B Synchronous Power Generating Modules

Figure ECC.6.3.15.2 - Voltage against time curve applicable to Type B Synchronous Power Generating Modules

| Voltage parameters (pu) |  | Time parameters (seconds) |  |
| --- | --- | --- | --- |
| Uret | 0.3 | tclear | 0.14 |
| Uclear | 0.7 | trec1 | 0.14 |
| Urec1 | 0.7 | trec2 | 0.45 |
| Urec2 | 0.9 | trec3 | 1.5 |

Table ECC.6.3.15.2 Voltage against time parameters applicable to Type B

Synchronous Power Generating Modules

ECC.6.3.15.3	Voltage against time curve and parameters applicable to Type C and D Synchronous Power Generating Modules connected below 110kV

Figure ECC.6.3.15.3 - Voltage against time curve applicable to Type C and D Synchronous Power Generating Modules connected below 110kV

| Voltage parameters (pu) |  | Time parameters (seconds) |  |
| --- | --- | --- | --- |
| Uret | 0.1 | tclear | 0.14 |
| Uclear | 0.7 | trec1 | 0.14 |
| Urec1 | 0.7 | trec2 | 0.45 |
| Urec2 | 0.9 | trec3 | 1.5 |

Table ECC.6.3.15.3 Voltage against time parameters applicable to Type C and D Synchronous Power Generating Modules connected below 110kV

ECC.6.3.15.4	Voltage against time curve and parameters applicable to Type D Synchronous Power Generating Modules connected at or above 110kV

Figure ECC.6.3.15.4 - Voltage against time curve applicable to Type D Synchronous Power Generating Modules connected at or above 110kV

| Voltage parameters (pu) |  | Time parameters (seconds) |  |
| --- | --- | --- | --- |
| Uret | 0 | tclear | 0.14 |
| Uclear | 0.25 | trec1 | 0.25 |
| Urec1 | 0.5 | trec2 | 0.45 |
| Urec2 | 0.9 | trec3 | 1.5 |

Table ECC.6.3.15.4 Voltage against time parameters applicable to Type D Synchronous Power Generating Modules connected at or above 110kV

ECC.6.3.15.5	Voltage against time curve and parameters applicable to Type B, C and D Power Park Modules connected below 110kV

Figure ECC.6.3.15.5 - Voltage against time curve applicable to Type B, C and D Power Park Modules connected below 110kV

| Voltage parameters (pu) |  | Time parameters (seconds) |  |
| --- | --- | --- | --- |
| Uret | 0.10 | tclear | 0.14 |
| Uclear | 0.10 | trec1 | 0.14 |
| Urec1 | 0.10 | trec2 | 0.14 |
| Urec2 | 0.85 | trec3 | 2.2 |

Table ECC.6.3.15.5 Voltage against time parameters applicable to Type B, C and D Power Park Modules connected below 110kV

ECC.6.3.15.6	Voltage against time curve and parameters applicable to Type D Power Park Modules with a Grid Entry Point or User System Entry Point at or above 110kV, DC Connected Power Park Modules at the HVDC Interface Point or OTSDUW Plant and Apparatus at the Interface Point.

Figure ECC.6.3.15.6 -  Voltage against time curve applicable to Type D Power Park Modules with a Grid Entry Point or User System Entry Point at or above 110kV, DC Connected Power Park Modules at the HVDC Interface Point or OTSDUW Plant and Apparatus at the Interface Point.

| Voltage parameters (pu) |  | Time parameters (seconds) |  |
| --- | --- | --- | --- |
| Uret | 0 | tclear | 0.14 |
| Uclear | 0 | trec1 | 0.14 |
| Urec1 | 0 | trec2 | 0.14 |
| Urec2 | 0.85 | trec3 | 2.2 |

Table ECC.6.3.15.6 	Voltage against time parameters applicable to a  Type D Power Park Modules with a Grid Entry Point or User System Entry Point at or above 110kV, DC Connected Power Park Modules at the HVDC Interface Point or OTSDUW Plant and Apparatus at the Interface Point.

ECC.6.3.15.7	Voltage against time curve and parameters applicable to HVDC Systems and Remote End HVDC Converter Stations

Figure ECC.6.3.15.7 - Voltage against time curve applicable to HVDC Systems and Remote End HVDC Converter Stations

| Voltage parameters (pu) |  | Time parameters (seconds) |  |
| --- | --- | --- | --- |
| Uret | 0 | tclear | 0.14 |
| Uclear | 0 | trec1 | 0.14 |
| Urec1 | 0 | trec2 | 0.14 |
| Urec2 | 0.85 | trec3 | 2.2 |

Table ECC.6.3.15.7 Voltage against time parameters applicable to HVDC Systems and Remote End HVDC Converter Stations

ECC.6.3.15.8	In addition to the requirements in ECC.6.3.15.1 – ECC.6.3.15.7:

- Each Type B, Type C and Type D Power Generating Module at the Grid Entry Point or User System Entry Point, HVDC Equipment (or OTSDUW Plant and Apparatus at the Interface Point) shall be capable of satisfying the above requirements when operating at Rated MW output and maximum leading Power Factor.

- The Company will specify upon request by the User the pre-fault and post fault short circuit capacity (in MVA) at the Grid Entry  Point or User System Entry Point (or HVDC Interface Point in the case of a remote end HVDC Converter Stations or Interface Point in the case of OTSDUW Plant and Apparatus).

- The pre-fault voltage shall be taken to be 1.0pu and the post fault voltage shall not be less than  0.9pu.

- To allow a User to model the Fault Ride Through performance of its Type B, Type C and/or Type D Power Generating Modules or HVDC Equipment, The Company will provide additional network data as may reasonably be required by the EU Code User to undertake such study work in accordance with PC.A.8. Alternatively, The Company may provide generic values derived from typical cases.

(v)	The Company will publish fault level data under maximum and minimum demand conditions in the Electricity Ten Year Statement.

(vi)	Each EU Generator (in respect of Type B, Type C, Type D Power Generating Modules and DC Connected Power Park Modules) and HVDC System Owners (in respect of HVDC Systems) shall satisfy the requirements in ECC.6.3.15.8(i) – (vii) unless the protection schemes and settings for internal electrical faults trips  the Type B, Type C and Type D Power Generating Module, HVDC Equipment (or OTSDUW Plant and Apparatus) from the System. The protection schemes and settings should not jeopardise Fault Ride Through performance as specified in ECC.6.3.15.8(i) – (vii). The undervoltage protection at the Grid Entry Point or User System Entry  Point (or HVDC Interface Point in the case of a Remote End HVDC Converter Stations or Interface Point in the case of OTSDUW Plant and Apparatus) shall be set by the EU Generator (or HVDC System Owner or OTSDUA in the case of OTSDUW Plant and Apparatus) according to the widest possible range unless The Company and the EU Code User have agreed to narrower settings.  All protection settings associated with undervoltage protection shall be agreed between the EU Generator and/or HVDC System Owner with The Company and Relevant Transmission Licensee’s and relevant Network Operator (as applicable).

(vii) 	Each Type B, Type C and Type D Power Generating Module, HVDC System and OTSDUW Plant and Apparatus at the Interface Point shall be designed such that upon clearance of the fault on the Onshore Transmission System and within 0.5 seconds of restoration of the voltage at the Grid Entry Point or User System Entry Point or HVDC Interface Point in the case of  a Remote End HVDC Converter Stations or Interface Point in the case of OTSDUW Plant and Apparatus to 90% of nominal voltage or greater, Active Power output (or Active Power transfer capability in the case of OTSDW Plant and Apparatus or Remote End HVDC Converter Stations) shall be restored to at least 90% of the level immediately before the fault.  Once Active Power output (or Active Power transfer capability in the case of OTSDUW Plant and Apparatus or Remote End HVDC Converter Stations) has been restored to the required level, Active Power oscillations shall be acceptable provided that:

- The total Active Energy delivered during the period of the oscillations is at least that which would have been delivered if the Active Power was constant

- The oscillations are adequately damped.

- In the event of power oscillations, Power Generating Modules shall retain steady state stability when operating at any point on the Power Generating Module Performance Chart.

For AC Connected Onshore and Offshore Power Park Modules comprising switched reactive compensation equipment (such as mechanically switched capacitors and reactors), such switched reactive compensation equipment shall be controlled such that it is not switched in or out of service during the fault but may act to assist in post fault voltage recovery.

ECC.6.3.15.9	General Fault Ride Through requirements for faults in excess of 140ms in duration.

ECC.6.3.15.9.1	General Fault Ride Through requirements applicable to HVDC Equipment and OTSDUW DC Converters subject to faults and voltage dips in excess of 140ms.

ECC.6.3.15.9.1.1	The requirements applicable to HVDC Equipment including OTSDUW DC Converters subject to faults and voltage disturbances at the Grid Entry Point or User System Entry Point or Interface Point or HVDC Interface Point, including Active Power transfer capability shall be specified in the Bilateral Agreement.

ECC.6.3.15.9.2 	Fault Ride Through requirements for Type C and Type D Synchronous Power Generating Modules and Type C and Type D Power Park Modules  and OTSDUW Plant and Apparatus subject to faults and voltage disturbances on the Onshore Transmission System in excess of 140ms

ECC.6.3.15.9.2.1	The Fault Ride Through requirements for Type C and Type D Synchronous Power Generating Modules subject to faults and voltage disturbances on the Onshore Transmission System in excess of 140ms are defined in ECC.6.3.15.9.2.1(a) and the Fault Ride Through Requirements for Type C and Type D Power Park Modules and OTSDUW Plant and Apparatus subject to faults and voltage disturbances on the Onshore Transmission System greater than 140ms in duration are defined in ECC.6.3.15.9.2.1(b).

(a)	Requirements applicable to Synchronous Power Generating Modules subject to Supergrid Voltage dips on the Onshore Transmission System greater than 140ms in duration.

In addition to the requirements of ECC.6.3.15.1 – ECC.6.3.15.8 each Synchronous Power Generating Module shall:

(i)	remain transiently stable and connected to the System without tripping of any Synchronous Power Generating Module for balanced Supergrid Voltage dips and associated durations on the Onshore Transmission System (which could be at the Interface Point) anywhere on or above the heavy black line shown in Figure ECC.6.3.15.9(a) Appendix 4 and Figures EA.4.3.2(a), (b) and (c) provide an explanation and illustrations of Figure ECC.6.3.15.9(a); and,

Figure ECC.6.3.15.9(a)

(ii)	provide Active Power output at the Grid Entry Point, during Supergrid Voltage dips on the Onshore Transmission System as described in Figure ECC.6.3.15.9(a), at least in proportion to the retained balanced voltage at the Onshore Grid Entry Point (for Onshore Synchronous Power Generating Modules) or Interface Point (for Offshore Synchronous Power Generating Modules) (or the retained balanced voltage at the User System Entry Point if Embedded) and shall generate maximum reactive current (where the voltage at the Grid Entry Point is outside the limits specified in ECC.6.1.4) without exceeding the transient rating limits of the Synchronous Power Generating Module and,

(iii)	restore Active Power output following Supergrid Voltage dips on the Onshore Transmission System as described in Figure ECC.6.3.15.9(a), within 1 second of restoration of the voltage to 1.0pu of the nominal voltage at the:

Onshore Grid Entry Point for directly connected Onshore Synchronous Power Generating Modules or,

Interface Point for Offshore Synchronous Power Generating Modules

or,

User System Entry Point for Embedded Onshore Synchronous Power Generating Modules

or,

User System Entry Point for Embedded Medium Power Stations not subject to a Bilateral Agreement which comprise Synchronous Generating Units and with an Onshore User System Entry Point (irrespective of whether they are located Onshore or Offshore)

to at least 90% of the level available immediately before the occurrence of the dip. Once the Active Power output has been restored to the required level, Active Power oscillations shall be acceptable provided that:

-	the total Active Energy delivered during the period of the oscillations is at least that which would have been delivered if the Active Power was constant

-	the oscillations are adequately damped.

For the avoidance of doubt a balanced Onshore Transmission System Supergrid Voltage meets the requirements of ECC.6.1.5 (b) and ECC.6.1.6.

(iv) For up to 30 minutes following such a Supergrid Voltage dip on the Onshore Transmission System each Synchronous Power Generating Module is required to remain connected and stable provided System operating conditions have returned within those specified in ECC.6.1

(b)	Requirements applicable to Type C and Type D Power Park Modules and OTSDUW Plant and Apparatus (excluding OTSDUW DC Converters) subject to Supergrid Voltage dips on the Onshore Transmission System greater than 140ms in duration.

In addition to the requirements of ECC.6.3.15.5, ECC.6.3.15.6 and ECC.6.3.15.8 (as applicable) each OTSDUW Plant and Apparatus or each Power Park Module and / or any constituent Power Park Unit, shall:

(i)	remain transiently stable and connected to the System without tripping of any OTSDUW Plant and Apparatus, or Power Park Module and / or any constituent Power Park Unit, for balanced Supergrid Voltage dips and associated durations on the Onshore Transmission System (which could be at the Interface Point) anywhere on or above the heavy black line shown in Figure ECC.6.3.15.9(b).  Appendix 4 and Figures EA.4.3.4 (a), (b) and (c) provide an explanation and illustrations of Figure ECC.6.3.15.9(b) ; and,

Figure ECC.6.3.15.9(b)

(ii)	be required to satisfy the requirements of ECC.6.3.16. In the case of a Non-Synchronous Generating Unit or OTSDUW Plant and Apparatus or Power Park Module where there has been a reduction in the Intermittent Power Source or in the case of OTSDUW Active Power transfer capability in the time range in Figure ECC.6.3.15.9(b) an allowance shall be made for the fall in input power and the corresponding reduction of real and reactive current.

(iii)	restore Active Power output (or, in the case of OTSDUW, Active Power transfer capability), following Supergrid Voltage dips on the Onshore Transmission System as described in Figure ECC.6.3.15.9(b), within 1 second of restoration of the voltage to 0.9 pu of the nominal voltage at the:

Onshore Grid Entry Point for directly connected Onshore Power Park Modules or,

Interface Point for OTSDUW Plant and Apparatus and Offshore Power Park Modules or,

User System Entry Point for Embedded Onshore Power Park Modules or ,

User System Entry Point for Embedded Medium Power Stations which comprise Power Park Modules not subject to a Bilateral Agreement and with an Onshore User System Entry Point (irrespective of whether they are located Onshore or Offshore)

to at least 90% of the level available immediately before the occurrence of the dip except in the case of a Non-Synchronous Generating Unit, OTSDUW Plant and Apparatus or Power Park Module where there has been a reduction in the Intermittent Power Source in the time range in Figure ECC.6.3.15.9(b)  that restricts the Active Power output or, in the case of OTSDUW, Active Power transfer capability below this level. Once the Active Power output or, in the case of OTSDUW, Active Power transfer capability has been restored to the required level, Active Power oscillations shall be acceptable provided that:

-	the total Active Energy delivered during the period of the oscillations is at least that which would have been delivered if the Active Power was constant

-	the oscillations are adequately damped.

For the avoidance of doubt a balanced Onshore Transmission System Supergrid Voltage meets the requirements of ECC.6.1.5 (b) and ECC.6.1.6.

(iv) 	For up to 30 minutes following such a Supergrid Voltage dip on the Onshore Transmission System each Power Park Module and / or any constituent Power Park Unit and OTSDUW Plant and Apparatus is required to remain connected and stable provided System operating conditions have returned within those specified in ECC.6.1.

ECC.6.3.15.10	Other Fault Ride Through Requirements

(i)	In the case of a Power Park Module (excluding Non-Synchronous Electricity Storage Modules), the requirements in ECC.6.3.15.9 do not apply when the Power Park Module (excluding Non-Synchronous Electricity Storage Modules) is operating at less than 5% of its Rated MW or during very high primary energy source conditions when more than 50% of the Power Park Units in a Power Park Module have been shut down or disconnected under an emergency shutdown sequence to protect User’s Plant and Apparatus.

(ii)	In addition to meeting the conditions specified in ECC.6.1.5(b) and ECC.6.1.6, each Non-Synchronous Generating Unit, OTSDUW Plant and Apparatus or Power Park Module and any constituent Power Park Unit thereof will be required to withstand, without tripping, the negative phase sequence loading incurred by clearance of a close-up phase-to-phase fault, by System Back-Up Protection on the Onshore Transmission System operating at Supergrid Voltage.

- Generators in respect of Type B, Type C and Type D Power Park Modules and HVDC System Owners are required to confirm to The Company, their repeated ability to operate through balanced and unbalanced faults and System disturbances each time the voltage at the Grid Entry Point or User System Entry Point falls outside the limits specified in ECC.6.1.4.  Demonstration of this capability would be satisfied by EU Generators and HVDC System Owners supplying the protection settings of their plant, informing The Company of the maximum number of repeated operations that can be performed under such conditions and any limiting factors to repeated operation such as protection or thermal rating; and

- Notwithstanding the requirements of ECC.6.3.15(v), Power Generating Modules shall be capable of remaining connected during single phase or three phase auto-reclosures to the National Electricity Transmission System and operating without power reduction as long as the voltage and frequency remain within the limits defined in ECC.6.1.4 and ECC.6.1.2; and

- For the avoidance of doubt the requirements specified in ECC.6.3.15 do not apply to Power Generating Modules connected to either an unhealthy circuit and/or islanded from the Transmission System even for delayed auto reclosure times.

- To avoid unwanted island operation, Non-Synchronous Generating Units in Scotland (and those directly connected to a Scottish Offshore Transmission System),  Power Park Modules in Scotland (and those directly connected to a Scottish Offshore Transmission System), or OTSDUW Plant and Apparatus with an Interface Point in Scotland shall be tripped for the following conditions:

(1)	Frequency above 52Hz for more than 2 seconds

(2)	Frequency below 47Hz for more than 2 seconds

(3)	Voltage as measured at the Onshore Connection Point or Onshore User 	System Entry Point or Offshore Grid Entry Point or Interface Point in the 	case of OTSDUW Plant and Apparatus is below 80% for more than 2.5 	seconds

Voltage as measured at the Onshore Connection Point or Onshore User System Entry Point or Offshore Grid Entry Point or Interface Point in the case of OTSDUW Plant and Apparatus is above 120% (115% for 275kV) for more than 1 second. The times in sections (1) and (2) are maximum trip times.  Shorter times may be used to protect the Non-Synchronous Generating Units, or OTSDUW Plant and Apparatus.

ECC.6.3.15.11	HVDC System Robustness

ECC.6.3.15.11.1	The HVDC System shall be capable of finding stable operation points with a minimum change in Active Power flow and voltage level, during and after any planned or unplanned change in the HVDC System or AC System  to which it is connected. The Company  shall specify the changes in the System conditions for which the HVDC Systems shall remain in stable operation.

ECC.6.3.15.11.2	The HVDC System owner shall ensure that the tripping or disconnection of an HVDC Converter Station, as part of any multi-terminal or embedded HVDC System, does not result in transients at the Grid Entry Point or User System Entry Point beyond the limit specified by The Company in co-ordination with the Relevant Transmission Licensee.

ECC.6.3.15.11.3 	The HVDC System shall withstand transient faults on HVAC lines in the network adjacent or close to the HVDC System, and shall not cause any of the equipment in the HVDC System to disconnect from the network due to autoreclosure of lines in the System.

ECC.6.3.15.11.4	The HVDC System Owner shall provide information to The Company on the resilience of the HVDC System to AC System disturbances.

ECC.6.3.16		FAST FAULT CURRENT INJECTION

ECC.6.3.16.1	General Fast Fault Current injection, principles and concepts applicable to Type B, Type C and Type D Power Park Modules and HVDC Equipment

ECC.6.3.16.1.1	In addition to the requirements of ECC.6.1.4, ECC.6.3.2, ECC.6.3.8 and ECC.A.7, each Type B, Type C and Type D Power Park Module or each Power Park Unit within a Type B, Type C and Type D Power Park Module or HVDC Equipment shall be required to satisfy the following requirements unless operating in a Grid Forming Capability mode in which case the requirements of ECC.6.3.19 shall apply instead. For the purposes of this requirement, current and voltage are assumed to be positive phase sequence values.

ECC.6.3.16.1.2	For any balanced fault which results in the positive phase sequence voltage falling below the voltage levels specified in ECC.6.1.4 at the Grid Entry Point or User System Entry Point (if Embedded), each Type B, Type C and Type D Power Park Module or each Power Park Unit within a Type B, Type C and Type D Power Park Module or  HVDC Equipment shall, as a minimum (unless an alternative type registered solution has  otherwise been agreed with The Company),  be required to inject a reactive current above the heavy black line shown in Figure ECC.16.3.16(a)

Figure ECC.6.3.16(a)

ECC.6.3.16.1.3 Figure ECC.6.3.16(a) defines the reactive current (IR) to be supplied under a faulted condition which shall be dependent upon the pre-fault operating condition and the retained voltage at the Grid Entry Point or User System Entry Point voltage. For the avoidance of doubt, each Power Park Module (and any constituent element thereof) or HVDC Equipment, shall be required to inject a reactive current (IR) which shall be not less than its pre-fault reactive current and which shall as a minimum increase with the fall in the retained voltage each time the voltage at the Grid Entry Point or User System Entry Point (if Embedded) falls below 0.9pu whilst ensuring the overall rating of the Power Park Module (or constituent element thereof) or HVDC Equipment shall not be exceeded.

ECC.6.3.16.1.4	In addition to the requirements of ECC.6.3.16.1.2 and ECC.6.3.16.1.3, each Type B, Type C and Type D Power Park Module or each Power Park Unit within a Type B, Type C and Type D Power Park Module or HVDC Equipment shall be required to inject reactive current above the shaded area shown in Figure ECC.6.3.16(b) and Figure ECC.6.3.16(c) which illustrates how the reactive current shall be injected over time from fault inception in which the value of IR is determined from Figure ECC.6.3.16(a).  In figures ECC.6.3.16(b) and ECC.6.3.16(c) IR is the value of the reactive current (IR) less the prefault current.  In this context fault inception is taken to be when the voltage at the Grid Entry Point or User System Entry Point falls below 0.9pu.

Figure ECC.16.3.16(b)

Figure ECC.16.3.16(c)

ECC.6.3.16.1.5	The injected reactive current (IR)shall be above the shaded area shown in Figure ECC.6.3.16(b) and Figure ECC.6.3.16(c) with priority being given to reactive current injection with any residual capability being supplied as active current.  Under any faulted condition, where the voltage falls outside the limits specified in ECC.6.1.4, there would be no requirement for each Power Park Module or constituent Power Park Unit or HVDC Equipment to exceed its transient or steady state rating of 1.0pu as defined in ECC.6.3.16.1.7.

ECC.6.3.16.1.6	For any planned or switching events (as outlined in ECC.6.1.7 of the Grid Code) or unplanned events which results in temporary power frequency over voltages (TOV’s), each Type B, Type C and Type D Power Generating Module or each Power Park Unit within a Type B, Type C or Type D Power Park Module or HVDC Equipment will be required to satisfy the transient overvoltage limits specified in the Bilateral Agreement.

ECC.6.3.16.1.7	For the purposes of this requirement, the maximum rated current is taken to be the maximum current each Power Park Module (or the sum of the constituent Power Park Units which are connected to the System at the Grid Entry Point or User System Entry Point) or HVDC Converter is capable of supplying. In the case of a Power Park Module this would be the maximum rated current at the Grid Entry Point (or User System Entry Point if Embedded) when the Power Park Module is operating at rated Active Power and rated Reactive Power (as required under ECC.6.3.2) whilst operating over the nominal voltage range as required under ECC.6.1.4 at the Grid Entry Point (or User System Entry Point if Embedded).  In the case of a Power Park Unit forming part of a Type B, Type C and Type D Power Park Module, the maximum rated current expected would be the maximum current supplied from each constituent Power Park Unit when the Power Park Module is operating at rated Active Power and rated Reactive Power over the nominal voltage operating range as defined in ECC.6.1.4 less the contribution from the reactive compensation equipment.

For example, in the case of a 100MW Power Park Module (consisting of 50 x 2MW Power Park Units and +10MVAr reactive compensation equipment) the Rated Active Power at the Grid Entry Point (or User System Entry Point if Embedded) would be taken as 100MW and the rated Reactive Power at the Grid Entry Point or (User System Entry Point if  Embedded) would be taken as 32.8MVArs (ie Rated MW output operating at 0.95 Power Factor lead or 0.95 Power Factor lag as required under ECC.6.3.2.4). In this example, the maximum rating of each constituent Power Park Unit is obtained when the Power Park 	Module is operating at 100MW, and +32.8MVAr less 10MVAr equal to 22.8MVAr or – 32.8MVAr (less the reactive compensation equipment component of 10MVAr (ie -22.8MVAr) when operating within the normal voltage operating range as defined under ECC.6.1.4 (allowing for any reactive compensation equipment or losses in the Power Park Module array network).

For the avoidance of doubt, the total current of 1.0pu would be assumed to be on the MVA 	rating of the Power Park Module or HVDC Equipment (less losses). Under all normal and 	abnormal conditions, the steady state or transient rating of the Power Park Module (or 	any constituent element including the Power Park Units) or HVDC Equipment, 	would not be required to exceed the locus shown in Figure 16.3.16(d).

Figure ECC.16.3.16(d)

ECC.6.3.16.1.7	Each Type B, Type C and Type D Power Park Module or HVDC Equipment shall be designed to ensure a smooth transition between voltage control mode and fault ride through mode in order to prevent the risk of instability which could arise in the transition between the steady state voltage operating range as defined under ECC.6.1.4 and abnormal conditions where the retained voltage falls below 90% of nominal voltage.  Such a requirement is necessary to ensure adequate performance between the pre-fault operating condition of the Power Park Module or HVDC Equipment and its subsequent behaviour under faulted conditions.  EU Generators and HVDC System Owners are required to both advise and agree with The Company the control strategy employed to mitigate the risk of such instability.

ECC.6.3.16.1.8  	Each Type B, Type C and Type D Power Park Module or HVDC Equipment  shall be   designed to reduce the risk of transient over voltage levels arising following clearance of the  fault and in order to mitigate the risk of any form of instability which could result. EU Generators or HVDC System Owners shall be permitted to block or employ other means where the anticipated transient overvoltage would otherwise exceed the maximum permitted values specified in ECC.6.1.7.  Figure ECC.16.3.16(b) and Figure ECC.16.3.16(c) shows the impact of variations in fault clearance time.  For main protection operating times this would not exceed 140ms. The requirements for the maximum transient  overvoltage withstand capability and associated time duration, shall be agreed between the EU Code User and The Company as part of the Bilateral Agreement. Where the EU Code User is able to demonstrate to The Company that blocking or other control strategies are required  in order to prevent the risk of transient over voltage excursions as specified in ECC.6.3.16.1.5, EU Generators and HVDC System Owners are required to both advise and agree with The Company the control strategy, which must also include the approach taken to de-blocking

ECC.6.3.16.1.9         In addition to the requirements of ECC.6.3.15, Generators in respect of Type B, Type C and Type D Power Park Modules or each Power Park Unit within a Type B, Type C and Type D Power Park Module or DC Connected Power Park Modules and HVDC System Owners in respect of HVDC Systems are required to confirm to The Company, their repeated ability to supply Fast Fault Current to the System each time the voltage at the Grid Entry Point or User System Entry Point falls outside the limits specified in ECC.6.1.4.   EU Generators and HVDC Equipment Owners should inform The Company of the maximum number of repeated operations that can be performed under such conditions and any limiting factors to repeated operation such as protection or thermal rating.

ECC.6.3.16.1.10    To permit additional flexibility for example from Power Park Modules made up of full converter machines, DFIG machines, induction generators or HVDC Systems or Remote End HVDC Converters,  The Company will permit transient or marginal deviations below the shaded area shown in Figures ECC.16.3.16(b) or ECC.16.3.16(c) provided the injected reactive current supplied exceeds the area bound in Figure ECC.6.3.16(b) or ECC.6.3.16(c). Such agreement would be confirmed and agreed between The Company and Generator.

ECC.6.3.16.1.11      In the case of a Power Park Module or DC Connected Power Park Module, where it is not practical to demonstrate the compliance requirements of ECC.6.3.16.1.1 to ECC.6.3.16.1.6 at the Grid Entry Point or User System Entry Point, The Company will accept compliance of the above requirements at the Power Park Unit terminals.

ECC.6.3.16.1.12     For the avoidance of doubt, Generators in respect of Type C and Type D Power Park       Modules and OTSDUW Plant and Apparatus are also required to satisfy the requirements of ECC.6.3.15.9.2.1(b) which specifies the requirements for fault ride through for voltage dips in excess of 140ms.

ECC.6.3.16.1.13 In the case of an unbalanced fault, each Type B, Type C and Type D Power Park Module     or each Power Park Unit within a Type B, Type C and Type D Power Park Module or HVDC Equipment shall be required to inject reactive current (IR) which shall as a minimum increase with the fall in the retained unbalanced voltage up to its maximum reactive current without exceeding the transient rating of the Power Park Module (or constituent element thereof) or HVDC Equipment.

ECC.6.3.16.1.14	In the case of a unbalanced fault, the Generator or HVDC System Owner shall confirm to The Company their ability to prevent transient overvoltages arising on the remaining healthy phases and the control strategy employed.

ECC.6.3.17 	SUBSYNCHRONOUS TORSIONAL INTERACTION DAMPING CAPABILITY, POWER OSCILLATION DAMPING CAPABILITY AND CONTROL FACILITIES FOR HVDC SYSTEMS

ECC.6.3.17.1 	Subsynchronous Torsional Interaction Damping Capability

ECC.6.3.17.1.1	HVDC System Owners, or Generators in respect of OTSDUW DC Converters or Network Operators in the case of an Embedded HVDC Systems not subject to a Bilateral Agreement must ensure that any of their Onshore HVDC Systems or OTSDUW DC Converters will not cause a sub-synchronous resonance problem on the Total System. Each HVDC System or OTSDUW DC Converter is required to be provided with sub-synchronous resonance damping control facilities.  HVDC System Owners and EU Generators in respect of OTSDUW DC Converters should also be aware of the requirements in ECC.6.1.9 and ECC.6.1.10.

ECC.6.3.17.1.2	Where specified in the Bilateral Agreement, each  OTSDUW DC Converter is required to be provided with power oscillation damping or any other identified additional control facilities.

ECC.6.3.17.1.3	Each HVDC System shall be capable of contributing to the damping of power oscillations on the National Electricity Transmission System. The control system of the HVDC System shall not reduce the damping of power oscillations. The Company in coordination with the Relevant Transmission Licensee (as applicable) shall specify a frequency range of oscillations that the control scheme shall positively damp and the System conditions when this occurs, at least accounting for any dynamic stability assessment studies undertaken by the Relevant Transmission Licensee or The Company (as applicable) to identify the stability limits and potential stability problems on the National Electricity Transmission System. The selection of the control parameter settings shall be agreed between The Company in coordination with the Relevant Transmission Licensee  and the HVDC System Owner.

ECC.6.3.17.1.4	The Company shall specify the necessary extent of SSTI studies and provide input parameters, to the extent available, related to the equipment and relevant system conditions on the National Electricity Transmission System. The SSTI studies shall be provided by the HVDC System Owner. The studies shall identify the conditions, if any, where SSTI exists and propose any necessary mitigation procedure. The responsibility for undertaking the studies in accordance with these requirements lies with the Relevant Transmission Licensee in co-ordination with The Company. All parties shall be informed of the results of the studies.

ECC.6.3.17.1.5	All parties identified by The Company as relevant to each Grid Entry Point or User System Entry Point (if Embedded) , including the Relevant Transmission Licensee, shall contribute to the studies and shall provide all relevant data and models as reasonably required to meet the purposes of the studies. The Company  shall collect this data and, where applicable, pass it on to the party responsible for the studies in accordance with Retained EU Law (Article 10 of Commission Regulation (EU) 2016/1447). Specific information relating to the interface schedules, input/output requirements, timing and submission of any studies or data would be agreed between the User and The Company and specified (where applicable) in the Bilateral Agreement.

ECC.6.3.17.1.6	 The Company in coordination with the Relevant Transmission Licensee shall assess the result of the SSTI studies. If necessary for the assessment, The Company in coordination with the Relevant Transmission Licensee may request that the HVDC System Owner perform further SSTI studies in line with this same scope and extent.

ECC.6.3.17.1.7	The Company in coordination with the Relevant Transmission Licensee may review or replicate the study. The HVDC System Owner shall provide The Company with all relevant data and models that allow such studies to be performed. Submission of this data to Relevant Transmission Licensee’s shall be in accordance with the requirements of Retained EU Law (Article 10 of Commission Regulation (EU) 2016/1447).

ECC.6.3.17.1.8	Any necessary mitigating actions identified by the studies carried out in accordance with paragraphs ECC.6.3.17.1.4 or ECC.6.3.17.1.6, and reviewed by The Company in coordination with the  Relevant Transmission Licensees, shall be undertaken by the HVDC System Owner as part of the connection of the new HVDC Converter Station.

ECC.6.3.17.1.9	As part of the studies and data flow in respect of ECC.6.3.17.1 – ECC.6.3.17.8 the following data exchange would take place with the time scales being pursuant to the terms of the Bilateral Agreement.

Information supplied by The Company and Relevant Transmission Licensees

Studies provided by the User

User review

The Company review

Changes to studies and agreed updates between The Company, the Relevant Transmission Licensee and User

Final review

ECC.6.3.17.2	Interaction between HVDC Systems or other User’s Plant and Apparatus

ECC.6.3.17.2.1	Notwithstanding the requirements of ECC6.1.9 and ECC.6.1.10, when several HVDC Converter Stations or other User’s Plant and Apparatus are within close electrical proximity, The Company may specify that a study is required, and the scope and extent of that study, to demonstrate that no adverse interaction will occur. If adverse interaction is identified, the studies shall identify possible mitigating actions to be implemented to ensure compliance with the requirements of ECC.6.1.9

ECC.6.3.17.2.2	The studies shall be carried out by the connecting HVDC System Owner with the participation of all other User’s identified by The Company in coordination with Relevant Transmission Licensees as relevant to each Connection Point.

ECC.6.3.17.2.3	All User’s identified by The Company as relevant to  the connection , and where applicable Relevant Transmission Licensee’s, shall contribute to the studies and shall provide all relevant data and models as reasonably required to meet the purposes of the studies.  The Company shall collect this input and, where applicable, pass it on to the party responsible for the studies in accordance with Retained EU Law (Article 10 of Commission Regulation (EU) 2016/1447). Specific information relating to the interface schedules, input/output requirements, timing and submission of any studies or data would be agreed between the User and The Company and specified (where applicable) in the Bilateral Agreement.

ECC.6.3.17.2.4	The Company in coordination with Relevant Transmission Licensees shall assess the result of the studies based on their scope and extent as specified in accordance with ECC.6.3.17.2.1. If necessary for the assessment, The Company in coordination with the Relevant Transmission Licensee may request the HVDC System Owner to perform further studies in line with the scope and extent specified in accordance with ECC.6.3.17.2.1.

ECC.6.3.17.2.5	The Company in coordination with the Relevant Transmission Licensee may review or replicate some or all of the studies. The HVDC System Owner shall provide The Company  all relevant data and models that allow such studies to be performed.

ECC.6.3.17.2.6	The EU Code User and The Company, in coordination with the Relevant Transmission Licensee, shall agree any mitigating actions identified by the studies carried out following the site specific requirements and works, including any transmission reinforcement works and / or User works required to ensure that all sub-synchronous oscillations are sufficiently damped.

ECC.6.1.17.3	Fast Recovery from DC faults

ECC.6.1.17.3.1	HVDC Systems, including DC overhead lines, shall be capable of fast recovery from transient faults within the HVDC System. Details of this capability shall be subject to the Bilateral Agreement and the protection requirements specified in ECC.6.2.2 .

ECC.6.1.17.4	Maximum loss of Active Power

ECC.6.1.14.4.1	An HVDC System shall be configured in such a way that its loss of Active Power injection in the GB Synchronous Area shall be in accordance with the requirements of the SQSS.

ECC.6.3.18	SYSTEM TO GENERATOR OPERATIONAL INTERTRIPPING SCHEMES

ECC.6.3.18.1	The Company may require that a System to Generator Operational Intertripping Scheme be installed as part of a condition of the connection of the EU Generator.  Scheme specific details shall be included in the relevant Bilateral Agreement and shall, include the following information:

(1)	the relevant category(ies) of the scheme (referred to as Category 1 Intertripping Scheme, Category 2 Intertripping Scheme, Category 3 Intertripping Scheme and Category 4 Intertripping Scheme);

(2)	the  Power Generating Module to be either permanently armed or that can be instructed to be armed in accordance with BC2.8;

(3)	the time within which the Power Generating Module circuit breaker(s) are to be automatically tripped;

(4)	the location to which the trip signal will be provided by The Company. Such location will be provided by The Company prior to the commissioning of the Power Generating Module.

Where applicable, the Bilateral Agreement shall include the conditions on the National Electricity Transmission System during which The Company may instruct the System to Generator Operational Intertripping Scheme to be armed and the conditions that would initiate a trip signal.

ECC.6.3.18.2 	The time within which the Power Generating Module(s) circuit breaker(s) need to be automatically tripped is determined by the specific conditions local to the EU Generator. This ‘time to trip’ (defined as the time from provision of the trip signal by The Company to the specified location, to circuit breaker main contact opening) can typically range from 100ms to 10sec. A longer time to trip may allow the initiation of an automatic reduction in the Power Generating Module(s) output prior to the automatic tripping of the Power Generating Module(s) circuit breaker. Where applicable The Company may provide separate trip signals to allow for either a longer or shorter ‘time to trip’ to be initiated.

ECC.6.3.19	GRID FORMING CAPABILITY

ECC.6.3.19.1	In order for the National Electricity Transmission System to satisfy the stability requirements defined in the National Electricity Transmission System Security and Quality of Supply Standards, it is an essential requirement that an appropriate volume of Grid Forming Plant is available and capable of providing a Grid Forming Capability.

ECC.6.3.19.2	Grid Forming Capability is not a mandatory requirement but one which will be delivered through market arrangements, the details of which shall be published on The Company’s Website.  Grid Forming Capability can be implemented by any technology including Electronic Power Converters with a GBGF- I ability, rotating Synchronous Generating Units or a combination of the two.

ECC.6.3.19.3	As noted in ECC.6.3.19.2, Grid Forming Capability is not a mandatory requirement, however where a User (be they a GB Code User or EU Code User) or Non-CUSC Party wishes to offer a Grid Forming Capability, then they will be required to ensure their Grid Forming Plant meets the following requirements.

- The Grid Forming Plant must fully comply with the applicable requirements of the Grid Code including but not limited to the Planning Code (PC), Connection Conditions (CC’s) or European Connection Conditions (ECC’s) (as applicable), Compliance Processes (CP’s) or European Compliance Processes (ECP’s) (as applicable), Operating Codes (OC’s), Balancing Codes (BC’s) and Data Registration Code (DRC).

- Each GBGF-I shall comprise an Internal Voltage Source and reactance.  For the avoidance of doubt, the reactance between the Internal Voltage Source and Grid Entry Point or User System Entry Point (if Embedded) within the Grid Forming Plant can only be made by a combination of several physical discrete reactances. This could include the reactance of the Synchronous Generating Unit or Power Park Unit or HVDC System or Electricity Storage Unit or Dynamic Reactive Compensation Equipment and the electrical Plant and Apparatus connecting the Synchronous Generating Unit or Power Park Unit or HVDC System or Electricity Storage Unit (such as a transformer) to the Grid Entry Point or User System Entry Point (if Embedded).

- In addition to meeting the requirements of CC.6.3.15 or ECC.6.3.15, each Grid Forming Plant is required to remain in synchronism with the Total System and maintain a Load Angle whose value can vary between 0 and 90 degrees (π/2 radians).

- When subject to a fault or disturbance, or System Frequency change, each Grid Forming Plant shall be capable of supplying Active ROCOF Response Power, Active Phase Jump Power, Active Damping Power, Active Control Based Power, Control Based Reactive Power, Voltage Jump Reactive Power and GBGF Fast Fault Current Injection.

- Each GBGF-I shall be capable of:-

- Providing a symmetrical ability for importing and exporting Active ROCOF Response Power, Active Phase Jump Power, Active Damping Power and Active Control Based Power under both rising and falling System Frequency conditions. Such requirements will apply over the full System Frequency range as detailed in CC.6.1.2 and CC.6.1.3 or ECC.6.1.2 (as applicable).  In satisfying these requirements, User’s and Non-CUSC Parties should be aware of (but not limited to) the exclusions in CC.6.3.3, CC.6.3.7 and BC3.7.2.1 (as applicable for GB Code User’s) or ECC.6.1.2, ECC.6.3.3, ECC.6.3.7 and BC3.7.2.1(b)(i) (as applicable for EU Code User’s and Non-CUSC Parties) during System Frequencies between 47Hz – 52Hz, excluding CC.6.1.3 or ECC.6.1,2.1,2 for a Grid Forming Plant with time limited output ratings. For the avoidance of doubt, an asymmetrical response is permissible as agreed with The Company when required to protect User’s and Non-CUSC Parties Plant and Apparatus or asymmetry in energy availability.

- Operating as a voltage source behind a real reactance.

- being designed so as not to cause any undue interactions which could cause damage to the Total System or other User’s Plant and Apparatus.

- include an Active Control Based Power part of the control system that can respond to changes in the Grid Forming Plant or external signals from the Total System available at the Grid Entry Point or User System Entry Point but with a bandwidth below 5 Hz to avoid AC System resonance problems.

- meeting the requirements of ECC.6.3.13 irrespective of being owned or operated by a GB Code User, EU Code User or Non-CUSC Party.

- GBGF-I with an importing capability mode of operation such as DC Converters, HVDC Systems and Electricity Storage Modules are required to have a predefined frequency response operating characteristic over the full import and export range which is contained within the envelope defined by the red and blue lines shown in Figure ECC.6.3.19.3.  This characteristic shall be submitted to The Company.  For the avoidance of doubt, Grid Forming Plants which are only capable of exporting Active Power to the Total System are only required to operate over the exporting power region

.

Figure ECC.6.3.19.3

- Each User or Non-CUSC Party shall design their GBGF-I system with an equivalent Damping Factor of between 0.2 and 5.0. It is down to the User or Non-CUSC Party to determine the Damping Factor, whose value shall be agreed with The Company.  It is typical for the Damping Factor to be less than 1.0, though this will be dependent upon the parameters of the Grid Forming Plant and the equivalent System impedance at the Grid Entry Point or User System Entry Point.

The output of the Grid Forming Plant shall be designed such that following a disturbance on the System, the Active Power output and Reactive Power output shall be adequately damped.  The damping shall be judged to be adequate if the corresponding Active Power response to a disturbance decays with a response that is in line with the response of second order system that has the same equivalent Damping Factor.

- Each GBGF-I shall be designed so as not to interact and affect the operation, performance, safety or capability of other User’s Plant and Apparatus connected to the Total System. To achieve this requirement, each User and Non-CUSC Party shall be required to submit the data required in PC.A.5.8

ECC.6.3.19.4	In addition to the requirements of ECC.6.3.19.1 – ECC.6.3.19.3 each Grid Forming Plant shall also be capable of: -

- satisfying the requirements of ECC.6.3.19.5.

- operating at a minimum short circuit level of zero MVA at the Grid Entry Point or User 	System Entry Point.

- providing any additional quality of supply requirements, including but not limited to reductions in the permitted frequency of  Temporary Power System  Over-voltage events (TOV’s) and System Frequency bandwidth limitations, as agreed with The Company. Such requirements will be pursuant to the terms of the Bilateral Agreement.  For the avoidance of doubt, this requirement is in addition the minimum quality of supply requirements detailed in CC.6.1.5, CC.6.1.6 and CC.6.1.7 (as applicable) or ECC.6.1.5, ECC.6.1.6 and ECC.6.1.7 (as applicable),

ECC.6.3.19.5	GBGF Fast Fault Current Injection

ECC.6.3.19.5.1	For any balanced fault which results in the positive phase sequence voltage falling below the voltage levels specified in CC.6.1.4 or ECC.6.1.4 (as applicable) at the Grid Entry Point or User System Entry Point (if Embedded), a Grid Forming Plant shall, as a minimum be required to inject a reactive current of at least their Peak Current Rating when the voltage at the Grid Entry Point or User System Entry Point drops to zero. For intermediate retained voltages at the Grid Entry Point or User System Entry Point, the injected reactive current shall be on or above a line drawn from the bottom left hand corner of the normal voltage control operating zone (shown in the rectangular green shaded area of Figure ECC.6.3.19.5(a)) and the specified Peak Current Rating at a voltage of zero at the Grid Entry Point or User System Entry Point as shown in Figure ECC.16.3.19.5(a). Typical examples of limit lines are shown in Figure ECC.16.3.19.5(a) for a Peak Current Rating of 1.0pu where the injected reactive current must be on or above the black line and a Peak Current Rating of 1.5pu where injected reactive current must be on or above the red line.

Figure ECC.6.3.19.5(a)

ECC.6.3.19.5.2 Figure ECC.6.3.19.5(a) defines the reactive current to be supplied under a faulted condition which shall be dependent upon the pre-fault operating condition and the retained voltage at the Grid Entry Point or User System Entry Point voltage. For the avoidance of doubt, each Grid Forming Plant (and any constituent element thereof), shall be required to inject a reactive current which shall be not less than its pre-fault reactive current and which shall as a minimum, increase each time the voltage at the Grid Entry Point or User System Entry Point (if Embedded) falls below 0.9pu whilst ensuring the overall rating of the Grid Forming Plant (or constituent element thereof) shall not be exceeded.

ECC.6.3.19.5.3	In addition to the requirements of ECC.6.3.19.5.1 and ECC.6.3.19.5.2, each Grid Forming Plant shall be required to inject reactive current above the shaded area shown in Figure ECC.6.3.19.5(b) when the retained voltage at the Grid Entry Point or User System Entry Point falls to 0pu. Where the retained voltage at the Grid Entry Point or User System Entry Point is below 0.9pu but above 0pu (for example when significant active current is drawn by loads and/or resistive components arising from both local and remote faults or disturbances from other Plant and Apparatus connected to the Total System) the injected reactive current component shall be in accordance with Figure ECC.6.3.19.5(a).

Figure ECC.6.3.19.5(b)

ECC.6.3.19.5.4	The injected current shall be above the shaded area shown in Figure ECC.6.3.19.5(b) for the duration of the fault clearance time which for faults on the Transmission System cleared in Main Protection operating times shall be up to 140ms.  Under any faulted condition, where the voltage falls outside the limits specified in CC.6.1.4 or ECC.6.1.4 (as applicable), there will be no requirement for each Grid Forming Plant or constituent part to exceed its transient or steady state rating as defined in Table PC.A.5.8.2.

ECC.6.3.19.5.5	For any planned or switching events (as outlined in CC.6.1.7 or ECC.6.1.7 of the Grid Code) or unplanned events which results in Temporary Power System Over Voltages (TOV’s), each Grid Forming Plant will be required to satisfy the transient overvoltage limits specified in the Bilateral Agreement.

ECC.6.3.19.5.6	For the purposes of this requirement, the maximum rated current will be the Peak Current Rating declared by the Grid Forming Plant Owner in accordance with Table PC.A.5.8.2.

ECC.6.3.19.5.7	Each Grid Forming Plant shall be designed to ensure a smooth transition between voltage control mode and Fault Ride Through mode in order to prevent the risk of instability which could arise in the transition between the steady state voltage operating range as defined under CC.6.1.4 or ECC.6.1.4 (as applicable) and abnormal conditions where the retained voltage falls below 90% of nominal voltage.  Such a requirement is necessary to ensure adequate performance between the pre-fault operating condition of the Grid Forming Plant and its subsequent behaviour under faulted conditions.  Grid Forming Plant Owners are required to both advise and agree with The Company the control strategy employed to mitigate the risk of such instability.

ECC.6.3.19.5.8.  	Each Grid Forming Plant shall be designed to reduce the risk of transient over voltage levels arising following clearance of the fault and in order to mitigate the risk of any form of instability which could result. The requirements for the maximum transient overvoltage withstand capability and associated time duration, shall be agreed between the User or Non-CUSC Party and The Company as part of the Bilateral Agreement.

ECC.6.3.19.5.9  	In addition to the requirements of CC.6.3.15 or ECC.6.3.15, each Grid Forming Plant Owner is required to confirm to The Company, their repeated ability to supply GBGF Fast Fault Current Injection to the System each time the voltage at the Grid Entry Point or User System Entry Point falls outside the limits specified in CC.6.1.4 or ECC.6.1.4 (as applicable). Grid Forming Plant Owners should inform The Company of the maximum number of repeated operations that can be performed under such conditions and any limiting factors to repeated operation such as protection or thermal rating.

ECC.6.3.19.5.10 In the case of a Power Park Module or DC Connected Power Park Module, where it is not practical to demonstrate the compliance requirements of ECC.6.3.19.5.1 to ECC.6.3.19.5.5 at the Grid Entry Point or User System Entry Point, The Company will accept compliance of the above requirements at the Power Park Unit terminals.

ECC.6.3.19.5.11 	In the case of an unbalanced fault, each Grid Forming Plant, shall be required to inject current which shall as a minimum increase with the fall in the unbalanced voltage without exceeding the transient Peak Current Rating of the Grid Forming Plant (or constituent element thereof).

ECC.6.3.19.5.12	In the case of an unbalanced fault, the User or Non-CUSC Party shall confirm to The Company their ability to prevent transient overvoltages arising on the remaining healthy phases and the control strategy employed.

ECC.6.4	General Network Operator And Non-Embedded Customer Requirements

ECC.6.4.1	This part of the Grid Code describes the technical and design criteria and performance requirements for Network Operators and Non-Embedded Customers.

Neutral Earthing

ECC.6.4.2	At nominal System voltages of 132kV and above the higher voltage windings of three phase transformers and transformer banks connected to the National Electricity Transmission System must be star connected with the star point suitable for connection to earth.  The earthing and lower voltage winding arrangement shall be such as to ensure that the Earth Fault Factor requirement of paragraph ECC.6.2.1.1 (b) will be met on the National Electricity Transmission System at nominal System voltages of 132kV and above.

Frequency Sensitive Relays

ECC.6.4.3	As explained under OC6, each Network Operator and Non Embedded Customer, will make arrangements that will facilitate automatic low Frequency Disconnection of Demand (based on Annual ACS Conditions). ECC.A.5.5. of Appendix E5 includes specifications of the local percentage Demand that shall be disconnected at specific frequencies.  The manner in which Demand subject to low Frequency disconnection will be split into discrete MW blocks is specified in OC6.6.  Technical requirements relating to Low Frequency Relays are also listed in Appendix E5.

Operational Metering

ECC.6.4.4	Where The Company can reasonably demonstrate that an Embedded Medium Power Station or Embedded HVDC System has a significant effect on the National Electricity Transmission System, it may require the Network Operator within whose System the Embedded Medium Power Station or Embedded HVDC System is situated to ensure that the operational metering equipment described in ECC.6.5.6 is installed such that The Company can receive the data referred to in ECC.6.5.6.  In the case of an Embedded Medium Power Station subject to, or proposed to be subject to a Bilateral Agreement, The Company shall notify such Network Operator of the details of such installation in writing within 3 months of being notified of the application to connect under CUSC and in the case of an Embedded Medium Power Station not subject to, or not proposed to be subject to a Bilateral Agreement in writing as a Site Specific Requirement in accordance with the timescales in CUSC 6.5.5.  In either case the Network Operator shall ensure that the data referred to in ECC.6.5.6 is provided to The Company.

ECC.6.4.5	Reactive Power Requirements at each EU Grid Supply Point

ECC.6.4.5.1	At each EU Grid Supply Point, Non-Embedded Customers and Network Operators who are EU Code Users shall ensure their Systems are capable of steady state operation within the Reactive Power limits as specified in ECC.6.4.5.1(a) and ECC.6.4.5.1(b).  Where The Company requires a Reactive Power range which is broader than the limits defined in ECC.6.4.5.1(a) and ECC.6.4.5.1(b), this will be agreed as a reasonable requirement through joint assessment between the relevant EU Code User and The Company and justified in accordance with the requirements of ECC.6.4.5.1(c), (d), (e) and (f).  For Non-Embedded Customers who are EU Code Users, the Reactive Power range at each EU Grid Supply Point, under both importing and exporting conditions, shall not exceed 48% of the larger of the Maximum Import Capability or Maximum Export Capability   (0.9 Power Factor import or export of Active Power), except in situations where either technical or financial system benefits are demonstrated for Non-Embedded Customers and accepted by The Company in coordination with the Relevant Transmission Licensee.

- For Network Operators who are EU Code Users at each EU Grid Supply Point, the Reactive Power range shall not exceed:

- 48 percent (i.e. 0.9 Power Factor) of the larger of the Maximum Import Capability or Maximum Export Capability during Reactive Power import (consumption); and

- 48 percent (i.e. 0.9 Power Factor) of the larger of the Maximum Import Capability or Maximum Export Capability during Reactive Power export (production);

Except in situations where either technical or financial system benefits are proved by The Company in coordination with the Relevant Transmission Licensee and the relevant Network Operator through joint analysis.

- The Company in co-ordination with the Relevant Transmission Licensee shall agree with the Network Operator on the scope of the analysis, which shall determine the optimal solution for Reactive Power exchange between their Systems at each EU Grid Supply Point, taking adequately into consideration the specific System characteristics, variable structure of power exchange, bidirectional flows and the Reactive Power capabilities of the Network Operator’s System.  Any proposed solutions shall take the above issues into account and shall be agreed as a reasonable requirement through joint assessment between the relevant Network Operator or Non-Embedded Customer and The Company in coordination with the Relevant Transmission Licensee.  In the event of a shared site between a GB Code User and EU Code User, the requirements would generally be allocated to each User on the basis of their Demand in the case of a Network Operator who is a GB Code User and applied on the basis of the Maximum Import Capability or Maximum Export Capability as specified in ECC.6.4.5.1 in the case of a Network Operator who is an EU Code User.

- The Company in coordination with the Relevant Transmission Licensee may specify the Reactive Power capability range at the EU Grid Supply Point in another form other than Power Factor.

- Notwithstanding the ability of Network Operators or Non Embedded Customers to apply for a derogation from ECC.6.4.5.1 (e), where an EU Grid Supply Point is shared between a Power Generating Module and a Non-Embedded Customers System, the Reactive Power range would be apportioned to each EU Code User at their Connection Point.

ECC.6.4.5.2		Where agreed with the Network Operator who is an EU Code User and justified though appropriate System studies, The Company may reasonably require the Network Operator not to export Reactive Power at the EU Grid Supply Point (at nominal voltage) at an Active Power flow of less than 25 % of the Maximum Import Capability. Where applicable, the Authority may require The Company in coordination with the Relevant Transmission Licensee to justify its request through a joint analysis with the relevant Network Operator and demonstrate that any such requirement is reasonable. If this requirement is not justified based on the joint analysis, The Company in coordination with the Relevant Transmission Licensee and the Network Operator shall agree on necessary requirements according to the outcomes of a joint analysis.

ECC.6.4.5.3		Notwithstanding the requirements of ECC.6.4.5.1(b) and subject to agreement between The Company and the relevant Network Operator there may be a requirement to actively control the exchange of Reactive Power at the EU Grid Supply Point for the benefit of the Total System. The Company and the relevant Network Operator shall agree on a method to carry out this control, to ensure the justified level of security of supply for both parties. Any such solution including joint study work and timelines would be agreed between The Company and the relevant Network Operator as reasonable, efficient and proportionate.

ECC.6.4.5.4		In accordance with ECC.6.4.5.3, the relevant Network Operator may require The Company to consider its Network Operator’s System for Reactive Power management.  Any such requirement would need to be agreed between The Company and the relevant Network Operator and justified by The Company.

ECC.6.4.6	System Restoration

ECC.6.4.6.1	Distribution Restoration Zone Plans are dependent upon Restoration Contractors who, have an Anchor Restoration Contract which requires the capability to Start-Up from Shutdown within 8 hours and to energise a part of a Network Operator’s System (and in some cases could extend to energisation of parts of the Transmission System) upon instruction from a relevant Network Operator, without an external electrical power supply.  Distribution Restoration Zone Plans may also be dependent upon Top Up Restoration Contractors. Network Operators shall be responsible for instructing Restoration Contractors in accordance with a Distribution Restoration Zone Plan once The Company has issued an instruction to the Network Operator to activate a Distribution Restoration Zone as provided for in OC9.4.7.8.1.

ECC.6.4.6.2.	Where a need for a Distribution Restoration Zone is agreed in accordance with OC9, the following requirements shall apply:-

- Where there is a requirement for two adjacent Distribution Restoration Zones to be  Synchronised as part of the wider System Restoration process and as catered for in the relevant Distribution Restoration Zone Plans, appropriate Synchronising facilities shall exist or shall be installed by the Network Operator or Relevant Transmission Licensee as set out in OC9.4.7.6.3(d).  Such Synchronising facilities shall be identified as part of the development of the Restoration Plan as set out in OC9.4.7.6.1.  Where a Distribution Restoration Zone extends to Transmission Plant and Apparatus as provided for in OC9.4.7.8.15, the responsibility for the provision of these facilities on Transmission equipment is the responsibility of the Relevant Transmission Licensee.

- The Company and the Network Operator and Relevant Transmission Licensee (where necessary) shall agree the monitoring and operational metering which shall be installed in the Network Operator’s System, including but not limited to, operational metering signals, status indications and the topology of the Network Operator’s System falling within the scope of the Local Joint Restoration Plan or Distribution Restoration Zone Plan, and the output and status of Restoration Contractor’s Plant and Apparatus.  Where appropriate, some of this information may be supplied as outputs from the Distribution Restoration Zone Control System within the Distribution Restoration Zone where one is installed.  This data shall be provided to The Company and Relevant Transmission Licensee (where necessary) through appropriate data links as agreed between The Company and the Network Operator.

(c) Network Operators shall have secure, robust and power resilient communications systems between their Control Centres and the point at which Restoration Contractor’s Plant and Apparatus is connected to the Network Operator’s System as provided for in ECC.7.10 and ECC.7.11.

ECC.6.5	Communications Plant

ECC.6.5.1	In order to ensure control of the National Electricity Transmission System, telecommunications between Users and The Company must (including in respect of any OTSDUW Plant and Apparatus at the OTSUA Transfer Time), if required by The Company, be established in accordance with the requirements set down below.

ECC.6.5.2	Control Telephony and System Telephony

ECC.6.5.2.1	Control Telephony provides secure point to point telephony for routine Control Calls, priority Control Calls and emergency Control Calls.

ECC.6.5.2.2	System Telephony uses an appropriate public communications network to provide telephony for Control Calls, inclusive of emergency Control Calls.  For the avoidance of doubt, System Telephony could include but shall not be limited to: an analogue or digital telephone line; a mobile telephone or an internet-based voice communication system, all of which would be connected to an appropriate public communications network.

ECC.6.5.2.3	Calls made and received over Control Telephony and System Telephony may be recorded and subsequently replayed for commercial and operational reasons.

ECC.6.5.3	Not Used

ECC.6.5.4	Obligations in respect of Control Telephony and System Telephony

ECC.6.5.4.1	Where The Company requires Control Telephony, Users are required to use the Control Telephony to communicate with The Company and / or the Transmission Licensees’ in respect of all Connection Points with the National Electricity Transmission System, all Embedded Large Power Stations, Embedded HVDC Systems and Network Operator’s Control Centres as appropriate. The Company shall provide Control Telephony interface equipment at the User’s Control Point or the Network Operators Control Centre as appropriate. Where the EU Code User’s or Network Operators Control Centre telephony equipment is not capable of providing the required facilities or is otherwise incompatible with the Transmission Control Telephony, The Company shall provide a Control Telephony handset(s). Details of and relating to the Control Telephony requirements are contained in the Bilateral Agreement with EU Code User’s.

ECC.6.5.4.2	Where in The Company’s sole opinion the installation of Control Telephony is not practicable at a User’s Control Point(s), The Company shall specify in the Bilateral Agreement whether System Telephony is required.  Where System Telephony is required by The Company, the User shall ensure that System Telephony is installed.

ECC.6.5.4.3	Where System Telephony is installed, EU Code Users are required to use the System Telephony for communication with The Company and the relevant Transmission Licensees’ Control Engineers in respect of those Control Point(s) for which it has been installed. Details of and relating to the System Telephony required are contained in the Bilateral Agreement.

ECC.6.5.4.4	Where Control Telephony or System Telephony is installed, routine testing of such facilities may be required by The Company (not normally more than once in any calendar month).  The User and The Company shall use reasonable endeavours to agree a test programme and where The Company requests the assistance of the User in performing the agreed test programme the User shall provide such assistance. The Company requires the EU Code User to test the backup power supplies feeding its Control Telephony facilities at least once every 5 years.

ECC.6.5.4.5	Control Telephony and System Telephony shall only be used for the purposes of operational voice communication between The Company and the relevant User.

ECC.6.5.4.6	Control Telephony contains emergency calling functionality to be used for operational communication only under normal and emergency conditions.  Functionality enables The Company and Users to utilise a priority call in the event of an emergency.  The Company and EU Code Users shall only use such priority call functionality for urgent operational communications.

ECC.6.5.5	Technical Requirements for Control Telephony and System Telephony

ECC.6.5.5.1	Detailed information on the technical interfaces and support requirements for Control Telephony is provided in the Control Telephony Electrical Standard identified in the Annex to the General Conditions.  Where additional information, or information in relation to Control Telephony applicable in Scotland, is requested by Users, this will be provided, where possible, by The Company.

ECC.6.5.5.2	System Telephony shall consist of a dedicated telephone connected to an appropriate public communications network that shall be configured by the relevant User.  The Company shall provide a dedicated free phone number (UK only), for the purposes of receiving incoming calls to The Company, which Users shall utilise for System Telephony.  System Telephony shall only be utilised by The Company’s Control Engineer and the User’s Responsible Engineer/Operator for the purposes of operational communications.

ECC.6.5.6	Operational Metering

ECC.6.5.6.1     	It is an essential requirement for The Company and Network Operators to have visibility of the real time output and status of indications of User’s Plant and Apparatus so they can control the operation of the System.

ECC.6.5.6.2	Type B, Type C and Type D  Power Park Modules,  HVDC Equipment, Network Operators and Non Embedded Customers are required to be capable of exchanging operational metering data with The Company and Relevant Transmission Licensees (as applicable) with time stamping.  Time stamping would generally be to a sampling rate of 1 second or better unless otherwise specified by The Company in the Bilateral Agreement.

ECC.6.5.6.3	The Company in coordination with the Relevant Transmission Licensee shall specify in the Bilateral Agreement the operational metering signals to be provided by the EU Generator, HVDC System Owner, Network Operator or Non-Embedded Customer.  In the case of Network Operators and Non-Embedded Customers, detailed specifications relating to the operational metering standards at EU Grid Supply Points and the data required are published as Electrical Standards in the Annex to the General Conditions.

ECC.6.5.6.4	(a) The Company or The Relevant Transmission Licensee, as applicable,  shall provide system control and data acquisition (SCADA) outstation interface equipment.  Each  EU Code User shall provide such voltage, current, Frequency, Active Power and Reactive Power measurement outputs and plant status indications and alarms to the  Transmission SCADA outstation interface equipment as required by The Company in accordance with the terms of the Bilateral Agreement. In the case of OTSDUW, the User shall provide such SCADA outstation interface equipment and voltage, current, Frequency, Active Power and Reactive Power measurement outputs and plant status indications and alarms to the SCADA outstation interface equipment as required by The Company in accordance with the terms of the Bilateral Agreement.

(b)	For the avoidance of doubt, for Active Power and Reactive Power measurements, circuit breaker and disconnector status indications from:

(i)	CCGT Modules from Type B, Type C and Type D Power Generating Modules, the outputs and status indications must each be provided to The Company on an individual CCGT Unit basis.  In addition, where identified in the Bilateral Agreement, Active Power and Reactive Power measurements from Unit Transformers and/or Station Transformers must be provided.

(ii)	For Type B, Type C and Type D Power Park Modules the outputs and status indications must each be provided to The Company on an individual Power Park Module basis. In addition, where identified in the Bilateral Agreement, Active Power and Reactive Power measurements from station transformers must be provided.

(iii)	In respect of OTSDUW Plant and Apparatus, the outputs and status indications must be provided to The Company for each piece of electrical equipment. In addition, where identified in the Bilateral Agreement, Active Power and Reactive Power measurements at the Interface Point must be provided.

(c)	For the avoidance of doubt, the requirements of ECC.6.5.6.4(a) in the case of a Cascade Hydro Scheme will be provided for each Generating Unit forming part of that Cascade Hydro Scheme.  In the case of Embedded Generating Units forming part of a Cascade Hydro Scheme the data may be provided by means other than the  SCADA outstation located at the Power Station, such as, with the agreement of the Network Operator in whose system such Embedded Generating Unit is located, from the Network Operator’s SCADA system to The Company.  Details of such arrangements will be contained in the relevant Bilateral Agreements between The Company and the Generator and the Network Operator.

(d)	In the case of a Power Park Module, additional energy input signals (e.g. wind speed, and wind direction) may be specified in the Bilateral Agreement. A Power Available signal will also be specified in the Bilateral Agreement. The signals would be used to establish the potential level of energy input from the Intermittent Power Source for monitoring pursuant to ECC.6.6.1 and Ancillary Services and will, in the case of a wind farm, be used to provide The Company with advanced warning of excess wind speed shutdown and to determine the level of Headroom available from Power Park Modules for the purposes of calculating response and reserve.  For the avoidance of doubt, the Power Available signal would be automatically provided to The Company and represent the sum of the potential output of all available and operational Power Park Units within the Power Park Module. The refresh rate of the Power Available signal shall be specified in the Bilateral Agreement. In the case of an Electricity Storage Module, the requirement to provide a Power Available Signal when the Plant is in both an importing and exporting mode of operation would be specified in the Bilateral Agreement.

(e)   In the case of an Electricity Storage Module, additional input signals (e.g. state of energy  (MWhr, and system availability) may be specified in the Bilateral Agreement. A Power Available signal will also be specified in the Bilateral Agreement in accordance with the requirements of ECC.6.5.6.4(d).

ECC.6.5.6.5	In addition to the requirements of the Balancing Codes, each HVDC Converter unit of an HVDC system shall be equipped with an automatic controller capable of receiving instructions from The Company. This automatic controller shall be capable of operating the HVDC Converter units of the HVDC System in a coordinated way. The Company shall specify the automatic controller hierarchy per HVDC Converter unit.

ECC.6.5.6.6	The automatic controller of the HVDC System referred to in paragraph ECC.6.5.6.5  shall be capable of sending the following signal types to The Company (where applicable) :

(a) operational metering signals, providing at least the following:

(i) start-up signals;

(ii) AC and DC voltage measurements;

(iii) AC and DC current measurements;

(iv) Active and Reactive Power measurements on the AC side;

(v) DC power measurements;

(vi) HVDC Converter unit level operation in a multi-pole type HVDC Converter;

(vii) elements and topology status; and

(viii) Frequency Sensitive Mode, Limited Frequency Sensitive Mode Overfrequency and 		Limited Frequency Sensitive Mode  Underfrequency Active Power ranges (where 		applicable).

(b) alarm signals, providing at least the following:

(i) emergency blocking;

(ii) ramp blocking;

(iii) fast Active Power reversal (where applicable)

ECC.6.5.6.7  	The automatic controller referred to in ECC.6.5.6.5  shall be capable of receiving the following signal types from The Company (where applicable) :

(a) operational metering signals, receiving at least the following:

(i) start-up command;

(ii) Active Power setpoints;

(iii) Frequency Sensitive Mode settings;

(iv) Reactive Power, voltage or similar setpoints;

(v) Reactive Power control modes;

(vi) power oscillation damping control; and

(b) alarm signals, receiving at least the following:

(i) emergency blocking command;

(ii) ramp blocking command;

(iii) Active Power flow direction; and

(iv)) fast Active Power reversal command.

ECC.6.5.6.8	With regards to operational metering signals, the resolution and refresh rate required would be 1 second or better unless otherwise agreed with The Company

ECC.6.5.6.9	In addition to the above requirements, Restoration Contractors shall be capable of providing the operational metering requirements specified in the Anchor Restoration Contract or Top Up Restoration Contract during System Restoration.  In particular for renewable generation, the volume of primary energy such as wind speed and in the case of storage, storage capacity shall be provided.

Instructor Facilities

ECC.6.5.7	The EU Code User shall accommodate Instructor Facilities provided by The Company for the receipt of operational messages relating to System conditions.

Electronic Data Communication Facilities

ECC.6.5.8	(a)	All BM Participants must ensure that appropriate electronic data communication facilities are in place to permit the submission of data, as required by the Grid Code, to The Company.

(b)	In addition,

(1)	any User that wishes to participate in the Balancing Mechanism;

or

(2)	any BM Participant in respect of its BM Units at a Power Station and the BM Participant is required to provide all Part 1 System Ancillary Services in accordance with ECC.8.1 (unless The Company has otherwise agreed)

must ensure that appropriate automatic logging devices are installed at the Control Points of its BM Units to submit data to and to receive instructions from The Company, as required by the Grid Code. For the avoidance of doubt, in the case of an Interconnector User the Control Point will be at the Control Centre of the appropriate Externally Interconnected System Operator.

(c)	Detailed specifications of these required electronic facilities will be provided by The Company on request and they are listed as Electrical Standards in the Annex to the General Conditions.

Facsimile Machines

ECC.6.5.9	Each User and The Company shall provide a facsimile machine or machines:

(a)	in the case of Generators, at the Control Point of each Power Station and at its Trading Point;

(b)	in the case of The Company and Network Operators, at the Control Centre(s); and

(c)	in the case of Non-Embedded Customers and HVDC Equipment owners at the Control Point.

Each User shall notify, prior to connection to the System of the User's Plant and Apparatus, The Company of its or their telephone number or numbers, and will notify The Company of any changes.  Prior to connection to the System of the User's Plant and Apparatus The Company shall notify each User of the telephone number or numbers of its facsimile machine or machines and will notify any changes.

ECC.6.5.10	Busbar Voltage

The Relevant Transmission Licensee shall, subject as provided below, provide each Generator or HVDC System Owner at each Grid Entry Point where one of its Power Stations or HVDC Systems is connected with appropriate voltage signals to enable the Generator or HVDC System  owner to obtain the necessary information to permit its Power Generating Modules (including DC Connected Power Park Modules) or HVDC System to be Synchronised to the National Electricity Transmission System.  The term "voltage signal" shall mean in this context, a point of connection on (or wire or wires from) a relevant part of Transmission Plant and/or Apparatus at the Grid Entry Point, to which the Generator or HVDC System Owner, with The Company's agreement (not to be unreasonably withheld) in relation to the Plant and/or Apparatus to be attached, will be able to attach its Plant and/or Apparatus (normally a wire or wires) in order to obtain measurement outputs in relation to the busbar.

ECC.6.5.11	Bilingual Message Facilities

(a)	A Bilingual Message Facility is the method by which the User’s Responsible Engineer/Operator, the Externally Interconnected System Operator and The Company’s Control Engineers communicate clear and unambiguous information in two languages for the purposes of control of the Total System in both normal and emergency operating conditions.

(b)	A Bilingual Message Facility, where required, will provide up to two hundred pre-defined messages with up to five hundred and sixty characters each. A maximum of one minute is allowed for the transmission to, and display of, the selected message at any destination. The standard messages must be capable of being displayed at any combination of locations and can originate from any of these locations. Messages displayed in the UK will be displayed in the English language.

(c)	Detailed information on a Bilingual Message Facility and suitable equipment required for individual User applications will be provided by The Company upon request.

ECC.6.6	Monitoring

ECC.6.6.1	System Monitoring

ECC.6.6.1.1	Each Type C and Type D Power Generating Module  including DC Connected Power Park Modules shall be equipped with a facility to provide fault recording and monitoring of dynamic system behaviour. These requirements are necessary to record conditions during System faults and detect poorly damped power oscillations. This facility shall record the following parameters:

— voltage,

— Active Power,

— Reactive Power, and

— Frequency.

ECC.6.6.1.2		Detailed specifications for fault recording and dynamic system monitoring equipment including triggering criteria and sample rates  are listed as Electrical Standards in the Annex to the General Conditions. For Dynamic System Monitoring, the specification for the communication protocol and recorded data shall also be included in the Electrical Standard.

ECC.6.6.1.3	The Company in coordination with the Relevant Transmission Licensee shall specify any requirements for Power Quality Monitoring in the Bilateral Agreement.   The power quality parameters to be monitored, the communication protocols for the recorded data and the time frames for compliance shall be agreed between The Company, the Relevant Transmission Licensee and EU Generator.

ECC.6.6.1.4	HVDC Systems shall be equipped with a facility to provide fault recording and dynamic system behaviour monitoring of the following parameters for each of its HVDC Converter Stations:

(a) AC and DC voltage;

(b) AC and DC current;

(c) Active Power;

(d) Reactive Power; and

(e) Frequency.

ECC.6.6.1.5	 The Company in coordination with the Relevant Transmission Licensee may specify quality of supply parameters to be complied with by the HVDC System, provided a reasonable prior notice is given.

ECC.6.6.1.6	 The particulars of the fault recording equipment referred to in ECC.6.6.1.4, including analogue and digital channels, the settings, including triggering criteria and the sampling rates, shall be agreed between the HVDC System Owner and The Company in coordination with the Relevant Transmission Licensee.

ECC.6.6.1.7	All dynamic system behaviour monitoring equipment shall include an oscillation trigger, specified by The Company, in coordination with the Relevant Transmission Licensee, with the purpose of detecting poorly damped power oscillations.

ECC.6.6.1.8	The facilities for quality of supply and dynamic system behaviour monitoring shall include arrangements for the HVDC System Owner and The Company and/or Relevant Transmission Licensee to access the information electronically. The communications protocols for recorded data shall be agreed between the HVDC System Owner, The Company and the Relevant Transmission Licensee.

ECC.6.6.1.9	In order to accurately monitor the performance of a Grid Forming Plant, each Grid Forming Plant shall be equipped with a facility to accurately record the following parameters at a rate of 10ms : -

- System Frequency using a nominated algorithm as defined by The Company

- The ROCOF rate using a nominated algorithm as defined by The Company based on a 500ms rolling average

- A technique for recording the Grid Phase Jump Angle by using either a nominated algorithm as defined by The Company or an algorithm that records the time period of each half cycle with a time resolution of 10 microseconds.  For a 50Hz System, a 1 degree phase jump is a time period change of 55.6 microseconds.

ECC.6.6.1.10	Detailed specifications for Grid Forming Capability Plant dynamic performance	including triggering criteria, sample rates, the communication protocol and recorded data shall be  specified by The Company in the Bilateral Agreement.

ECC.6.6.2	Frequency Response Monitoring

ECC.6.6.2.1	Each Type C and Type D Power Generating Module including DC Connected Power Park Modules shall be fitted with equipment capable of monitoring the real time Active Power output of a Power Generating Module when operating in Frequency Sensitive Mode.

ECC.6.6.2.2

Detailed specifications of the Active Power Frequency response requirements including the communication requirements are listed as Electrical Standards in the Annex to the General Conditions.

ECC.6.6.2.3	The Company in co-ordination with the Relevant Transmission Licensee shall specify additional signals to be provided by the EU Generator by monitoring and recording devices in order to verify the performance of the Active Power Frequency response provision of participating Power Generating Modules.

ECC.6.6.3	Compliance Monitoring

ECC.6.6.3.1	For all on site monitoring by The Company of witnessed tests pursuant to the CP or OC5 or ECP the User shall provide suitable test signals as outlined in either OC5.A.1or ECP.A.4 (as applicable).

ECC.6.6.3.2	The signals which shall be provided by the User to The Company for onsite monitoring shall be of the following resolution, unless otherwise agreed by The Company:

(i)	1 Hz for reactive range tests

(ii)	10 Hz for frequency control tests

(iii)	100 Hz for voltage control tests

(iv)	1 kHz for Grid Forming Plant signals including fast fault current measurements

(v)	100Hz for the other Grid Forming Plant tests carried out in accordance with ECC.6.6.1.9

ECC.6.6.3.3	The User will provide all relevant signals for this purpose in the form of d.c. voltages within the range -10V to +10V. In exceptional circumstances some signals may be accepted as d.c. voltages within the range -60V to +60V with prior agreement between the User and The Company. All signals shall:

(i)	in the case of an Onshore Power Generating Module or Onshore  HVDC Convertor Station, be suitably terminated in a single accessible location at the Generator or HVDC Converter Station owner’s site.

(ii)	in the case of an Offshore Power Generating Module and OTSDUW Plant and Apparatus, be transmitted onshore without attenuation, delay or filtering which would result in the inability to fully demonstrate the objectives of the test, or identify any potential safety or plant instability issues, and be suitably terminated in a single robust location normally located at or near the onshore Interface Point of the Offshore Transmission System to which it is connected.

ECC.6.6.3.4	All signals shall be suitably scaled across the range. The following scaling would (unless The Company notify the User otherwise) be acceptable to The Company:

(a)	0MW to Maximum Capacity or Interface Point Capacity 0-8V dc

(b)	Maximum leading Reactive Power to maximum lagging Reactive Power  -8 to 8V dc

(c)	48 – 52Hz as -8 to 8V dc

(d)	Nominal terminal or connection point voltage -10% to +10% as -8 to 8V dc

ECC.6.6.3.5	The User shall provide to The Company a 230V power supply adjacent to the signal terminal location.

ECC.7	SITE RELATED CONDITIONS

ECC.7.1	Not used.

ECC.7.2	Responsibilities For Safety

ECC.7.2.1	Any User entering and working on its Plant and/or Apparatus (including, until the OTSUA Transfer Time, any OTSUA) on a Transmission Site will work to the Safety Rules of the Relevant Transmission Licensee, as advised by The Company.

ECC.7.2.2	For User Sites, The Company shall procure that the Relevant Transmission Licensee entering and working on Transmission Plant and/or Apparatus on a User Site will work to the User’s Safety Rules.

ECC.7.2.3	A User may, with a minimum of six weeks notice, apply to The Company for permission to work according to that Users own Safety Rules when working on its Plant and/or Apparatus on a Transmission Site rather than those set out in ECC.7.2.1.  If The Company is of the opinion that the User's Safety Rules provide for a level of safety commensurate with those set out in ECC.7.2.1, The Company will notify the User, in writing, that, with effect from the date requested by the User, the User may use its own Safety Rules when working on its Plant and/or Apparatus on the Transmission Site.  For a Transmission Site, in forming its opinion, The Company will seek the opinion of the Relevant Transmission Licensee. Until receipt of such written approval from The Company, the User will continue to use the Safety Rules as set out in ECC.7.2.1.

ECC.7.2.4		In the case of a User Site, The Company may, with a minimum of six weeks notice, apply to a User for permission for the Relevant Transmission Licensee to work according to the Relevant Transmission Licensee’s Safety Rules when working on Transmission Plant and/or Apparatus on that User Site, rather than the User’s Safety Rules.  If the User is of the opinion that the Relevant Transmission Licensee’s Safety Rules, provide for a level of safety commensurate with that of that User’s Safety Rules, it will notify The Company, in writing, that, with effect from the date requested by The Company, that the Relevant Transmission Licensee may use its own Safety Rules when working on its Transmission Plant and/or Apparatus on that User’s Site.  Until receipt of such written approval from the User, The Company shall procure that the Relevant Transmission Licensee shall continue to use the User’s Safety Rules.

ECC.7.2.5		For a Transmission Site, if The Company gives its approval for the User’s Safety Rules to apply to the User when working on its Plant and/or Apparatus, that does not imply that the User’s Safety Rules will apply to entering the Transmission Site and access to the User’s Plant and/or Apparatus on that Transmission Site.  Bearing in mind the Relevant Transmission Licensee’s responsibility for the whole Transmission Site, entry and access will always be in accordance with the Relevant Transmission Licensee’s site access procedures.  For a User Site, if the User gives its approval for Relevant Transmission Licensee Safety Rules to apply to the Relevant Transmission Licensee when working on its Plant and Apparatus, that does not imply that the Relevant Transmission Licensee’s Safety Rules will apply to entering the User Site, and access to the Transmission Plant and Apparatus on that User Site.  Bearing in mind the User’s responsibility for the whole User Site, entry and access will always be in accordance with the User’s site access procedures.

ECC.7.2.6		For User Sites, Users shall notify The Company of any Safety Rules that apply to the Relevant Transmission Licensee’s staff working on User Sites. The Company shall procure that the Relevant Transmission Licensee shall notify Users of any Safety Rules that apply to the User’s staff working on the Transmission Site.

ECC.7.2.7	Each Site Responsibility Schedule must have recorded on it the Safety Rules which apply to each item of Plant and/or Apparatus.

ECC.7.2.8	In the case of OTSUA a User Site or Transmission Site shall, for the purposes of this ECC.7.2, include a site at which there is an Interface Point until the OTSUA Transfer Time when it becomes part of the National Electricity Transmission System.

ECC.7.3	Site Responsibility Schedules

ECC.7.3.1	In order to inform site operational staff and The Company’s Control Engineers of agreed responsibilities for Plant and/or Apparatus at the operational interface, a Site Responsibility Schedule shall be produced for Connection Sites (and in the case of OTSUA,  until the OTSUA Transfer Time, Interface Sites) for The Company, the Relevant Transmission Licensee and Users with whom they interface.

ECC.7.3.2	The format, principles and basic procedure to be used in the preparation of Site Responsibility Schedules are set down in Appendix 1.

ECC.7.4	Operation And Gas Zone Diagrams

Operation Diagrams

ECC.7.4.1	An Operation Diagram shall be prepared for each Connection Site at which a Connection Point exists (and in the case of OTSDUW Plant and Apparatus, by User’s for each Interface Point) using, where appropriate, the graphical symbols shown in Part 1A of Appendix 2.  Users should also note that the provisions of OC11 apply in certain circumstances.

ECC.7.4.2	The Operation Diagram shall include all HV Apparatus and the connections to all external circuits and incorporate numbering, nomenclature and labelling, as set out in OC11. At those Connection Sites (or in the case of OTSDUW Plant and Apparatus, Interface Points) where gas-insulated metal enclosed switchgear and/or other gas-insulated HV Apparatus is installed, those items must be depicted within an area delineated by a chain dotted line which intersects gas-zone boundaries. The nomenclature used shall conform with that used on the relevant Connection Site and circuit (and in the case of OTSDUW Plant and Apparatus, Interface Point and circuit).  The Operation Diagram (and the list of technical details) is intended to provide an accurate record of the layout and circuit interconnections, ratings and numbering and nomenclature of HV Apparatus and related Plant.

ECC.7.4.3	A non-exhaustive guide to the types of HV Apparatus to be shown in the Operation Diagram is shown in Part 2 of Appendix 2, together with certain basic principles to be followed unless equivalent principles are approved by The Company.

Gas Zone Diagrams

ECC.7.4.4	A Gas Zone Diagram shall be prepared for each Connection Site at which a Connection Point (and in the case of OTSDUW Plant and Apparatus, by User’s for an Interface Point) exists where gas-insulated switchgear and/or other gas-insulated HV Apparatus is utilised.  They shall use, where appropriate, the graphical symbols shown in Part 1B of Appendix 2.

ECC.7.4.5	The nomenclature used shall conform with that used in the relevant Connection Site and circuit (and in the case of OTSDUW Plant and Apparatus, relevant Interface Point and circuit).

ECC.7.4.6	The basic principles set out in Part 2 of Appendix 2 shall be followed in the preparation of Gas Zone Diagrams unless equivalent principles are approved by The Company.

Preparation of Operation and Gas Zone Diagrams for Users' Sites and Transmission Interface Sites

ECC.7.4.7	In the case of a User Site, the User shall prepare and submit to The Company, an Operation Diagram for all HV Apparatus on the User side of the Connection Point (and in the case of OTSDUW Plant and Apparatus, on what will be the Offshore Transmission side of the Connection Point and the Interface Point) and The Company shall provide the User with an Operation Diagram for all HV Apparatus on the Transmission side of the Connection Point (and in the case of OTSDUW Plant and Apparatus on what will be the Onshore Transmission side of the Interface Point, in accordance with the timing requirements of the Bilateral Agreement and/or Construction Agreement prior to the Completion Date under the Bilateral Agreement and/or Construction Agreement.

ECC.7.4.8	The User will then prepare, produce and distribute, using the information submitted on the User's Operation Diagram and The Company’s Operation Diagram, a composite Operation Diagram for the complete Connection Site (and in the case of OTSDUW Plant and Apparatus, Interface Point), also in accordance with the timing requirements of the Bilateral Agreement and/or Construction Agreement .

ECC.7.4.9	The provisions of ECC.7.4.7 and ECC.7.4.8 shall apply in relation to Gas Zone Diagrams where gas-insulated switchgear and/or other gas-insulated HV Apparatus is utilised.

Preparation of Operation and Gas Zone Diagrams for Transmission Sites

ECC.7.4.10	In the case of an Transmission Site, the User shall prepare and submit to The Company an Operation Diagram for all HV Apparatus on the User side of the Connection Point, in accordance with the timing requirements of the Bilateral Agreement and/or Construction Agreement.

ECC.7.4.11	The Company will then prepare, produce and distribute, using the information submitted on the User's Operation Diagram, a composite Operation Diagram for the complete Connection Site, also in accordance with the timing requirements of the Bilateral Agreement and/or Construction Agreement .

ECC.7.4.12	The provisions of ECC.7.4.10 and ECC.7.4.11 shall apply in relation to Gas Zone Diagrams where gas-insulated switchgear and/or other gas-insulated HV Apparatus is utilised.

ECC.7.4.13	Changes to Operation and Gas Zone Diagrams

ECC.7.4.13.1	When The Company has decided that it wishes to install new HV Apparatus or it wishes to change the existing numbering or nomenclature of Transmission HV Apparatus at a Transmission Site, The Company will (unless it gives rise to a Modification under the CUSC, in which case the provisions of the CUSC as to the timing apply) one month prior to the installation or change, send to each such User a revised Operation Diagram of that Transmission Site, incorporating the new Transmission HV Apparatus to be installed and its numbering and nomenclature or the changes, as the case may be. OC11 is also relevant to certain Apparatus.

ECC.7.4.13.2	When a User has decided that it wishes to install new HV Apparatus, or it wishes to change the existing numbering or nomenclature of its HV Apparatus at its User Site, the User will (unless it gives rise to a Modification under the CUSC, in which case the provisions of the CUSC as to the timing apply) one month prior to the installation or change, send to The Company a revised Operation Diagram of that User Site incorporating the EU Code User  HV Apparatus to be installed and its numbering and nomenclature or the changes as the case may be. OC11 is also relevant to certain Apparatus.

ECC.7.4.13.3	The provisions of ECC.7.4.13.1 and ECC.7.4.13.2 shall apply in relation to Gas Zone Diagrams where gas-insulated switchgear and/or other gas-insulated HV Apparatus is installed.

Validity

ECC.7.4.14	(a)	The composite Operation Diagram prepared by The Company or the User, as the case may be, will be the definitive Operation Diagram for all operational and planning activities associated with the Connection Site. If a dispute arises as to the accuracy of the composite Operation Diagram, a meeting shall be held at the Connection Site, as soon as reasonably practicable, between The Company and the User, to endeavour to resolve the matters in dispute.

(b)	The composite Operation Diagram prepared by The Company or the User, as the case may be, will be the definitive Operation Diagram for all operational and planning activities associated with the Interface Point until the OTSUA Transfer Time. If a dispute arises as to the accuracy of the composite Operation Diagram prior to the OTSUA Transfer Time, a meeting shall be held at the Interface Point, as soon as reasonably practicable, between The Company and the User, to endeavour to resolve the matters in dispute.

(c)	An equivalent rule shall apply for Gas Zone Diagrams where they exist for a Connection Site.

ECC.7.4.15	In the case of OTSUA, a User Site and Transmission Site shall, for the purposes of this ECC.7.4, include a site at which there is an Interface Point until the OTSUA Transfer Time when it becomes part of the National Electricity Transmission System and references to HV Apparatus in this ECC.7.4 shall include references to HV OTSUA.

ECC.7.5	Site Common Drawings

ECC.7.5.1	Site Common Drawings will be prepared for each Connection Site (and in the case of OTSDUW, each Interface Point) and will include Connection Site (and in the case of OTSDUW, Interface Point) layout drawings, electrical layout drawings, common Protection/control drawings and common services drawings.

Preparation of Site Common Drawings for a User Site and Transmission Interface Site

ECC.7.5.2	In the case of a User Site, The Company shall prepare and submit to the User, Site Common Drawings for the Transmission side of the Connection Point (and in the case of OTSDUW Plant and Apparatus, on what will be the Onshore Transmission side of the Interface Point,) and the User shall prepare and submit to The Company, Site Common Drawings for the User side of the Connection Point (and in the case of OTSDUW, on what will be the Offshore Transmission side of the Interface Point) in accordance with the timing requirements of the Bilateral Agreement and/or Construction Agreement.

ECC.7.5.3	The User will then prepare, produce and distribute, using the information submitted on the Transmission Site Common Drawings, Site Common Drawings for the complete Connection Site (and in the case of OTSDUW, Interface Point) in accordance with the timing requirements of the Bilateral Agreement and/or Construction Agreement .

Preparation of Site Common Drawings for a Transmission Site

ECC.7.5.4	In the case of a Transmission Site, the User will prepare and submit to The Company Site Common Drawings for the User side of the Connection Point in accordance with the timing requirements of the Bilateral Agreement and/or Construction Agreement.

ECC.7.5.5	The Company will then prepare, produce and distribute, using the information submitted in the User's Site Common Drawings, Site Common Drawings for the complete Connection Site in accordance with the timing requirements of the Bilateral Agreement and/or Construction Agreement.

ECC.7.5.6	When a User becomes aware that it is necessary to change any aspect of the Site Common Drawings at a Connection Site (and in the case of OTSDUW, Interface Point) it will:

(a)	if it is a User Site, as soon as reasonably practicable, prepare, produce and distribute revised Site Common Drawings for the complete Connection Site (and in the case of OTSDUW, Interface Point); and

(b)	if it is a Transmission Site, as soon as reasonably practicable, prepare and submit to The Company revised Site Common Drawings for the User side of the Connection Point (and in the case of OTSDUW, Interface Point) and The Company will then, as soon as reasonably practicable, prepare, produce and distribute, using the information submitted in the User's Site Common Drawings, revised Site Common Drawings for the complete Connection Site (and in the case of OTSDUW, Interface Point).

In either case, if in the User's reasonable opinion the change can be dealt with by it notifying The Company in writing of the change and for each party to amend its copy of the Site Common Drawings (or where there is only one set, for the party holding that set to amend it), then it shall so notify and each party shall so amend.  If the change gives rise to a Modification under the CUSC, the provisions of the CUSC as to timing will apply.

ECC.7.5.7	When The Company becomes aware that it is necessary to change any aspect of the Site Common Drawings at a Connection Site(and in the case of OTSDUW, Interface Point)  it will:

(a)	if it is a Transmission Site, as soon as reasonably practicable, prepare, produce and distribute revised Site Common Drawings for the complete Connection Site (and in the case of OTSDUW, Interface Point); and

(b)	if it is a User Site, as soon as reasonably practicable, prepare and submit to the User revised Site Common Drawings for the Transmission side of the Connection Point (in the case of OTSDUW, Interface Point) and the User will then, as soon as reasonably practicable, prepare, produce and distribute, using the information submitted in the Transmission Site Common Drawings, revised Site Common Drawings for the complete Connection Site (and in the case of OTSDUW, Interface Point).

In either case, if in The Company's reasonable opinion the change can be dealt with by it notifying the User in writing of the change and for each party to amend its copy of the Site Common Drawings (or where there is only one set, for the party holding that set to amend it), then it shall so notify and each party shall so amend.  If the change gives rise to a Modification under the CUSC, the provisions of the CUSC as to timing will apply.

Validity

ECC.7.5.8	(a)	The Site Common Drawings for the complete Connection Site prepared by the User or The Company, as the case may be, will be the definitive Site Common Drawings for all operational and planning activities associated with the Connection Site. If a dispute arises as to the accuracy of the Site Common Drawings, a meeting shall be held at the Site, as soon as reasonably practicable, between The Company and the User, to endeavour to resolve the matters in dispute.

(b)	The Site Common Drawing prepared by The Company or the User, as the case may be, will be the definitive Site Common Drawing for all operational and planning activities associated with the Interface Point until the OTSUA Transfer Time. If a dispute arises as to the accuracy of the composite Operation Diagram prior to the OTSUA Transfer Time, a meeting shall be held at the Interface Point, as soon as reasonably practicable, between The Company and the User, to endeavour to resolve the matters in dispute.

ECC.7.5.9	In the case of OTSUA, a User Site and Transmission Site shall, for the purposes of this ECC.7.5, include a site at which there is an  Interface Point until the OTSUA Transfer Time when it becomes part of the National Electricity Transmission System.

ECC.7.6	Access

ECC.7.6.1	The provisions relating to access to Transmission Sites by Users, and to Users' Sites by Relevant Transmission Licensees, are set out in each Interface Agreement (or in the case of Interfaces Sites prior to the OTSUA Transfer Time agreements in similar form) with, the Relevant Transmission Licensee and each User.

ECC.7.6.2	In addition to those provisions, where a Transmission Site contains exposed HV conductors, unaccompanied access will only be granted to individuals holding an Authority for Access issued by the Relevant Transmission Licensee.

ECC.7.6.3	The procedure for applying for an Authority for Access is contained in the Interface Agreement.

ECC.7.7	Maintenance Standards

ECC.7.7.1	It is the User's responsibility to ensure that all its Plant and Apparatus (including, until the OTSUA Transfer Time, any OTSUA) on a Transmission Site is tested and maintained adequately for the purpose for which it is intended, and to ensure that it does not pose a threat to the safety of any Transmission Plant, Apparatus or personnel on the Transmission Site.  The Company will have the right to inspect the test results and maintenance records relating to such Plant and Apparatus at any time

ECC.7.7.2		For User Sites, The Company shall procure that the Relevant Transmission Licensee has a responsibility to ensure that all Transmission Plant and Apparatus on a User Site is tested and maintained adequately for the purposes for which it is intended and to ensure that it does not pose a threat to the safety of any User’s Plant, Apparatus or personnel on the User Site.

The User will have the right to inspect the test results and maintenance records relating to such Plant and Apparatus on its User Site at any time.

ECC.7.8	Site Operational Procedures

ECC.7.8.1	Where there is an interface with National Electricity Transmission System The Company and Users must make available staff to take necessary Safety Precautions and carry out operational duties as may be required to enable work/testing to be carried out and for the operation of Plant and Apparatus (including, prior to the OTSUA Transfer Time, any OTSUA) connected to the Total System.

ECC.7.9	Generators, HVDC System owners and BM Participants (including Virtual Lead Parties)   shall provide a Control Point.

- In the case of EU Generators and HVDC System owners, for each Power Station or HVDC System directly connected to the National Electricity Transmission System and for each Embedded Large Power Station or Embedded HVDC System, the Control Point shall receive and act upon instructions pursuant to OC7 and BC2 at all times that Power Generating Modules at the Power Station are generating or available to generate or HVDC Systems are importing or exporting or available to do so. In the case of all BM Participants, the Control Point shall be continuously staffed except in the case of an Embedded Power Station where Purchase Contracts for its Main Plant and Apparatus had been concluded before 1st June 2027 and where the Bilateral Agreement specifies that compliance with BC2 is not required, in which case the Control Point shall be staffed between the hours of 0800 and 1800 each day. Any Generator in respect of an Embedded Large Power Station where Purchase Contracts for its Main Plant and Apparatus had been concluded on or after 1st June 2027 or where Purchase Contracts relating to a Substantial Modification in respect of its Main Plant and Apparatus had been concluded on or after 1st June 2027 and which applied for a Connection Agreement on or after XXXXXX [XXXXXX this being the Implementation Date,  which is ten working days after the Authority Decision date], shall be required to have a Control Point that shall be continuously staffed.

- In the case of BM Participants, the BM Participant’s Control Point shall be capable of receiving and acting upon instructions from The Company and the relevant Transmission Licensees’ Control Engineers.

The Company will normally issue instructions via automatic logging devices in accordance with the requirements of ECC.6.5.8(b).

Where the BM Participant’s Plant and Apparatus does not respond to an instruction from The Company via automatic logging devices, or where it is not possible for The Company to issue the instruction via automatic logging devices, The Company shall issue the instruction by telephone.

In the case of BM Participants who own and/or operate Power Stations or HVDC Systems with an aggregated Registered Capacity or BM Participants with BM Units with an aggregated Demand Capacity per Control Point of less than 50MW, or, where a site is not part of a Virtual Lead Party as defined in the BSC, a Registered Capacity or Demand Capacity per site of less than 10MW

- where this situation arises, a representative of the BM Participant is required to be available to respond to instructions from The Company via the Control Telephony or System Telephony system, as provided for in ECC.6.5.4, between the hours of 0800-1800 each day.

- Outside the hours of 0800-1800 each day, the requirements of BC2.9.7 shall apply.

For the avoidance of doubt, BM Participants who are unable to provide Control Telephony and do not have a continuously staffed Control Point may be unable to act as a Defence Service Provider and shall be unable to act as a Restoration Contractor where these require Control Telephony or a Control Point in respect of the specification of any such services falling into these categories.

ECC.7.10	Obligations on Users in respect of Critical Tools and Facilities

ECC.7.10.1		From 04/09/2024 The Company, each Generator, HVDC System Owner, Network Operator, Non-Embedded Customer and each Restoration Contractor with a continuously staffed Control Point or Control Centre as provided for in ECC.7.9 shall:-

- Ensure they have the appropriate Critical Tools and Facilities, necessary to control their assets for System Restoration, from their Control Point or Control Centre, as appropriate, for a minimum period of 72 hours (or such longer period as agreed between the Generator, HVDC System Owner, Network Operator, Non-Embedded Customer and/or Restoration Contractor and The Company) following a Total Shutdown or Partial Shutdown.

- Ensure as far as reasonably practical that they have adequate control equipment redundancy in place so that in the event of a failure of one or more components of the control system its function is unimpaired.

- Report on the results of their management and testing for their Critical Tools and Facilities on request from The Company.

ECC.7.10.2	From 04/09/2024 each BM Participant including a Virtual Lead Party with a continuously staffed Control Point as provided for in ECC.7.9 (excluding those BM Participants covered by the requirements of ECC.7.10.1), shall:-

- Ensure they have the appropriate Critical Tools and Facilities (as defined in clause (c) of the definition of Critical Tools and Facilities in the Grid Code Glossary and Definitions) for a minimum period of 72 hours (or such longer period as agreed between the BM Participant including a Virtual Lead Party and The Company) following a Total Shutdown or Partial Shutdown.

- Ensure as far as reasonably practical that they have adequate control equipment redundancy in place at their Control Point so that in the event of a failure of one or more components of their Critical Tools and Facilities its function is unimpaired.

- Report on the results of their management and testing for their Critical Tools and Facilities on request by The Company.

ECC.7.10.3	In the case of a BM Participant or Virtual Lead Party which has an Anchor Restoration Contract or Top Up Restoration Contract in respect of one or more of its aggregated Plants, the requirements of ECC.7.10.1 shall only apply between the Control Point of the BM Participant or Virtual Lead Party and that Plant with an Anchor Plant Capability or Top Up Restoration Capability.  For other non-contracted Plants under the control of the BM Participant or Virtual Lead Party, the requirements of ECC.7.10.2 shall continue to apply.

ECC.7.10.4	Where a Network Operator installs a Distribution Restoration Zone Control System to facilitate operation of a Distribution Restoration Zone Plan, the high level functional requirements of the Distribution Restoration Zone Control System shall be in accordance with the guidance provided in the applicable electrical standard listed in the annex to the General Conditions.

ECC.7.10.5	Network Operators shall ensure that their substations which are required to be operable during System Restoration have 72 hour electrical supply resilience to facilitate Network Operators being able to:

- restore auxiliary supplies to Transmission substations;

- switch Demand in accordance with a Restoration Plan;

- support The Company in satisfying the requirements of the Electricity System Restoration Standard.

ECC.7.10.6	The Company, each EU Code User and Restoration Contractor shall ensure their Critical Tools and Facilities are cyber secure accordance with the Security of Network and Information System (NIS) Regulations.  This requirement applies to The Company, EU Code Users and Restoration Contractors at all times.

ECC.7.10.7	Notwithstanding the requirements of ECC.7.10.1, The Company, each EU Code User and Restoration Contractor shall ensure that their control systems, communications systems, operational metering and telemetry systems including SCADA, are sufficiently robust and reliable such that they are capable of handling, processing and prioritising the significant volumes of data that could reasonably be expected to occur during System Restoration.

ECC.7.10.8	Where an Offshore Generator is connected to an Offshore Transmission System and the Offshore Transmission Licensee does not have Critical Tools and Facilities installed on its Offshore Transmission System, The Company will make an allowance for the Critical Tools and Facilities required to be installed by the Offshore Generator.

ECC.7.11		Obligations on and Assurance from The Company, EU Code Users and Restoration Contractors during Total Shutdown and Partial Shutdown conditions

ECC.7.11.1	In respect of The Company, its Apparatus shall be designed such that it can safely shutdown and does not pose a risk to personnel or Apparatus in the event of a total loss of supply.

ECC.7.11.2	All EU Code Users and Restoration Contractors shall ensure their Plant and Apparatus can safely shut down and does not pose a risk to Plant and/or personnel in the event of a total loss of supplies at a EU Code User’s Site(s) or Restoration Contractor’s site be it caused by a Total Shutdown, Partial Shutdown or such other event.   In satisfying this requirement, Generators, HVDC System Owners and Restoration Contractors shall be able to demonstrate to The Company that in the event supplies were to be lost to their Site, then on the restoration of supplies, their Plant can be made operational and begin to operate in at least the same way and as quickly as would be expected for a cold start following a Total System Shutdown or Partial System Shutdown in accordance with the data submitted in PC.A.5.7 in accordance with the Week 24 process.   For EU Code Users where they believe this requirement is cost prohibitive or technically impossible, such EU Code Users shall discuss the issue with The Company, and The Company shall inform The Authority of the details agreed.  Where such an issue cannot be agreed by The Company following all reasonable attempts or where the capability provided by the EU Code User cannot be agreed by The Company as being sufficient after examining all reasonable alternative solutions through the Compliance Processes, the EU Code User may apply for a derogation from the Grid Code.

ECC.7.11.3	The requirements of ECC.7.11.1 and ECC.7.11.2 shall apply for a period of total loss of supplies to The Company’s operational sites or an EU Code User’s Site or Restoration Contractor’s site of up to 72 hours.  EU Code Users and Restoration Contractors shall confirm to The Company that the total loss of supplies to their Site for a period of up to 72 hours shall not result in damage to Plant and Apparatus such that it would then be unable to operate upon restoration of electrical supplies to the site.

ECC.7.11.4	Network Operators shall ensure that in coordination with The Company and relevant Transmission Licensees, they have the capability to switch Demand at sufficient speed to support The Company in satisfying the requirements of the Electricity System Restoration Standard.  This requirement assumes:

- the successful implementation of Restoration Plans;

- the successful delivery of the obligations of Restoration Contractors who are parties to these plans; and

- the further requirements of OC9 have been implemented.

ECC.8	ANCILLARY SERVICES

ECC.8.1	System Ancillary Services

The ECC contain requirements for the capability for certain Ancillary Services, which are needed for System reasons ("System Ancillary Services").  There follows a list of these System Ancillary Services, together with the paragraph number of the ECC (or other part of the Grid Code) in which the minimum capability is required or referred to.  The list is divided into two categories:  Part 1 lists the System Ancillary Services which

(a)	Generators in respect of Type C and Type D Power Generating Modules (including DC Connected Power Park Modules and Electricity Storage Modules) are obliged to provide; and,

(b)	HVDC System Owners are obliged to have the capability to supply;

(c)	Generators in respect of Medium Power Stations (except Embedded Medium Power Stations) are obliged to provide in respect of Reactive Power only:

and Part 2 lists the System Ancillary Services which Generators or Restoration Contractors will provide only if agreement to provide them is reached with The Company  or in the case where a Restoration Contractor is party to a Distribution Restoration Zone Plan, agreement is reached with The Company and Network Operator:

Part 1

(a)	Reactive Power supplied (in accordance with ECC.6.3.2)

(b)	Frequency Control by means of Frequency sensitive generation - ECC.6.3.7 and BC3.5.1.

Part 2

(c)	Frequency Control by means of Fast Start - ECC.6.3.14.

(d)	Anchor Plant Capability or Top Up Restoration Capability - ECC.6.3.5.

(e)	System to Generator Operational Intertripping.

(f)	Services provided by Restoration Contractors.

ECC.8.2	Commercial Ancillary Services

Other Ancillary Services are also utilised by The Company in operating the Total System if these have been agreed to be provided by a User (or other person) under an Ancillary Services Agreement or under a Bilateral Agreement, with payment being dealt with under an Ancillary Services Agreement or in the case of Externally Interconnected System Operators or Interconnector Users, under any other agreement (and in the case of Externally Interconnected System Operators and Interconnector Users includes ancillary services equivalent to or similar to System Ancillary Services) ("Commercial Ancillary Services").  The capability for these Commercial Ancillary Services is set out in the relevant Ancillary Services Agreement or Bilateral Agreement (as the case may be).

APPENDIX E1 - SITE RESPONSIBILITY SCHEDULES

FORMAT, PRINCIPLES AND BASIC PROCEDURE TO BE USED IN THE PREPARATION OF SITE RESPONSIBILITY SCHEDULES

ECC.A.1.1	Principles

Types of Schedules

ECC.A.1.1.1	At all Complexes (which in the context of this ECC shall include, Interface Sites until the OTSUA Transfer Time) the following Site Responsibility Schedules shall be drawn up using the relevant proforma attached or with such variations as may be agreed between The Company and EU Code Users, but in the absence of agreement the relevant proforma attached will be used. In addition, in the case of OTSDUW Plant and Apparatus, and in readiness for the OTSUA Transfer Time, the User shall provide The Company with the necessary information such that Site Responsibility Schedules in this form can be prepared by the Relevant Transmission Licensees for the Transmission Interface Site:

(a)	Schedule of HV Apparatus

(b)	Schedule of Plant, LV/MV Apparatus, services and supplies;

(c)	Schedule of telecommunications and measurements Apparatus.

Other than at Power Generating Module (including DC Connected Power Park Modules) and Power Station locations, the schedules referred to in (b) and (c) may be combined.

New Connection Sites

ECC.A.1.1.2	In the case of a new Connection Site each Site Responsibility Schedule for a Connection Site shall be prepared by The Company in consultation with relevant Users at least 2 weeks prior to the Completion Date (or, where the OTSUA is to become Operational prior to the OTSUA Transfer Time, an alternative date) under the Bilateral Agreement and/or Construction Agreement for that Connection Site (which may form part of a Complex).   In the case of a new Interface Site where the OTSUA is to become Operational prior to the OTSUA Transfer Time each Site Responsibility Schedule for an Interface Site shall be prepared by The Company in consultation with relevant Users at least 2 weeks prior to the Completion Date under the Bilateral Agreement and/or Construction Agreement for that Interface Site (which may form part of a Complex) (and references to and requirements placed on “Connection Site” in this ECC shall also be read as “Interface Site” where the context requires and until the OTSUA Transfer Time).  Each User shall, in accordance with the timing requirements of the Bilateral Agreement and/or Construction Agreement , provide information to The Company to enable it to prepare the Site Responsibility Schedule.

Sub-division

ECC.A.1.1.3	Each Site Responsibility Schedule will be subdivided to take account of any separate Connection Sites on that Complex.

Scope

ECC.A.1.1.4	Each Site Responsibility Schedule shall detail for each item of Plant and Apparatus:

(a)	Plant/Apparatus ownership;

(b)	Site Manager (Controller) (except in the case of Plant/Apparatus located in SPT’s Transmission Area);

(c)	Safety issues comprising applicable Safety Rules and Control Person or other responsible person (Safety Co-ordinator), or such other person who is responsible for safety;

(d)	Operations issues comprising applicable Operational Procedures and control engineer;

(e)	Responsibility to undertake statutory inspections, fault investigation and  maintenance.

Each Connection Point shall be precisely shown.

Detail

ECC.A.1.1.5	(a)	In the case of Site Responsibility Schedules referred to in ECC.A.1.1.1(b) and (c), with the exception of Protection Apparatus and Intertrip Apparatus operation, it will be sufficient to indicate the responsible User or Transmission Licensee, as the case may be.

(b)	In the case of the Site Responsibility Schedule referred to in ECC.A.1.1.1(a) and for Protection Apparatus and Intertrip Apparatus, the responsible management unit must be shown in addition to the User or Transmission Licensee, as the case may be.

ECC.A.1.1.6	The HV Apparatus Site Responsibility Schedule for each Connection Site must include lines and cables emanating from or traversing the Connection Site.

Issue Details

ECC.A.1.1.7	Every page of each Site Responsibility Schedule shall bear the date of issue and the issue number.

Accuracy Confirmation

ECC.A.1.1.8	When a Site Responsibility Schedule is prepared it shall be sent by The Company to the Users involved for confirmation of its accuracy.

ECC.A.1.1.9	The Site Responsibility Schedule shall then be signed on behalf of The Company by its Responsible Manager (see ECC.A.1.1.16) and on behalf of each User involved by its Responsible Manager (see ECC.A.1.1.16), by way of written confirmation of its accuracy.  The Site Responsibility Schedule will also be signed on behalf of the Relevant Transmission Licensee by its Responsible Manager.

Distribution and Availability

ECC.A.1.1.10	Once signed, two copies will be distributed by The Company, not less than two weeks prior to its implementation date, to each User which is a party on the Site Responsibility Schedule, accompanied by a note indicating the issue number and the date of implementation.

ECC.A.1.1.11	The Company and Users must make the Site Responsibility Schedules readily available to operational staff at the Complex and at the other relevant control points.

Alterations to Existing Site Responsibility Schedules

ECC.A 1.1.12	Without prejudice to the provisions of ECC.A.1.1.15 which deals with urgent changes, when a User identified on a Site Responsibility Schedule becomes aware that an alteration is necessary, it must inform The Company immediately and in any event 8 weeks prior to any change taking effect (or as soon as possible after becoming aware of it, if less than 8 weeks remain when the User becomes aware of the change).  This will cover the commissioning of new Plant and/or Apparatus at the Connection Site, whether requiring a revised Bilateral Agreement or not, de-commissioning of Plant and/or Apparatus, and other changes which affect the accuracy of the Site Responsibility Schedule.

ECC.A 1.1.13	Where The Company has been informed of a change by a User, or itself proposes a change, it will prepare a revised Site Responsibility Schedule by not less than six weeks prior to the change taking effect (subject to it having been informed or knowing of the change eight weeks prior to that time) and the procedure set out in ECC.A.1.1.8 shall be followed with regard to the revised Site Responsibility Schedule.

ECC.A 1.1.14	The revised Site Responsibility Schedule shall then be signed in accordance with the procedure set out in ECC.A.1.1.9 and distributed in accordance with the procedure set out in ECC.A.1.1.10, accompanied by a note indicating where the alteration(s) has/have been made, the new issue number and the date of implementation.

Urgent Changes

ECC.A.1.1.15	When a User identified on a Site Responsibility Schedule, or The Company, as the case may be, becomes aware that an alteration to the Site Responsibility Schedule is necessary urgently to reflect, for example, an emergency situation which has arisen outside its control, the User shall notify The Company, or The Company shall notify the User, as the case may be, immediately and will discuss:

(a)	what change is necessary to the Site Responsibility Schedule;

(b)	whether the Site Responsibility Schedule is to be modified temporarily or permanently;

(c)	the distribution of the revised Site Responsibility Schedule.

The Company will prepare a revised Site Responsibility Schedule as soon as possible, and in any event within seven days of it being informed of or knowing the necessary alteration.  The Site Responsibility Schedule will be confirmed by Users and signed on behalf of The Company and Users and the Relevant Transmission Licensee (by the persons referred to in ECC.A.1.1.9) as soon as possible after it has been prepared and sent to Users for confirmation.

Responsible Managers

ECC.A.1.1.16	Each User shall, prior to the Completion Date under each Bilateral Agreement and/or Construction Agreement, supply to The Company a list of Managers who have been duly authorised to sign Site Responsibility Schedules on behalf of the User and The Company shall, prior to the Completion Date under each Bilateral Agreement and/or Construction Agreement, supply to that User the name of its Responsible Manager and the name of the Relevant Transmission Licensee’s Responsible Manager and each shall supply to the other any changes to such list six weeks before the change takes effect where the change is anticipated, and as soon as possible after the change, where the change was not anticipated.

De-commissioning of Connection Sites

ECC.A.1.1.17	Where a Connection Site is to be de-commissioned, whichever of The Company or the User who is initiating the de-commissioning must contact the other to arrange for the Site Responsibility Schedule to be amended at the relevant time.

PROFORMA FOR SITE RESPONSIBILITY SCHEDULE

|  | AREA |
| --- | --- |

| COMPLEX: |  |  | SCHEDULE: |  |
| --- | --- | --- | --- | --- |

| CONNECTION SITE: |  |
| --- | --- |

| ITEM OF PLANT/ APPARATUS | PLANT APPARATUS OWNER | SITE MANAGER | SAFETY |  | OPERATIONS |  | PARTY RESPONSIBLE FOR UNDERTAKING STATUTORY INSPECTIONS, FAULT INVESTIGATION & MAINTENANCE | REMARKS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | SAFETY RULES | CONTROL OR OTHER RESPONSIBLE PERSON (SAFETY CO-ORDINATOR | OPERATIONAL PROCEDURES | CONTROL OR OTHER RESPONSIBLE ENGINEER |  |  |

| PAGE: |  |  | ISSUE NO: |  |  | DATE: |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

PROFORMA FOR SITE RESPONSIBILITY SCHEDULE

|  | AREA |
| --- | --- |

| COMPLEX: |  |  | SCHEDULE: |  |
| --- | --- | --- | --- | --- |

| CONNECTION SITE: |  |
| --- | --- |

| ITEM OF PLANT/ APPARATUS | PLANT APPARATUS OWNER | SITE MANAGER | SAFETY |  | OPERATIONS |  | PARTY RESPONSIBLE FOR UNDERTAKING STATUTORY INSPECTIONS, FAULT INVESTIGATION & MAINTENANCE | REMARKS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | SAFETY RULES | CONTROL OR OTHER RESPONSIBLE PERSON (SAFETY CO-ORDINATOR | OPERATIONAL PROCEDURES | CONTROL OR OTHER RESPONSIBLE ENGINEER |  |  |

NOTES:

| SIGNED: |  | NAME: |  | COMPANY: |  | DATE: |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

| SIGNED: |  | NAME: |  | COMPANY: |  | DATE: |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

| SIGNED: |  | NAME: |  | COMPANY: |  | DATE: |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

| SIGNED: |  | NAME: |  | COMPANY: |  | DATE: |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

| PAGE: |  |  | ISSUE NO: |  |  | DATE: |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

APPENDIX E2 - OPERATION DIAGRAMS

PART 1A - PROCEDURES RELATING TO OPERATION DIAGRAMS

PART E1B - PROCEDURES RELATING TO GAS ZONE DIAGRAMS

PART E2 - NON-EXHAUSTIVE LIST OF APPARATUS

TO BE INCLUDED ON OPERATION DIAGRAMS

Basic Principles

(1)	Where practicable, all the HV Apparatus on any Connection Site shall be shown on one Operation Diagram.  Provided the clarity of the diagram is not impaired, the layout shall represent as closely as possible the geographical arrangement on the Connection Site.

(2)	Where more than one Operation Diagram is unavoidable, duplication of identical information on more than one Operation Diagram must be avoided.

(3)	The Operation Diagram must show accurately the current status of the Apparatus e.g. whether commissioned or decommissioned.  Where decommissioned, the associated switchbay will be labelled "spare bay".

(4)	Provision will be made on the Operation Diagram for signifying approvals, together with provision for details of revisions and dates.

(5)	Operation Diagrams will be prepared in A4 format or such other format as may be agreed with The Company.

(6)	The Operation Diagram should normally be drawn single line. However, where appropriate, detail which applies to individual phases shall be shown. For example, some HV Apparatus is numbered individually per phase.

Apparatus To Be Shown On Operation Diagram

(1)	Busbars

(2)	Circuit Breakers

(3)	Disconnector (Isolator) and Switch Disconnecters (Switching Isolators)

(4)	Disconnectors (Isolators) - Automatic Facilities

(5)	Bypass Facilities

(6)	Earthing Switches

(7)	Maintenance Earths

(8)	Overhead Line Entries

(9)	Overhead Line Traps

(10)	Cable and Cable Sealing Ends

(11)	Generating Unit

(12)	Generator Transformers

(13)	Generating Unit Transformers, Station Transformers, including the lower voltage circuit-breakers.

(14)	Synchronous Compensators

(15)	Static Variable Compensators

(16)	Capacitors (including Harmonic Filters)

(17)	Series or Shunt Reactors (Referred to as "Inductors" at nuclear power station sites)

(18)	Supergrid and Grid Transformers

(19)	Tertiary Windings

(20)	Earthing and Auxiliary Transformers

(21)	Three Phase VT's

(22)	Single Phase VT & Phase Identity

(23)	High Accuracy VT and Phase Identity

(24)	Surge Arrestors/Diverters

(25)	Neutral Earthing Arrangements on HV Plant

(26)	Fault Throwing Devices

(27)	Quadrature Boosters

(28)	Arc Suppression Coils

(29)	Single Phase Transformers (BR) Neutral and Phase Connections

(30)	Current Transformers (where separate plant items)

(31)	Wall Bushings

(32)	Combined VT/CT Units

(33)	Shorting and Discharge Switches

(34)	Thyristor

(35)	Resistor with Inherent Non-Linear Variability, Voltage Dependent

(36)	Gas Zone

APPENDIX E3 - MINIMUM FREQUENCY RESPONSE CAPABILITY REQUIREMENT PROFILE AND OPERATING RANGE FOR  POWER GENERATING MODULES AND HVDC EQUIPMENT

ECC.A.3.1	Scope

The frequency response capability is defined in terms of Primary Response, Secondary Response and High Frequency Response.  In addition to the requirements defined in ECC.6.3.7 this appendix defines the minimum frequency response requirements for:-

- each Type C and Type D Power Generating Module

- each DC Connected Power Park Module

- each HVDC System

For the avoidance of doubt, this appendix does not apply to Type A and Type B Power Generating Modules.

OTSDUW Plant and Apparatus should facilitate the delivery of frequency response services provided by Offshore Generating Units and Offshore Power Park Units.

The functional definition provides appropriate performance criteria relating to the provision of Frequency control by means of Frequency sensitive generation in addition to the other requirements identified in ECC.6.3.7.

In this Appendix 3 to the ECC, for a Power Generating Module including a CCGT Module or a Power Park Module or DC Connected Power Park Module, the phrase Minimum Regulating Level applies to the entire CCGT Module or Power Park Module or DC Connected Power Park Module operating with all Generating Units Synchronised to the System.

The minimum Frequency response requirement profile is shown diagrammatically in Figure ECC.A.3.1.  The capability profile specifies the minimum required level of Frequency Response Capability throughout the normal plant operating range.

ECC.A.3.2	Plant Operating Range

The upper limit of the operating range is the Maximum Capacity of the Power Generating Module or Generating Unit or CCGT Module or HVDC Equipment.

The Minimum Stable Operating Level  may be less than, but must not be more than, 65% of the Maximum Capacity.  Each Power Generating Module and/or Generating Unit and/or CCGT Module and/or Power Park Module or HVDC Equipment must be capable of operating satisfactorily down to the Minimum Regulating Level as dictated by System operating conditions, although it will not be instructed to below its Minimum Stable Operating Level .  If a Power Generating Module or Generating Unit or CCGT Module or Power Park Module, or HVDC Equipment is operating below Minimum Stable Operating Level because of high System Frequency, it should recover adequately to its Minimum Stable Operating Level as the System Frequency returns to Target Frequency so that it can provide Primary and Secondary Response from its Minimum Stable Operating Level if the System Frequency continues to fall.  For the avoidance of doubt, under normal operating conditions steady state operation below the Minimum Stable Operating Level is not expected. The  Minimum Regulating Level must not be more than 55% of Maximum Capacity.

In the event of a Power Generating Module or Generating Unit or CCGT Module or Power Park Module or HVDC Equipment load rejecting down to no less than its Minimum Regulating Level it should not trip as a result of automatic action as detailed in BC3.7.  If the load rejection is to a level less than the  Minimum Regulating Level then it is accepted that the condition might be so severe as to cause it to be disconnected from the System.

ECC.A.3.3	Minimum Frequency Response Requirement Profile

Figure ECC.A.3.1 shows the minimum Frequency response capability requirement profile diagrammatically for a 0.5 Hz change in Frequency.  The percentage response capabilities and loading levels are defined on the basis of the Maximum Capacity of the Power Generating Module or CCGT Module or Power Park Module or HVDC Equipment.  Each Power Generating Module or and/or CCGT Module or Power Park Module (including a DC Connected Power Park Module) and/or HVDC Equipment must be capable of operating in a manner to provide Frequency response at least to the solid boundaries shown in the figure.  If the Frequency response capability falls within the solid boundaries, the Power Generating Module or CCGT Module or Power Park Module or HVDC Equipment is providing response below the minimum requirement which is not acceptable.  Nothing in this appendix is intended to prevent a Power Generating Module or CCGT Module or Power Park Module or HVDC Equipment from being designed to deliver a Frequency response in excess of the identified minimum requirement.

The Frequency response delivered for Frequency deviations of less than 0.5 Hz should be no less than a figure which is directly proportional to the minimum Frequency response requirement for a Frequency deviation of 0.5 Hz.  For example, if the Frequency deviation is 0.2 Hz, the corresponding minimum Frequency response requirement is 40% of the level shown in Figure ECC.A.3.1.  The Frequency response delivered for Frequency deviations of more than 0.5 Hz should be no less than the response delivered for a Frequency deviation of 0.5 Hz.

Each Power Generating Module and/or CCGT Module and/or Power Park Module or HVDC Equipment must be capable of providing some response, in keeping with its specific operational characteristics, when operating between 95% to 100% of Maximum Capacity as illustrated by the dotted lines in Figure ECC.A.3.1.

At the Minimum Stable Operating level, each Power Generating Module and/or CCGT Module and/or Power Park Module and/or HVDC Equipment  is required to provide high and low frequency response depending on the System Frequency conditions. Where the Frequency is high, the Active Power output is therefore expected to fall below the Minimum Stable Operating level.

The Minimum Regulating Level is the output at which a Power Generating Module and/or CCGT Module and/or Power Park Module  and/or HVDC Equipment has no High Frequency Response capability.  It may be less than, but must not be more than, 55% of the Maximum Capacity.  This implies that a Power Generating Module or CCGT Module or Power Park Module ) or HVDC Equipment  is not obliged to reduce its output to below this level unless the Frequency is at or above 50.5 Hz (cf BC3.7).

ECC.A.3.4	Testing of Frequency Response Capability

The frequency response capabilities shown diagrammatically in Figure ECC.A.3.1 are measured by taking the responses as obtained from some of the dynamic step response tests specified by The Company and carried out by Generators and HVDC System owners for compliance purposes. The injected signal is a step of 0.5Hz from zero to 0.5 Hz Frequency change, and is sustained at 0.5 Hz Frequency change thereafter, the latter as illustrated diagrammatically in figures ECC.A.3.4 and ECC.A.3.5.

In addition to provide and/or to validate the content of Ancillary Services Agreements a progressive injection of a Frequency change to the plant control system (i.e. governor and load controller) is used.  The injected signal is a ramp of 0.5Hz from zero to 0.5 Hz Frequency change over a ten second period, and is sustained at 0.5 Hz Frequency change thereafter, the latter as illustrated diagrammatically in figures ECC.A.3.2 and ECC.A.3.3.   In the case of an Embedded Medium Power Station not subject to a Bilateral Agreement or Embedded HVDC System not subject to a Bilateral Agreement, The Company may require the Network Operator within whose System the Embedded Medium Power Station or Embedded HVDC System is situated, to ensure that the Embedded Person performs the dynamic response tests reasonably required by The Company in order to demonstrate compliance within the relevant requirements in the ECC.

The Primary Response capability (P) of a Power Generating Module or a CCGT Module or Power Park Module or HVDC Equipment  is the minimum increase in Active Power output between 10 and 30 seconds after the start of the ramp injection as illustrated diagrammatically in Figure ECC.A.3.2. This increase in Active Power output should be released increasingly with time over the period 0 to 10 seconds from the time of the start of the Frequency fall as illustrated by the response from Figure ECC.A.3.2.

The Secondary Response capability (S) of a Power Generating Module or a CCGT Module or Power Park Module or HVDC Equipment is the minimum increase in Active Power output between 30 seconds and 30 minutes after the start of the ramp injection as illustrated diagrammatically in Figure ECC.A.3.2.

The High Frequency Response capability (H) of a Power Generating Module or a CCGT Module or Power Park Module or HVDC Equipment is the decrease in Active Power output provided 10 seconds after the start of the ramp injection and sustained thereafter as illustrated diagrammatically in Figure ECC.A.3.3. This reduction in Active Power output should be released increasingly with time over the period 0 to 10 seconds from the time of the start of the Frequency rise as illustrated by the response in Figure ECC.A.3.2.

ECC.A.3.5	Repeatability of Response

When a Power Generating Module or CCGT Module or Power Park Module or HVDC Equipment has responded to a significant Frequency disturbance, its response capability must be fully restored as soon as technically possible.  Full response capability should be restored no later than 20 minutes after the initial change of System Frequency arising from the Frequency disturbance.

Figure ECC.A.3.1 - Minimum Frequency Response requirement profile for a 0.5 Hz frequency change from Target Frequency

ECC.4 - APPENDIX 4 - FAULT RIDE THROUGH REQUIREMENTS

FAULT RIDE THROUGH REQUIREMENTS FOR TYPE B, TYPE C AND TYPE D POWER GENERATING MODULES (INCLUDING OFFSHORE POWER PARK MODULES WHICH ARE EITHER AC CONNECTED POWER PARK MODULES OR DC CONNECTED POWER PARK MODULES), HVDC SYSTEMS  AND OTSDUW PLANT AND APPARATUS

ECC.A.4A.1	Scope

The Fault Ride Through requirements are defined in ECC.6.3.15. This Appendix provides illustrations by way of examples only of ECC.6.3.15.1 to ECC.6.3.15.10 and further background and illustrations and is not intended to show all possible permutations.

ECC.A.4A.2	Short Circuit Faults At Supergrid Voltage On The Onshore Transmission System Up To 140ms In Duration

For short circuit faults at Supergrid Voltage on the Onshore Transmission System (which could be at an Interface Point) up to 140ms in duration, the Fault Ride Through requirement is defined in ECC.6.3.15. In summary any Power Generating Module (including a DC Connected Power Park Module) or HVDC System   is required to remain connected and stable whilst connected to a healthy circuit. Figure ECC.A.4.A.2 illustrates this principle.

Figure ECC.A.4.A.2

In Figure ECC.A.4.A.2 a solid three phase short circuit fault is applied adjacent to substation A resulting in zero voltage at the point of fault. All circuit breakers on the faulty circuit (Lines ABC) will open within 140ms resulting in Gen X tripping.  The effect of this fault, due to the low impedance of the network, will be the observation of a low voltage at each substation node across the Total System until the fault has been cleared. In this example, Gen Y and Gen Z (an Embedded Generator) would need to remain connected and stable as both are still connected to the Total System and remain connected to healthy circuits .

The criteria for assessment is based on a voltage against time curve at each Grid Entry Point or User System Entry Point. The voltage against time curve at the Grid Entry Point or User System Entry Point varies for each different type and size of Power Generating Module as detailed in ECC.6.3.15.2. – ECC.6.3.15.7.

The voltage against time curve represents the voltage profile at a Grid Entry Point or User System Entry  Point that would be obtained by plotting the voltage at that Grid Entry Point or User System Entry  Point before during and after the fault. This is not to be confused with a voltage duration curve (as defined under ECC.6.3.15.9) which represents a voltage level and associated time duration.

The post fault voltage at a Grid Entry Point or User System Entry Point is largely influenced by the topology of the network rather than the behaviour of the Power Generating Module itself. The EU Generator therefore needs to ensure each Power Generating Module remains connected and stable for a close up solid three phase short circuit fault for 140ms at the Grid Entry Point or User System Entry Point.

Two examples are shown in Figure EA.4.2(a) and Figure EA4.2(b). In Figure EA.4.2(a) the post fault profile is above the heavy black line. In this case the Power Generating Module must remain connected and stable. In Figure EA4.2(b) the post fault voltage dips below the heavy black line in which case the Power Generating Module is permitted to trip.

Figure EA.4.2(a)

Figure EA.4.2(b)

The process for demonstrating Fault Ride Through compliance against the requirements of ECC.6.3.15 is detailed in ECP.A.3.5 and ECP.A.6.7 (as applicable).

ECC.A.4A.3	Supergrid Voltage Dips On The Onshore Transmission System Greater Than 140ms In Duration

ECC.A.4A3.1	Requirements applicable to Synchronous Power Generating Modules subject to Supergrid Voltage dips on the Onshore Transmission System greater than 140ms in duration.

For balanced Supergrid Voltage dips on the Onshore Transmission System having durations greater than 140ms and up to 3 minutes, the Fault Ride Through requirement is defined in ECC.6.3.15.9.2.1(a) and Figure ECC.6.3.15.9(a) which is reproduced in this Appendix as Figure EA.4.3.1 and termed the voltage–duration profile.

This profile is not a voltage-time response curve that would be obtained by plotting the transient voltage response at a point on the Onshore Transmission System (or User System if located Onshore) to a disturbance. Rather, each point on the profile (ie the heavy black line) represents a voltage level and an associated time duration which connected Synchronous Power Generating Modules must withstand or ride through.

Figures EA.4.3.2 (a), (b) and (c) illustrate the meaning of the voltage-duration profile for voltage dips having durations greater than 140ms.

Figure EA.4.3.1

Figure EA.4.3.2  (a)

Figure EA.4.3.2  (b)

Figure EA.4.3.2  (c)

ECC.A.4A3.2	Requirements applicable to Power Park Modules or OTSDUW Plant and Apparatus subject to Supergrid Voltage dips on the Onshore Transmission System greater than 140ms in duration

For balanced Supergrid Voltage dips on the Onshore Transmission System (which could be at an Interface Point) having durations greater than 140ms and up to 3 minutes the Fault Ride Through requirement is defined in ECC.6.3.15.9.2.1(b) and Figure ECC.6.3.15.9(b) which is reproduced in this Appendix as Figure EA.4.3.3 and termed the voltage–duration profile.

This profile is not a voltage-time response curve that would be obtained by plotting the transient voltage response at a point on the Onshore Transmission System (or User System if located Onshore) to a disturbance. Rather, each point on the profile (ie the heavy black line) represents a voltage level and an associated time duration which connected Power Park Modules or OTSDUW Plant and Apparatus must withstand or ride through.

Figures EA.4.3.4 (a), (b) and (c) illustrate the meaning of the voltage-duration profile for voltage dips having durations greater than 140ms.

Figure EA.4.3.3

Figure EA.4.3.4(a)

Figure EA.4.3.4 (b)

Figure EA.4.3.4 (c)

APPENDIX E5 - TECHNICAL REQUIREMENTS

LOW FREQUENCY RELAYS FOR THE AUTOMATIC

DISCONNECTION OF SUPPLIES AT LOW FREQUENCY

ECC.A.5.1	Low Frequency Relays

ECC.A.5.1.1	The Low Frequency Relays to be used shall have a setting range of 47.0 to 50Hz and be suitable for operation from a nominal AC input of 63.5, 110 or 240V.  The following parameters specify the requirements of approved Low Frequency Relays:

| (a) Frequency settings: | 47-50Hz in steps of 0.05Hz or better, preferably 0.01Hz; |
| --- | --- |
| (b) Operating time: | Relay operating time shall not be more than 150 ms; |
| (c) Voltage lock-out: (d) Direction | Selectable within a range of 55 to 90% of nominal voltage; Tripping interlock for forward or reverse power flow capable of being set in either position or off |
| (e) Facility stages: | One or two stages of Frequency operation; |
| (f) Output contacts: | Two output contacts per stage to be capable of repetitively making and breaking for 1000 operations: |
| (g) Accuracy: | 0.01 Hz maximum error under reference environmental and system voltage conditions. 0.05 Hz maximum error at 8% of total harmonic distortion Electromagnetic Compatibility Level. |

In the case of Network Operators who are GB Code Users, the above requirements only apply to a relay (if any) installed at the EU Grid Supply Point.  Network Operators who are also GB Code Users should continue to satisfy the requirements for low frequency relays as specified in the CCs as applicable to their System.

ECC.A.5.2	Low Frequency Relay Voltage Supplies

ECC.A.5.2.1	It is essential that the voltage supply to the Low Frequency Relays shall be derived from the primary System at the supply point concerned so that the Frequency of the Low Frequency Relays input voltage is the same as that of the primary System.  This requires either:

(a)	the use of a secure supply obtained from voltage transformers directly associated with the grid transformer(s) concerned, the supply being obtained where necessary via a suitable automatic voltage selection scheme; or

(b)	the use of the substation 240V phase-to-neutral selected auxiliary supply, provided that this supply is always derived at the supply point concerned and is never derived from a standby supply Power Generating Module or from another part of the User System.

ECC.A.5.3	Scheme Requirements

ECC.A.5.3.1	The tripping facility should be engineered in accordance with the following reliability considerations:

(a)	Dependability

Failure to trip at any one particular Demand shedding point would not harm the overall operation of the scheme. However, many failures would have the effect of reducing the amount of Demand under low Frequency control.  An overall reasonable minimum requirement for the dependability of the Demand shedding scheme is 96%, i.e. the average probability of failure of each Demand shedding point should be less than 4%.  Thus the Demand under low Frequency control will not be reduced by more than 4% due to relay failure.

(b)	Outages

Low Frequency Demand shedding schemes will be engineered such that the amount of Demand under control is as specified in Table ECC.A.5.5.1a and is not reduced unacceptably during equipment outage or maintenance conditions.

ECC.A.5.3.2	The total operating time of the scheme, including circuit breakers operating time, shall where reasonably practicable, be less than 200 ms. For the avoidance of doubt, the replacement of plant installed prior to October 2009 will not be required in order to achieve lower total scheme operating times.

ECC.A.5.4	Low Frequency Relay Testing

ECC.A.5.4.1	Low Frequency Relays installed and commissioned after 1st January 2007 shall be type tested in accordance with and comply with the functional test requirements for Frequency Protection contained in Energy Networks Association Technical Specification 48-6-5 Issue 1 dated 2005 “ENA Protection Assessment Functional Test Requirements – Voltage and Frequency Protection”.

For the avoidance of doubt, Low Frequency Relays installed and commissioned before 1st January 2007 shall comply with the version of ECC.A.5.1.1 applicable at the time such Low Frequency Relays were commissioned.

ECC.A.5.4.2	Each Non-Embedded Customer shall aim to execute testing on its low frequency demand disconnection relays installed within its network and in service at least once every three years, although this may be extended to no more than every five years if considered to be required for operational purposes.

ECC.A.5.4.3	Each Network Operator and Relevant Transmission Licensee shall aim to execute testing on its low frequency demand disconnection relays installed within its network and in service at least once every three years, although this may be extended to no more than every five years if considered to be required for operational purposes.

ECC.A.5.5	Scheme Settings

ECC.A.5.5.1	Table CC.A.5.5.1a shows, for each Transmission Area, the percentage of Demand (based on Annual ACS Conditions) at the time of forecast National Electricity Transmission System peak Demand that each Network Operator whose System is connected to the Onshore Transmission System within such Transmission Area shall disconnect by Low Frequency Relays at a range of frequencies. Where a Network Operator’s System is connected to the National Electricity Transmission System in more than one Transmission Area, the settings for the Transmission Area in which the majority of the Demand is connected shall apply.

| Frequency Hz | % Demand disconnection for each Network Operator in Transmission Area |  |  |
| --- | --- | --- | --- |
|  | NGET | SPT | SHETL |
| 48.8 | 5 |  |  |
| 48.75 | 5 |  |  |
| 48.7 | 10 |  |  |
| 48.6 | 7.5 |  | 10 |
| 48.5 | 7.5 | 10 |  |
| 48.4 | 7.5 | 10 | 10 |
| 48.2 | 7.5 | 10 | 10 |
| 48.0 | 5 | 10 | 10 |
| 47.8 | 5 |  |  |
| Total % Demand | 60 | 40 | 40 |

Table ECC.A.5.5.1a

Note – the percentages in table ECC.A.5.5.1a are cumulative such that, for example, should the frequency fall to 48.6 Hz in NGET’s Transmission Area, 27.5% of the total Demand connected to the National Electricity Transmission System in NGET’s Transmission Area shall be disconnected by the action of Low Frequency Relays.

The percentage Demand at each stage shall be allocated as far as reasonably practicable. The cumulative total percentage Demand is a minimum.

ECC.A.5.5.2	In the case of a Non-Embedded Customer (who is also an EU Code User) the percentage of Demand (based on Annual ACS Conditions) at the time of forecast National Electricity Transmission System peak Demand that each Non-Embedded Customer whose System is connected to the Onshore Transmission System which shall be disconnected by Low Frequency Relays shall be in accordance with OC6.6 and the Bilateral Agreement.

ECC.A.5.6	Connection and Reconnection

ECC.A.5.6.1	As defined under OC.6.6 once automatic low Frequency Demand Disconnection has taken place, the Network Operator on whose User System it has occurred, will not reconnect until The Company instructs that Network Operator  to do so in accordance with OC6.  The same requirement equally applies to Non-Embedded Customers.

ECC.A.5.6.2	Once The Company instructs the Network Operator or Non Embedded Customer to reconnect to the National Electricity Transmission System following operation of the Low Frequency Demand Disconnection scheme it shall do so in accordance with the requirements of ECC.6.2.3.10 and OC6.6.

ECC.A.5.6.3	Network Operators or Non Embedded Customers shall be capable of being remotely disconnected from the National Electricity Transmission System when instructed by The Company. Any requirement for the automated disconnection equipment for reconfiguration of the National Electricity Transmission System in preparation for block loading and the time required for  remote disconnection shall be specified by The Company in accordance with the terms of the Bilateral Agreement.

ECC.A.5.6.4	During System Restoration, the Total System may be operated outside of Licence Standards as provided for in OC9.4.3. During such periods, on or after 31 December 2026, Transmission Licensees in accordance with the requirements of the STC, Network Operators and Non-Embedded Customers shall have the remote capability to inhibit and restore the operation of their Low Frequency Relays upon instruction from The Company as provided for in OC9.5.7(a).

APPENDIX E6 - PERFORMANCE REQUIREMENTS FOR CONTINUOUSLY ACTING AUTOMATIC EXCITATION CONTROL SYSTEMS FOR ONSHORE SYNCHRONOUS POWER GENERATING MODULES,

ECC.A.6.1	Scope

ECC.A.6.1.1 	This Appendix sets out the performance requirements of continuously acting automatic excitation control systems for Type C and Type D Onshore Synchronous Power Generating Modules that must be complied with by the User. This Appendix does not limit any site specific requirements where in The Company's reasonable opinion these facilities are necessary for system reasons.

ECC.A.6.1.2 	Where the requirements may vary the likely range of variation is given in this Appendix. It may be necessary to specify values outside this range where The Company identifies a system need, and notwithstanding anything to the contrary The Company may specify values outside of the ranges provided in this Appendix 6. The most common variations are in the on-load excitation ceiling voltage requirements and the response time required of the Exciter. Actual values will be included in the Bilateral Agreement.

ECC.A.6.1.3	Should an EU Generator anticipate making a change to the excitation control system it shall notify The Company under the Planning Code (PC.A.1.2(b) and (c)) as soon as the EU Generator anticipates making the change. The change may require a revision to the Bilateral Agreement.

ECC.A.6.2	Requirements

ECC.A.6.2.1	The Excitation System of a Type C or Type D Onshore Synchronous Power Generating Module shall include an excitation source (Exciter), and a continuously acting Automatic Voltage Regulator (AVR) and shall meet the following functional specification.  Type D Synchronous Power Generating Modules are also required to be fitted with a Power System Stabiliser in accordance with the requirements of ECC.A.6.2.5.

ECC.A.6.2.3	Steady State Voltage Control

ECC.A.6.2.3.1	An accurate steady state control of the Onshore Synchronous Power Generating Module pre-set Synchronous Generating Unit terminal voltage is required.  As a measure of the accuracy of the steady-state voltage control, the Automatic Voltage Regulator shall have static zero frequency gain, sufficient to limit the change in terminal voltage to a drop not exceeding 0.5% of rated terminal voltage, when the output of a Synchronous Generating Unit within an Onshore Synchronous Power Generating Module is gradually changed from zero to rated MVA output at rated voltage, Active Power and Frequency.

ECC.A.6.2.4	Transient Voltage Control

ECC.A.6.2.4.1	For a step change from 90% to 100% of the nominal Onshore Synchronous Generating Unit terminal voltage, with the Onshore Synchronous Generating Unit on open circuit, the Excitation System response shall have a damped oscillatory characteristic. For this characteristic, the time for the Onshore Synchronous Generating Unit terminal voltage to first reach 100% shall be less than 0.6 seconds. Also, the time to settle within 5% of the voltage change shall be less than 3 seconds.

ECC.A.6.2.4.2 	To ensure that adequate synchronising power is maintained, when the Onshore Power Generating Module is subjected to a large voltage disturbance, the Exciter whose output is varied by the Automatic Voltage Regulator shall be capable of providing its achievable upper and lower limit ceiling voltages to the Onshore Synchronous Generating Unit field in a time not exceeding that specified in the Bilateral Agreement. This will normally be not less than 50 ms and not greater than 300 ms. The achievable upper and lower limit ceiling voltages may be dependent on the voltage disturbance.

ECC.A.6.2.4.3 	The Exciter shall be capable of attaining an Excitation System On Load Positive Ceiling Voltage of not less than a value specified in the Bilateral Agreement that will be:

not less than 2 per unit (pu)

normally not greater than 3 pu

exceptionally up to 4 pu

of Rated Field Voltage when responding to a sudden drop in voltage of 10 percent or more at the Onshore Synchronous Generating Unit terminals. The Company may specify a value outside the above limits where The Company identifies a system need.

ECC.A.6.2.4.4	If a static type Exciter is employed:

(i)	the field voltage should be capable of attaining a negative ceiling level specified in the Bilateral Agreement after the removal of the step disturbance of ECC.A.6.2.4.3. The specified value will be 80% of the value specified in ECC.A.6.2.4.3. The Company may specify a value outside the above limits where The Company identifies a system need.

(ii)	the Exciter must be capable of maintaining free firing when the Onshore Synchronous Generating Unit terminal voltage is depressed to a level which may be between 20% to 30% of rated terminal voltage

(iii)	the Exciter shall be capable of attaining a positive ceiling voltage not less than 80% of the Excitation System On Load Positive Ceiling Voltage upon recovery of the Onshore Synchronous Generating Unit terminal voltage to 80% of rated terminal voltage following fault clearance. The Company may specify a value outside the above limits where The Company identifies a system need.

(iv)	the requirement to provide a separate power source for the Exciter will be specified if The Company identifies a Transmission System need.

ECC.A.6.2.5	Power Oscillations Damping Control

ECC.A.6.2.5.1 	To allow  Type D Onshore Power Generating Modules to maintain second and subsequent swing stability and also to ensure an adequate level of low frequency electrical damping power, the Automatic Voltage Regulator of each Onshore Synchronous Generating Unit within each Type D  Onshore Synchronous Power Generating Module shall include a Power System Stabiliser as a means of supplementary control.

ECC.A.6.2.5.2 	Whatever supplementary control signal is employed, it shall be of the type which operates into the Automatic Voltage Regulator to cause the field voltage to act in a manner which results in the damping power being improved while maintaining adequate synchronising power.

ECC.A.6.2.5.3 	The arrangements for the supplementary control signal shall ensure that the Power System Stabiliser output signal relates only to changes in the supplementary control signal and not the steady state level of the signal.  For example, if generator electrical power output is chosen as a supplementary control signal then the Power System Stabiliser output should relate only to changes in the Synchronous Generating Unit electrical power output and not the steady state level of power output.  Additionally the Power System Stabiliser should not react to mechanical power changes in isolation for example during rapid changes in steady state load or when providing frequency response.

ECC.A.6.2.5.4	The output signal from the Power System Stabiliser shall be limited to not more than ±10% of the Onshore Synchronous Generating Unit terminal voltage signal at the Automatic Voltage Regulator input. The gain of the Power System Stabiliser shall be such that an increase in the gain by a factor of 3 shall not cause instability.

ECC.A.6.2.5.5	The Power System Stabiliser shall include elements that limit the bandwidth of the output signal.  The bandwidth limiting must ensure that the highest frequency of response cannot excite torsional oscillations on other plant connected to the network.  A bandwidth of 0-5Hz would be judged to be acceptable for this application.

ECC.A.6.2.5.6 	The EU Generator in respect of its Type D Synchronous Power Generating Modules will agree Power System Stabiliser settings with The Company prior to the on-load commissioning detailed in BC2.11.2(d). To allow assessment of the performance before on-load commissioning the EU Generator will provide to The Company a report covering the areas specified in ECP.A.3.2.1.

ECC.A.6.2.5.7	The Power System Stabiliser must be active within the Excitation System at all times when Synchronised including when the Under Excitation Limiter or Over Excitation Limiter are active.  When operating at low load when Synchronising or De-Synchronising an Onshore Synchronous Generating Unit, within a Type D Synchronous Power Generating Module, the Power System Stabiliser may be out of service.

ECC.A.6.2.5.8	Where a Power System Stabiliser is fitted to a Pumped Storage Unit within a Type D Synchronous Power Generating Module it must function when the Pumped Storage Unit is in both generating and pumping modes. In addition, where a Power System Stabiliser is fitted to an Electricity Storage Unit within a Type D Synchronous Electricity Storage Module, it must function when the Synchronous Electricity Storage Unit is in both importing and exporting modes of operation.

ECC.A.6.2.6	Overall Excitation System Control Characteristics

ECC.A.6.2.6.1	The overall Excitation System shall include elements that limit the bandwidth of the output signal. The bandwidth limiting must be consistent with the speed of response requirements and ensure that the highest frequency of response cannot excite torsional oscillations on other plant connected to the network.  A bandwidth of 0-5 Hz will be judged to be acceptable for this application.

ECC.A.6.2.6.2	The response of the Automatic Voltage Regulator combined with the Power System Stabiliser shall be demonstrated by injecting similar step signal disturbances into the Automatic Voltage Regulator reference as detailed in ECPA.5.2 and ECPA.5.4. The Automatic Voltage Regulator shall include a facility to allow step injections into the Automatic Voltage Regulator voltage reference,  with the Onshore Type D Power Generating Module operating at points specified by The Company (up to rated MVA output).  	The damping shall be judged to be adequate if the corresponding Active Power response to the disturbances decays within two cycles of oscillation.

ECC.A.6.2.6.3	A facility to inject a band limited random noise signal into the Automatic Voltage Regulator voltage reference shall be provided for demonstrating the frequency domain response of the Power System Stabiliser. The tuning of the Power System Stabiliser shall be judged to be adequate if the corresponding Active Power response shows improved damping with the Power System Stabiliser in combination with the Automatic Voltage Regulator compared with the Automatic Voltage Regulator alone over the frequency range 0.3Hz – 2Hz.

ECC.A.6.2.7	Under-Excitation Limiters

ECC.A.6.2.7.1 	The security of the power system shall also be safeguarded by means of MVAr Under Excitation Limiters fitted to the Synchronous Power Generating Module  Excitation System. The Under Excitation Limiter shall prevent the Automatic Voltage Regulator reducing the Synchronous Generating Unit excitation to a level which would endanger synchronous stability. The Under Excitation Limiter shall operate when the excitation system is providing automatic control. The Under Excitation Limiter shall respond to changes in the Active Power (MW) the Reactive Power (MVAr) and to the square of the Synchronous Generating Unit voltage in such a direction that an increase in voltage will permit an increase in leading MVAr. The characteristic of the Under Excitation Limiter shall be substantially linear from no-load to the maximum Active Power output of the Onshore Power Generating Module at any setting and shall be readily adjustable.

ECC.A.6.2.7.2 	The performance of the Under Excitation Limiter shall be independent of the rate of change of the Onshore Synchronous Power Generating Module load and shall be demonstrated by testing as detailed in ECP.A.5.5. The resulting maximum overshoot in response to a step injection which operates the Under Excitation Limiter shall not exceed 4% of the Onshore Synchronous Generating Unit rated MVA. The operating point of the Onshore Synchronous Generating Unit shall be returned to a steady state value at the limit line and the final settling time shall not be greater than 5 seconds.  When the step change in Automatic Voltage Regulator reference voltage is reversed, the field voltage should begin to respond without any delay and should not be held down by the Under Excitation Limiter.  Operation into or out of the preset limit levels shall ensure that any resultant oscillations are damped so that the disturbance is within 0.5% of the Onshore Synchronous Generating Unit MVA rating within a period of 5 seconds.

ECC.A.6.2.7.3 	The EU Generator shall also make provision to prevent the reduction of the Onshore Synchronous Generating Unit excitation to a level which would endanger synchronous stability when the Excitation System is under manual control.

ECC.A.6.2.8	Over-Excitation and Stator Current Limiters

ECC.A.6.2.8.1 	The settings of the Over-Excitation Limiter and stator current limiter, shall ensure that the Onshore Synchronous Generating Unit excitation is not limited to less than the maximum value that can be achieved whilst ensuring the Onshore Synchronous Generating Unit is operating within its design limits. If the Onshore Synchronous Generating Unit excitation is reduced following a period of operation at a high level, the rate of reduction shall not exceed that required to remain within any time dependent operating characteristics of the Onshore Synchronous Power Generating Module.

ECC.A.6.2.8.2	The performance of the Over-Excitation Limiter, shall be demonstrated by testing as described in ECP.A.5.6. Any operation beyond the Over-Excitation Limit shall be controlled by the Over-Excitation Limiter or stator current limiter without the operation of any Protection that could trip the Onshore Synchronous Power Generating Module.

ECC.A.6.2.8.3 	The EU Generator shall also make provision to prevent any over-excitation restriction of the Onshore Synchronous Generating Unit when the Excitation System is under manual control, other than that necessary to ensure the Onshore Power Generating Module is operating within its design limits.

APPENDIX E7 - PERFORMANCE REQUIREMENTS FOR CONTINUOUSLY ACTING AUTOMATIC VOLTAGE CONTROL SYSTEMS FOR AC CONNECTED ONSHORE POWER PARK MODULES AND OTSDUW PLANT AND APPARATUS AT THE INTERFACE POINT HVDC SYSTEMS AND REMOTE END HVDC CONVERTER STATIONS

ECC.A.7.1	Scope

ECC.A.7.1.1	This Appendix sets out the performance requirements of continuously acting automatic voltage control systems for Onshore Power Park Modules, Onshore HVDC Converters   Remote End HVDC Converter Stations and OTSDUW Plant and Apparatus at the Interface Point that must be complied with by the User. This Appendix does not limit any site specific requirements where in The Company's reasonable opinion these facilities are necessary for system reasons.  The control performance requirements applicable to Configuration 2 AC Connected Offshore Power Park Modules and Configuration 2 DC Connected Power Park Modules are defined in Appendix E8.

ECC.A.7.1.2	Proposals by EU Generators or HVDC System Owners to make a change to the voltage control systems are required to be notified to The Company under the Planning Code (PC.A.1.2(b) and (c)) as soon as the Generator or HVDC System Owner anticipates making the change. The change may require a revision to the Bilateral Agreement.

ECC.A.7.1.3	In the case of a Remote End HVDC Converter at a HVDC Converter Station, the control performance requirements shall be specified in the Bilateral Agreement.  These requirements shall be consistent with those specified in ECC.6.3.2.4.  In the case where the Remote End HVDC Converter  is required to ensure the zero transfer of Reactive Power at the HVDC Interface Point then the requirements shall be specified in the Bilateral Agreement which shall be consistent with those requirements specified in ECC.A.8 .  In the case where a wider reactive capability has been specified in ECC.6.3.2.4, then the requirements consistent with those specified in ECC.A.7.2 shall apply with any variations being agreed between the User and The Company.

ECC.A.7.2	Requirements

ECC.A.7.2.1	The Company requires that the continuously acting automatic voltage control system for the Onshore Power Park Module, Onshore HVDC Converter  or OTSDUW Plant and Apparatus shall meet the following functional performance specification. If a Network Operator has confirmed to The Company that its network to which an Embedded Onshore Power Park Module or Onshore HVDC Converter or OTSDUW Plant and Apparatus is connected is restricted such that the full reactive range under the steady state voltage control requirements (ECC.A.7.2.2) cannot be utilised, The Company may specify alternative limits to the steady state voltage control range that reflect these restrictions. Where the Network Operator subsequently notifies The Company that such restriction has been removed, The Company may propose a Modification to the Bilateral Agreement (in accordance with the CUSC contract) to remove the alternative limits such that the continuously acting automatic voltage control system meets the following functional performance specification. All other requirements of the voltage control system will remain as in this Appendix.

ECC.A.7.2.2	Steady State Voltage Control

ECC.A.7.2.2.1	The Onshore Power Park Module, Onshore HVDC Converter or OTSDUW Plant and Apparatus shall provide continuous steady state control of the voltage at the  Onshore Grid Entry Point (or Onshore User System Entry Point if Embedded) (or the Interface Point in the case of OTSDUW Plant and Apparatus ) with a Setpoint Voltage and Slope characteristic as illustrated in Figure ECC.A.7.2.2a.

Figure ECC.A.7.2.2a

ECC.A.7.2.2.2	The continuously acting automatic control system shall be capable of operating to a Setpoint Voltage between 95% and 105% with a resolution of 0.25% of the nominal voltage. For the avoidance of doubt values of 95%, 95.25%, 95.5% … may be specified, but not intermediate values. The initial Setpoint Voltage will be 100%. The tolerance within which this Setpoint Voltage shall be achieved is specified in BC2.A.2.6. For the avoidance of doubt, with a tolerance of 0.25% and a Setpoint Voltage of 100%, the achieved value shall be between 99.75% and 100.25%. The Company may request the EU Generator or HVDC System Owner to implement an alternative Setpoint Voltage within the range of 95% to 105%. For Embedded Generators and Embedded HVDC System Owners the Setpoint Voltage will be discussed between The Company and the relevant Network Operator and will be specified to ensure consistency with ECC.6.3.4.

ECC.A.7.2.2.3	The Slope characteristic of the continuously acting automatic control system shall be adjustable over the range 2% to 7% (with a resolution of 0.5%). For the avoidance of doubt values of 2%, 2.5%, 3% may be specified, but not intermediate values. The initial Slope setting will be 4%. The tolerance within which this Slope shall be achieved is specified in BC2.A.2.6. For the avoidance of doubt, with a tolerance of 0.5% and a Slope setting of 4%, the achieved value shall be between 3.5% and 4.5%. The Company may request the EU Generator or HVDC System Owner to implement an alternative slope setting within the range of 2% to 7%. For Embedded Generators and Onshore Embedded HVDC Converter Station Owners the Slope setting will be discussed between The Company and the relevant Network Operator and will be specified to ensure consistency with ECC.6.3.4.

Figure ECC.A.7.2.2b

Figure ECC.A.7.2.2c

ECC.A.7.2.2.4	Figure ECC.A.7.2.2b shows the required envelope of operation for -, OTSDUW Plant and Apparatus, Onshore Power Park Modules and Onshore HVDC Converters except for those Embedded at 33kV and below or directly connected to the National Electricity Transmission System at 33kV and below. Figure ECC.A.7.2.2c shows the required envelope of operation for Onshore Power Park Modules Embedded at 33kV and below, or directly connected to the National Electricity Transmission System at 33kV and below. The enclosed area within points ABCDEFGH is the required capability range within which the Slope and Setpoint Voltage can be changed.

ECC.A.7.2.2.5	Should the operating point of the, OTSDUW Plant and Apparatus or Onshore Power Park Module, or Onshore HVDC Converter  deviate so that it is no longer a point on the operating characteristic (figure ECC.A.7.2.2a) defined by the target Setpoint Voltage and Slope, the continuously acting automatic voltage control system shall act progressively to return the value to a point on the required characteristic within 5 seconds.

ECC.A.7.2.2.6	Should the Reactive Power output of the OTSDUW Plant and Apparatus or Onshore Power Park Module or Onshore HVDC Converter  reach its maximum lagging limit at a Onshore Grid Entry Point voltage (or Onshore User System Entry Point voltage if Embedded (or Interface Point in the case of OTSDUW Plant and Apparatus )  above 95%, the OTSDUW Plant and Apparatus or Onshore Power Park Module or HVDC System  shall maintain maximum lagging Reactive Power output for voltage reductions down to 95%. This requirement is indicated by the line EF in figures ECC.A.7.2.2b and ECC.A.7.2.2c as applicable. Should the Reactive Power output of the OTSDUW Plant and Apparatus or Onshore Power Park Module, or Onshore HVDC Converter reach its maximum leading limit at a Onshore Grid Entry  Point voltage  (or Onshore User System Entry Point voltage if Embedded or Interface Point in the case of  OTSDUW Plant and Apparatus) below 105%, the OTSDUW Plant and Apparatus or Onshore Power Park Module, or  Onshore HVDC Converter   shall maintain maximum leading Reactive Power output for voltage increases up to 105%. This requirement is indicated by the line AB in figures ECC.A.7.2.2b and ECC.A.7.2.2c as applicable.

ECC.A.7.2.2.7	For Onshore Grid Entry  Point voltages (or Onshore User System Entry Point voltages if Embedded or Interface Point voltages) below 95%, the lagging Reactive Power capability of the OTSDUW Plant and Apparatus or Onshore Power Park Module or Onshore HVDC Converters   should be that which results from the supply of maximum lagging reactive current whilst ensuring the current remains within design operating limits. An example of the capability is shown by the line DE in figures ECC.A.7.2.2b and ECC.A.7.2.2c. For Onshore Grid Entry Point voltages (or User System Entry Point voltages if Embedded or Interface Point voltages) above 105%, the leading Reactive Power capability of the OTSDUW Plant and Apparatus or Onshore Power Park Module or  Onshore HVDC System Converter should be that which results from the supply of maximum leading reactive current whilst ensuring the current remains within design operating limits. An example of the capability is shown by the line AH in figures ECC.A.7.2.2b and ECC.A.7.2.2c as applicable. Should the Reactive Power output of the OTSDUW Plant and Apparatus or Onshore Power Park Module or Onshore HVDC Converter  reach its maximum lagging limit at an Onshore Grid Entry Connection Point voltage (or Onshore User System Entry Point voltage if Embedded or Interface Point in the case of OTSDUW Plant and Apparatus) below 95%, the Onshore Power Park Module, Onshore HVDC Converter  shall maintain maximum lagging reactive current output for further voltage decreases. Should the Reactive Power output of the OTSDUW Plant and Apparatus or Onshore Power Park Module or Onshore HVDC Converter  reach its maximum leading limit at a Onshore Grid Entry  Point voltage  (or User System Entry Point voltage if Embedded or Interface Point voltage in the case of an OTSDUW Plant and Apparatus) above 105%, the OTSDUW Plant and Apparatus or Onshore Power Park Module or Onshore HVDC Converter shall maintain maximum leading reactive current output for further voltage increases.

ECC.A.7.2.2.8	All OTSDUW Plant and Apparatus must be capable of enabling EU Code Users undertaking OTSDUW to comply with an instruction received from The Company relating to a variation of the Setpoint Voltage at the Interface Point within 2 minutes of such instruction being received.

ECC.A.7.2.2.9	For OTSDUW Plant and Apparatus connected to a Network Operator’s System where the Network Operator has confirmed to The Company that its System is restricted in accordance with ECC.A.7.2.1, clause ECC.A.7.2.2.8 will not apply unless The Company can reasonably demonstrate that the magnitude of the available change in Reactive Power has a significant effect on voltage levels on the Onshore National Electricity Transmission System.

ECC.A.7.2.3	Transient Voltage Control

ECC.A.7.2.3.1	For an on-load step change in Onshore Grid Entry Point or Onshore User System Entry Point voltage, or in the case of OTSDUW Plant and Apparatus an on-load step change in Transmission Interface Point voltage, the continuously acting automatic control system shall respond according to the following minimum criteria:

(i)	the Reactive Power output response of the, OTSDUW Plant and Apparatus or Onshore Power Park Module or Onshore HVDC Converter  shall commence within 0.2 seconds of the application of the step. It shall progress linearly although variations from a linear characteristic shall be acceptable provided that the MVAr seconds delivered at any time up to 1 second are at least those that would result from the response shown in figure ECC.A.7.2.3.1a.

(ii)	the response shall be such that 90% of the change in the Reactive Power output of the, OTSDUW Plant and Apparatus or Onshore Power Park Module, or Onshore HVDC Converter  will be achieved within

    - 2 seconds, where the step is sufficiently large to require a change in the steady state Reactive Power output from its maximum leading value to its maximum lagging value or vice versa and

    - 1 second where the step is sufficiently large to require a change in the steady state Reactive Power output from zero to its maximum leading value or maximum lagging value as required by ECC.6.3.2 (or, if appropriate ECC.A.7.2.2.6 or ECC.A.7.2.2.7);

(iii)	the magnitude of the Reactive Power output response produced within 1 second shall vary linearly in proportion to the magnitude of the step change.

(iv)	within  5 seconds from achieving 90% of the response as defined in ECC.A.7.2.3.1 (ii), the peak to peak magnitude of any oscillations shall be less than 5% of the change in steady state maximum Reactive Power.

(v)	following the transient response, the conditions of ECC.A.7.2.2 apply.

MVArs

Seconds

Required response at 1 second

0.2

1

Figure ECC.A.7.2.3.1a

ECC.A.7.2.3.2 	OTSDUW Plant and Apparatus or Onshore Power Park Modules or Onshore HVDC Converters  shall be capable of

##### (a)	changing its Reactive Power output from its maximum lagging value to its maximum leading value, or vice versa, then reverting back to the initial level of Reactive Power output once every 15 seconds for at least 5 times within any 5 minute period; and

##### (b)	changing its Reactive Power output from zero to its maximum leading value then reverting back to zero Reactive Power output at least 25 times within any 24 hour period and from zero to its maximum lagging value then reverting back to zero Reactive Power output at least 25 times within any 24 hour period.  Any subsequent restriction on reactive capability shall be notified to The Company in accordance with BC2.5.3.2, and BC2.6.1.

##### In all cases, the response shall be in accordance to ECC.A.7.2.3.1 where the change in Reactive Power output is in response to an on-load step change in Onshore Grid Entry Point or Onshore User System Entry Point voltage, or in the case of OTSDUW Plant and Apparatus an on-load step change in Transmission Interface Point voltage.

ECC.A.7.2.4	Power Oscillation Damping

ECC.A.7.2.4.1	The requirement for the continuously acting voltage control system to be fitted with a Power System Stabiliser (PSS) shall be specified if, in The Company’s view, this is required for system reasons.  However if a Power System Stabiliser is included in the voltage control system its settings and performance shall be agreed with The Company and commissioned in accordance with BC2.11.2.  To allow assessment of the performance before on-load commissioning the Generator will provide to The Company a report covering the areas specified in ECP.A.3.2.2.

ECC.A.7.2.5	Overall Voltage Control System Characteristics

ECC.A.7.2.5.1	The continuously acting automatic voltage control system is required to respond to minor variations, steps, gradual changes or major variations in Onshore Grid Entry Point voltage (or Onshore User System Entry Point voltage if Embedded or Interface Point voltage in the case of OTSDUW Plant and Apparatus).

ECC.A.7.2.5.2	The overall voltage control system shall include elements that limit the bandwidth of the output signal. The bandwidth limiting must be consistent with the speed of response requirements and ensure that the highest frequency of response cannot excite torsional oscillations on other plant connected to the network.  A bandwidth of 0-5Hz would be judged to be acceptable for this application.  All other control systems employed within the OTSDUW Plant and Apparatus or Onshore Power Park Module or Onshore HVDC Converter should also meet this requirement

ECC.A.7.2.5.3	The response of the voltage control system (including the Power System Stabiliser if employed) shall be demonstrated by testing in accordance with ECP.A.6.

ECC.A.7.3	Reactive Power Control

ECC.A.7.3.1		As defined in ECC.6.3.8.3.4, Reactive Power control mode of operation is not required in respect of Onshore Power Park Modules or OTSDUW Plant and Apparatus or Onshore HVDC Converters  unless otherwise specified by The Company in coordination with the relevant Network Operator.  However where there is a requirement for Reactive Power control mode of operation, the following requirements shall apply.

ECC.A.7.3.2	The Onshore Power Park Module or OTSDUW Plant and Apparatus or Onshore HVDC Converter  shall be capable of setting the Reactive Power setpoint anywhere in the Reactive Power range as specified in ECC.6.3.2.4 with setting steps no greater than 5 MVAr or 5% (whichever is smaller) of full Reactive Power, controlling the reactive power at the Grid Entry Point or User System Entry Point if Embedded to an accuracy within plus or minus 5MVAr or plus or minus 5% (whichever is smaller) of the full Reactive Power.

ECC.A.7.3.3		Any additional requirements for Reactive Power control mode of operation shall be specified by The Company in coordination with the relevant Network Operator..

ECC.A.7.4	Power Factor Control

ECC.A.7.4.1	As defined in ECC.6.3.8.4.3, Power Factor control mode of operation is not required in respect of Onshore Power Park Modules or OTSDUW Plant and Apparatus or Onshore HVDC Converters   unless otherwise specified by The Company in coordination with the relevant Network Operator.   However where there is a requirement for Power Factor control mode of operation, the following requirements shall apply.

ECC.A.7.4.2	The Onshore Power Park Module or OTSDUW Plant and Apparatus or Onshore HVDC Converter  shall be capable of controlling the Power Factor at the Grid Entry Point or User System Entry Point (if Embedded)  within the required Reactive Power range as specified in ECC.6.3.2.2.1 and ECC.6.3.2.4 to a specified target Power Factor.  The Company shall specify the target Power Factor value (which shall be achieved within 0.01 of the set Power Factor), its tolerance and the period of time to achieve the target Power Factor following a sudden change of Active Power output.  The tolerance of the target Power Factor shall be expressed through the tolerance of its corresponding Reactive Power.  This Reactive Power tolerance shall be expressed by either an absolute value or by a percentage of the maximum Reactive Power of the Onshore Power Park Module or OTSDUW Plant and Apparatus or Onshore HVDC  Converter. The details of these requirements being pursuant to the terms of the Bilateral Agreement.

ECC.A.7.4.3		Any additional requirements for Power Factor control mode of operation shall be specified by The Company in coordination with the relevant Network Operator.

APPENDIX E8 - PERFORMANCE REQUIREMENTS FOR CONTINUOUSLY ACTING AUTOMATIC VOLTAGE CONTROL SYSTEMS FOR CONFIGURATION 2 AC CONNECTED OFFSHORE POWER PARK MODULES AND CONFIGURATION 2 DC CONNECTED POWER PARK MODULES

ECC.A.8.1	Scope

ECC.A.8.1.1	This Appendix sets out the performance requirements of continuously acting automatic voltage control systems for Configuration 2 AC Connected Offshore Power Park Modules and Configuration 2 DC Connected Power Park Modules that must be complied with by the EU Code User. This Appendix does not limit any site specific requirements that may be specified where in The Company's reasonable opinion these facilities are necessary for system reasons.

ECC.A.8.1.2	These requirements also apply to Configuration 2 DC Connected Power Park Modules.  In the case of a Configuration 1 DC Connected Power Park Module the technical performance requirements shall be specified by The Company.  Where the EU Generator in respect of a DC Connected Power Park Module has agreed to a wider reactive capability range as defined under ECC.6.3.2.5 and ECC.6.2.3.6 then the requirements that apply will be specified by The Company and which shall reflect the performance requirements detailed in ECC.A.8.2 below but with different parameters such as droop and Setpoint Voltage.

ECC.A.8.1.3	Proposals by EU Generators to make a change to the voltage control systems are required to be notified to The Company under the Planning Code (PC.A.1.2(b) and (c)) as soon as the Generator anticipates making the change. The change may require a revision to the Bilateral Agreement.

ECC.A.8.2	Requirements

ECC.A.8.2.1	The Company requires that the continuously acting automatic voltage control system for the Configuration 2 AC connected Offshore Power Park Module and Configuration 2 DC Connected Power Park Module shall meet the following functional performance specification.

ECC.A.8.2.2	Steady State Voltage Control

ECC.A.8.2.2.1	The Configuration 2 AC connected Offshore Power Park Module and Configuration 2 DC Connected Power Park Module shall provide continuous steady state control of the voltage at the Offshore Connection Point with a Setpoint Voltage and Slope characteristic as illustrated in Figure ECC.A.8.2.2a.

Figure ECC.A.8.2.2a

ECC.A.8.2.2.2	The continuously acting automatic control system shall be capable of operating to a Setpoint Voltage between 95% and 105% with a resolution of 0.25% of the nominal voltage. For the avoidance of doubt values of 95%, 95.25%, 95.5% … may be specified, but not intermediate values. The initial Setpoint Voltage will be 100%. The tolerance within which this Setpoint Voltage shall be achieved is specified in BC2.A.2.6. For the avoidance of doubt, with a tolerance of 0.25% and a Setpoint Voltage of 100%, the achieved value shall be between 99.75% and 100.25%. The Company may request the EU Generator to implement an alternative Setpoint Voltage within the range of 95% to 105%.

ECC.A.8.2.2.3	The Slope characteristic of the continuously acting automatic control system shall be adjustable over the range 2% to 7% (with a resolution of 0.5%). For the avoidance of doubt values of 2%, 2.5%, 3% may be specified, but not intermediate values. The initial Slope setting will be 4%. The tolerance within which this Slope shall be achieved is specified in BC2.A.2.6. For the avoidance of doubt, with a tolerance of 0.5% and a Slope setting of 4%, the achieved value shall be between 3.5% and 4.5%. The Company may request the EU Generator to implement an alternative slope setting within the range of 2% to 7%.

Figure ECC.A.8.2.2b

ECC.A.8.2.2.4	Figure ECC.A.8.2.2b shows the required envelope of operation for Configuration 2 AC connected Offshore Power Park Module and Configuration 2 DC Connected Power Park Module. The enclosed area within points ABCDEFGH is the required capability range within which the Slope and Setpoint Voltage can be changed.

ECC.A.8.2.2.5	Should the operating point of the Configuration 2 AC connected Offshore Power Park or Configuration 2 DC Connected Power Park Module deviate so that it is no longer a point on the operating characteristic (Figure ECC.A.8.2.2a) defined by the target Setpoint Voltage and Slope, the continuously acting automatic voltage control system shall act progressively to return the value to a point on the required characteristic within 5 seconds.

ECC.A.8.2.2.6	Should the Reactive Power output of the Configuration 2 AC connected Offshore Power Park Module or Configuration 2 DC Connected Power Park Module reach its maximum lagging limit at an Offshore Grid Entry Point or Offshore User System Entry Point or HVDC Interface Point voltage above 95%, the Configuration 2 AC connected Offshore Power Park Module or Configuration 2 DC Connected Power Park Module shall maintain maximum lagging Reactive Power output for voltage reductions down to 95%. This requirement is indicated by the line EF in figure ECC.A.8.2.2b. Should the Reactive Power output of the Configuration 2 AC connected Offshore Power Park Module or Configuration 2 DC Connected Power Park Module reach its maximum leading limit at the Offshore Grid Entry  Point or Offshore User System Entry Point or HVDC Interface Point  voltage below 105%, the Configuration 2 AC connected Offshore Power Park Module or Configuration 2 DC Connected Power Park Module shall maintain maximum leading Reactive Power output for voltage increases up to 105%. This requirement is indicated by the line AB in figures ECC.A.8.2.2b.

ECC.A.8.2.2.7	For Offshore Grid Entry Point or User System Entry Point or HVDC Interface Point voltages below 95%, the lagging Reactive Power capability of the Configuration 2 AC connected Offshore Power Park Module or Configuration 2 DC Connected Power Park Module should be that which results from the supply of maximum lagging reactive current whilst ensuring the current remains within design operating limits. An example of the capability is shown by the line DE in figures ECC.A.8.2.2b. For Offshore Grid Entry Point or Offshore User System Entry Point voltages or HVDC Interface Point voltages above 105%, the leading Reactive Power capability of the Configuration 2 AC connected Offshore Power Park Module or Configuration 2 DC Connected Power Park Module should be that which results from the supply of maximum leading reactive current whilst ensuring the current remains within design operating limits. An example of the capability is shown by the line AH in figures ECC.A.8.2.2b. Should the Reactive Power output of the Configuration 2 AC connected Offshore Power Park Module or Configuration 2 DC Connected Power Park Module reach its maximum lagging limit at an Offshore Grid Entry Point or Offshore User System Entry voltage or HVDC Interface Point voltage below 95%, the Configuration 2 AC connected Offshore Power Park Module or Configuration 2 DC Connected Power Park Module shall maintain maximum lagging reactive current output for further voltage decreases. Should the Reactive Power output of the Configuration 2 AC connected Offshore Power Park Module or Configuration 2 DC Connected Power Park Module reach its maximum leading limit at an Offshore Grid Entry Point or Offshore User System Entry voltage  or HVDC Interface Point voltage above 105%, the Configuration 2 AC connected Offshore Power Park Module or Configuration 2 DC Connected Power Park Module shall maintain maximum leading reactive current output for further voltage increases.

ECC.A.8.2.3	Transient Voltage Control

ECC.A.8.2.3.1	For an on-load step change in Offshore Grid Entry Point or Offshore User System Entry Point voltage or HVDC Interface Point voltage, the continuously acting automatic control system shall respond according to the following minimum criteria:

(i)	the Reactive Power output response of the Configuration 2 AC connected Offshore Power Park Module or Configuration 2 DC Connected Power Park Module shall commence within 0.2 seconds of the application of the step. It shall progress linearly although variations from a linear characteristic shall be acceptable provided that the MVAr seconds delivered at any time up to 1 second are at least those that would result from the response shown in figure ECC.A.8.2.3.1a.

(ii)	the response shall be such that 90% of the change in the Reactive Power output of the Configuration 2 AC connected Offshore Power Park Module or Configuration 2 DC Connected Power Park Module will be achieved within

    - 2 seconds, where the step is sufficiently large to require a change in the steady state Reactive Power output from its maximum leading value to its maximum lagging value or vice versa and

    - 1 second where the step is sufficiently large to require a change in the steady state Reactive Power output from zero to its maximum leading value or maximum lagging value as required by ECC.6.3.2 (or, if appropriate ECC.A.8.2.2.6 or ECC.A.8.2.2.7);

(iii)	the magnitude of the Reactive Power output response produced within 1 second shall vary linearly in proportion to the magnitude of the step change.

(iv)	within 5 seconds from achieving 90% of the response as defined in ECC.A.8.2.3.1 (ii), the peak to peak magnitude of any oscillations shall be less than 5% of the change in steady state maximum Reactive Power.

(v)	following the transient response, the conditions of ECC.A.8.2.2 apply.

MVArs

Seconds

Required response at 1 second

0.2

1

Figure ECC.A.8.2.3.1a

ECC.A.8.2.3.2 	Configuration 2 AC connected Offshore Power Park Module or Configuration 2 DC Connected Power Park Module shall be capable of

##### (a)	changing their Reactive Power output from maximum lagging value to maximum leading value, or vice versa, then reverting back to the initial level of Reactive Power output once every 15 seconds for at least 5 times within any 5 minute period; and

##### (b)	changing Reactive Power output from zero to maximum leading value then reverting back to zero Reactive Power output at least 25 times within any 24 hour period and from zero to its maximum lagging value then reverting back to zero Reactive Power output at least 25 times within any 24 hour period. Any subsequent restriction on reactive capability shall be notified to The Company in accordance with BC2.5.3.2, and BC2.6.1.

##### In all cases, the response shall be in accordance to ECC.A.8.2.3.1 where the change in Reactive Power output is in response to an on-load step change in Offshore Grid Entry Point or Offshore User System Entry Point voltage or HVDC Interface Point voltage.

ECC.A.8.2.4	Power Oscillation Damping

ECC.A.8.2.4.1	The requirement for the continuously acting voltage control system to be fitted with a Power System Stabiliser (PSS) shall be specified if, in  The Company’s view, this is required for system reasons.  However if a Power System Stabiliser is included in the voltage control system its settings and performance shall be agreed with The Company and commissioned in accordance with BC2.11.2.  To allow assessment of the performance before on-load commissioning the Generator or HVDC System Owner will provide to The Company a report covering the areas specified in ECP.A.3.2.2.

ECC.A.8.2.5	Overall Voltage Control System Characteristics

ECC.A.8.2.5.1	The continuously acting automatic voltage control system is required to respond to minor variations, steps, gradual changes or major variations in Offshore Grid Entry Point or Offshore User System Entry Point or HVDC Interface Point voltage.

ECC.A.8.2.5.2	The overall voltage control system shall include elements that limit the bandwidth of the output signal. The bandwidth limiting must be consistent with the speed of response requirements and ensure that the highest frequency of response cannot excite torsional oscillations on other plant connected to the network.  A bandwidth of 0-5Hz would be judged to be acceptable for this application.  All other control systems employed within the Configuration 2 AC connected Offshore Power Park Module or Configuration 2 DC Connected Power Park Module should also meet this requirement

ECC.A.8.2.5.3	The response of the voltage control system (including the Power System Stabiliser if employed) shall be demonstrated by testing in accordance with ECP.A.6.

ECC.A.8.3	Reactive Power Control

ECC.A.8.3.1		Reactive Power control mode of operation is not required in respect of Configuration 2 AC connected Offshore Power Park Modules or Configuration 2 DC Connected Power Park Modules unless otherwise specified by The Company.  However where there is a requirement for Reactive Power control mode of operation, the following requirements shall apply.

ECC.A.8.3.2	Configuration 2 AC connected Offshore Power Park Modules or Configuration 2 DC Connected Power Park Modules shall be capable of setting the Reactive Power setpoint anywhere in the Reactive Power range as specified in ECC.6.3.2.8.2 with setting steps no greater than 5 MVAr or 5% (whichever is smaller) of full Reactive Power, controlling the Reactive Power at the Offshore Grid Entry Point or Offshore User System Entry Point or HVDC Interface Point to an accuracy within plus or minus 5MVAr or plus or minus 5% (whichever is smaller) of the full Reactive Power.

ECC.A.8.3.3		Any additional requirements for Reactive Power control mode of operation shall be specified by The Company.

ECC.A.8.4	Power Factor Control

ECC.A.8.4.1	Power Factor control mode of operation is not required in respect of Configuration 2 AC connected Offshore Power Park Modules or Configuration 2 DC Connected Power Park Modules unless otherwise specified by The Company.  However where there is a requirement for Power Factor control mode of operation, the following requirements shall apply.

ECC.A.8.4.2	Configuration 2 AC connected Offshore Power Park Modules or Configuration 2 DC Connected Power Park Modules shall be capable of controlling the Power Factor at the Offshore Grid Entry Point or Offshore User System Entry Point or HVDC Interface Point within the required Reactive Power range as specified in ECC.6.3.2.8.2 with a target Power Factor.  The Company shall specify the target Power Factor (which shall be achieved to within 0.01 of the set Power Factor), its tolerance and the period of time to achieve the target Power Factor following a sudden change of Active Power output.  The tolerance of the target Power Factor shall be expressed through the tolerance of its corresponding Reactive Power.  This Reactive Power tolerance shall be expressed by either an absolute value or by a percentage of the maximum Reactive Power of the Configuration 2 AC connected Offshore Power Park Module or Configuration 2 DC Connected Power Park Module.  The details of these requirements being specified by The Company.

ECC.A.8.4.3		Any additional requirements for Power Factor control mode of operation shall be specified by The Company.

< END OF EUROPEAN CONNECTION CONDITIONS >

Details of circuits traversing the Connection Site are only needed from the date which is the earlier of the date when the Site Responsibility Schedule is first updated and 15th October 2004. In Scotland or Offshore, from a date to be agreed between The Company and the Relevant Transmission Licensee.