## Version
Date | Version | Details
2024-10-15 | 1 | This file only contains the indicative reporting associated with draft data for GC0151 for October 2024. This file will be updated in November 2024 to reflect the full data set.
2024-11-15 | 2 | This file only contains the indicative reporting associated with data for GC0151 for October 2024. This file is updated in November 2024 to reflect the full data set.
2024-12-06 | 3 | This file contains the reporting associated with data for GC0105 & GC0151 for October 2024.

## Notes
Subject | Notes
RoCoF | RoCoF=(frequency_500ms - frequency_0ms)/500ms RoCoF is calculated using 500ms sliding window. Note that smaller losses will have less accurate ROCOF calculations The RoCoF figure in this report is from external service
System Inertia | Monitoring which transmission-connected generators are running and adding an estimate of inertia from embedded generation and demand
Data 'N/A' | N/A: data not applicable or potentially unreliable. For example, there maybe events when the loss of infeed or exfeed is not instantaneous (over long time period), the calculated RoCoF may not be indicative. For some events, during a disturbance the data may potentially be unreliable. NGESO will apply engineering judgement to determine whether the derived/calculated data is suitable for sharing.
MW trip/loss of all generation/ interconnection related to the incident | Positive sign: indicates a loss of infeed, generator or importing interconnector. Negative sign: indicates a loss of outfeed, exporting interconnector.

## Transmission Faults (GC0151)
Location | Network Operator | Date Time | Voltage Trace (Refer to sheet) | Notes
Fort Augustus - Quoich - Broadford (FQ/QQ/QB1) 132kV circuit | SHETL | 2024-10-04 04:49
Sloy - Dunoon - Whistlefield - Windyhill 1 (SWE1/E1/GL1)132kV circuit | SHETL | 2024-10-08 10:14
Hutton-Middleton-Penwortham 400kV circuit | NGET | 2024-10-11 02:26
Glenlee - Glenluce - Newton Stewart 1 132kV & Glenluce GT1 circuit | SPT | 2024-10-12 14:30
Berkswell - Coventry 1 275kV Circuit | NGET | 2024-10-25 14:03

## System Incidents (GC0105)
|  |  | Date and time of the incident | System frequency trace (1-second interval) for the incident | System frequency immediately before the incident | System frequency immediately after the incident | Maximum/Minimum rate of change of frequency (RoCoF) of the incident | System inertia at the time of the incident | Where known, MW trip/loss of all generation/ interconnection related to the incident |  | Where known, MW trip/loss of all Embedded Generation(EG) related to the incident | Where known, MW trip/loss of all DNO demand related to the incident; | Transmission fault associated with the incident; | Any transient voltage dip (loss % and duration) at the local substation associated with the incident | Any other data to gain a clearer understanding of the incident and its potential implications
Reference | Name | Notes | Date Time | System Frequency (Refer to sheet) | Pre-Event Frequency (Hz) | Post-Event Frequency (Hz) | RoCoF (Hz/s) | System Inertia (GVAs) | Generation/Interconnection (MW) |  | EG (MW) | Demand (MW) | Transmission fault | Voltage Dip | Additional data
20241002-1 | Trip of TSREP-1 |  | 2024-10-02 14:06 | 20241002-1 | 49.918 | 49.837 | -0.03463 | 186 | TSREP-1 | 269.3
20241008-1 | Trip of North Sea Link | Importing from Norway to GB | 2024-10-08 08:48 | 20241008-1 | 49.896 | 49.614 | -0.20806 | 190 | NSL | 1396.81
20241010-1 | Trip of HEYM-11 |  | 2024-10-10 10:15 | 20241010-1 | 50.121 | 50.036 | -0.022278 | 180 | HEYM-11 | 515.66
20241013-1 | Trip of PEMB-11 |  | 2024-10-13 13:03 | 20241013-1 | 50.101 | 49.955 | -0.064835 | 223 | PEMB-11 | 434.02
20241017-1 | Trip of ROCK-1 |  | 2024-10-17 18:11 | 20241017-1 | 50.023 | 49.928 | -0.024242 | 259 | ROCK-1 | 292.56
20241020-1 | Trip of GRAI-6 |  | 2024-10-20 05:44 | 20241020-1 | 49.937 | 49.817 | -0.023362 | 122 | GRAI-6 | 347.88
20241021-1 | Trip of SUTB-1 |  | 2024-10-21 14:15 | 20241021-1 | 49.98 | 49.888 | -0.033506 | 188 | SUTB-1 | 367.45
20241028-1 | Trip of HUMR-1 |  | 2024-10-28 06:00 | 20241028-1 | 50.0871 | 49.974 | -0.043912 | 154 | HUMR-1 | 286.5
20241028-2 | Trip of Viking Link | Importing from Denmark to GB | 2024-10-28 08:19 | 20241028-2 | 50.068 | 49.767 | -0.14942 | 186 | VKL | 1183
20241030-1 | Trip of KEAD-2 |  | 2024-10-30 17:31 | 20241030-1 | 50.058 | 49.77 | -0.05168 | 274 | KEAD-2 | 836.1

## 20241002-1
In GMT
Date | Time | Freq
2024-10-02 | 13:05 | 49.983 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-10-02 | 13:05 | 49.986 | 222 | BRITNED | 676.211
2024-10-02 | 13:05 | 49.989 | 268 | WBURB-2 | 428.156
2024-10-02 | 13:05 | 49.987 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-10-02 | 13:05 | 49.988 |  | Viking Link | -648.9
2024-10-02 | 13:05 | 49.986 |  | Viking Link | 1398.96
2024-10-02 | 13:05 | 49.986 | 209 | DRAXX-3 | 626.95
2024-10-02 | 13:05 | 49.986 | 154 | CDCL-1 | 391.57
2024-10-02 | 13:05 | 49.985 | 268 | ROCK-1 | 468.495
2024-10-02 | 13:05 | 49.985 | 148 | IFA Bipole1 | 945.473
2024-10-02 | 13:05 | 49.982 | 132 | IFA Bipole1 | 999.1
2024-10-02 | 13:05 | 49.98 | 141 | IFA Bipole2 | 1000
2024-10-02 | 13:05 | 49.978 | 135 | IFA Bipole1 | 996.75
2024-10-02 | 13:05 | 49.977 |  | Viking Link | -780.3
2024-10-02 | 13:05 | 49.975
2024-10-02 | 13:05 | 49.977
2024-10-02 | 13:05 | 49.975
2024-10-02 | 13:05 | 49.975
2024-10-02 | 13:05 | 49.976
2024-10-02 | 13:05 | 49.974 | 130 | HEYM12 | 271.908
2024-10-02 | 13:05 | 49.975 | 228 | HUMR-1 | 303.75
2024-10-02 | 13:05 | 49.975
2024-10-02 | 13:05 | 49.975
2024-10-02 | 13:05 | 49.975
2024-10-02 | 13:05 | 49.98
2024-10-02 | 13:05 | 49.981
2024-10-02 | 13:05 | 49.982
2024-10-02 | 13:05 | 49.982
2024-10-02 | 13:05 | 49.98
2024-10-02 | 13:05 | 49.978
2024-10-02 | 13:05 | 49.978 | 211 | CDCL-1 | 291.5
2024-10-02 | 13:06 | 49.975 | 199 | STAY-2 | 413.125
2024-10-02 | 13:06 | 49.975 | 173 | CDCL-1 | 397.375
2024-10-02 | 13:06 | 49.975 | 248 | SEAB-2 | 361.25
2024-10-02 | 13:06 | 49.976 | 255 | FRANCE | 995.65
2024-10-02 | 13:06 | 49.977 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-10-02 | 13:06 | 49.975
2024-10-02 | 13:06 | 49.975
2024-10-02 | 13:06 | 49.973
2024-10-02 | 13:06 | 49.974
2024-10-02 | 13:06 | 49.976
2024-10-02 | 13:06 | 49.978
2024-10-02 | 13:06 | 49.98
2024-10-02 | 13:06 | 49.982
2024-10-02 | 13:06 | 49.984
2024-10-02 | 13:06 | 49.984
2024-10-02 | 13:06 | 49.985
2024-10-02 | 13:06 | 49.986
2024-10-02 | 13:06 | 49.986
2024-10-02 | 13:06 | 49.985
2024-10-02 | 13:06 | 49.982
2024-10-02 | 13:06 | 49.98
2024-10-02 | 13:06 | 49.977
2024-10-02 | 13:06 | 49.974
2024-10-02 | 13:06 | 49.967
2024-10-02 | 13:06 | 49.959
2024-10-02 | 13:06 | 49.953
2024-10-02 | 13:06 | 49.948
2024-10-02 | 13:06 | 49.945
2024-10-02 | 13:06 | 49.936
2024-10-02 | 13:06 | 49.928
2024-10-02 | 13:06 | 49.921
2024-10-02 | 13:06 | 49.919
2024-10-02 | 13:06 | 49.919
2024-10-02 | 13:06 | 49.918
2024-10-02 | 13:06 | 49.92
2024-10-02 | 13:06 | 49.919
2024-10-02 | 13:06 | 49.917
2024-10-02 | 13:06 | 49.918
2024-10-02 | 13:06 | 49.916
2024-10-02 | 13:06 | 49.915
2024-10-02 | 13:06 | 49.912
2024-10-02 | 13:06 | 49.882
2024-10-02 | 13:06 | 49.86
2024-10-02 | 13:06 | 49.849
2024-10-02 | 13:06 | 49.842
2024-10-02 | 13:06 | 49.838
2024-10-02 | 13:06 | 49.837
2024-10-02 | 13:06 | 49.838
2024-10-02 | 13:06 | 49.839
2024-10-02 | 13:06 | 49.841
2024-10-02 | 13:06 | 49.843
2024-10-02 | 13:06 | 49.845
2024-10-02 | 13:06 | 49.846
2024-10-02 | 13:06 | 49.847
2024-10-02 | 13:06 | 49.85
2024-10-02 | 13:06 | 49.852
2024-10-02 | 13:06 | 49.854
2024-10-02 | 13:06 | 49.852
2024-10-02 | 13:06 | 49.85
2024-10-02 | 13:07 | 49.852
2024-10-02 | 13:07 | 49.85
2024-10-02 | 13:07 | 49.849
2024-10-02 | 13:07 | 49.844
2024-10-02 | 13:07 | 49.844
2024-10-02 | 13:07 | 49.842
2024-10-02 | 13:07 | 49.838
2024-10-02 | 13:07 | 49.839
2024-10-02 | 13:07 | 49.838
2024-10-02 | 13:07 | 49.837
2024-10-02 | 13:07 | 49.841
2024-10-02 | 13:07 | 49.838
2024-10-02 | 13:07 | 49.839
2024-10-02 | 13:07 | 49.837
2024-10-02 | 13:07 | 49.841
2024-10-02 | 13:07 | 49.842
2024-10-02 | 13:07 | 49.842
2024-10-02 | 13:07 | 49.844
2024-10-02 | 13:07 | 49.844
2024-10-02 | 13:07 | 49.844
2024-10-02 | 13:07 | 49.844
2024-10-02 | 13:07 | 49.843
2024-10-02 | 13:07 | 49.842
2024-10-02 | 13:07 | 49.841
2024-10-02 | 13:07 | 49.841
2024-10-02 | 13:07 | 49.843
2024-10-02 | 13:07 | 49.843
2024-10-02 | 13:07 | 49.841
2024-10-02 | 13:07 | 49.842
2024-10-02 | 13:07 | 49.843
2024-10-02 | 13:07 | 49.842
2024-10-02 | 13:07 | 49.841
2024-10-02 | 13:07 | 49.838
2024-10-02 | 13:07 | 49.836
2024-10-02 | 13:07 | 49.836
2024-10-02 | 13:07 | 49.838
2024-10-02 | 13:07 | 49.839
2024-10-02 | 13:07 | 49.838
2024-10-02 | 13:07 | 49.835
2024-10-02 | 13:07 | 49.834
2024-10-02 | 13:07 | 49.834
2024-10-02 | 13:07 | 49.833
2024-10-02 | 13:07 | 49.835
2024-10-02 | 13:07 | 49.836
2024-10-02 | 13:07 | 49.836
2024-10-02 | 13:07 | 49.839
2024-10-02 | 13:07 | 49.84
2024-10-02 | 13:07 | 49.844
2024-10-02 | 13:07 | 49.843
2024-10-02 | 13:07 | 49.845
2024-10-02 | 13:07 | 49.848
2024-10-02 | 13:07 | 49.845
2024-10-02 | 13:07 | 49.843
2024-10-02 | 13:07 | 49.844
2024-10-02 | 13:07 | 49.842
2024-10-02 | 13:07 | 49.84
2024-10-02 | 13:07 | 49.839
2024-10-02 | 13:07 | 49.839
2024-10-02 | 13:07 | 49.838
2024-10-02 | 13:07 | 49.839
2024-10-02 | 13:08 | 49.843
2024-10-02 | 13:08 | 49.842
2024-10-02 | 13:08 | 49.844
2024-10-02 | 13:08 | 49.844
2024-10-02 | 13:08 | 49.843
2024-10-02 | 13:08 | 49.845
2024-10-02 | 13:08 | 49.847
2024-10-02 | 13:08 | 49.849
2024-10-02 | 13:08 | 49.853
2024-10-02 | 13:08 | 49.856
2024-10-02 | 13:08 | 49.86
2024-10-02 | 13:08 | 49.862
2024-10-02 | 13:08 | 49.864
2024-10-02 | 13:08 | 49.865
2024-10-02 | 13:08 | 49.867
2024-10-02 | 13:08 | 49.866
2024-10-02 | 13:08 | 49.867
2024-10-02 | 13:08 | 49.868
2024-10-02 | 13:08 | 49.871
2024-10-02 | 13:08 | 49.869
2024-10-02 | 13:08 | 49.868
2024-10-02 | 13:08 | 49.868
2024-10-02 | 13:08 | 49.868
2024-10-02 | 13:08 | 49.869
2024-10-02 | 13:08 | 49.871
2024-10-02 | 13:08 | 49.869
2024-10-02 | 13:08 | 49.867
2024-10-02 | 13:08 | 49.867
2024-10-02 | 13:08 | 49.868
2024-10-02 | 13:08 | 49.867
2024-10-02 | 13:08 | 49.868
2024-10-02 | 13:08 | 49.869
2024-10-02 | 13:08 | 49.868
2024-10-02 | 13:08 | 49.869
2024-10-02 | 13:08 | 49.869
2024-10-02 | 13:08 | 49.87
2024-10-02 | 13:08 | 49.872
2024-10-02 | 13:08 | 49.876
2024-10-02 | 13:08 | 49.875
2024-10-02 | 13:08 | 49.877
2024-10-02 | 13:08 | 49.876
2024-10-02 | 13:08 | 49.873
2024-10-02 | 13:08 | 49.872
2024-10-02 | 13:08 | 49.871
2024-10-02 | 13:08 | 49.873
2024-10-02 | 13:08 | 49.871
2024-10-02 | 13:08 | 49.872
2024-10-02 | 13:08 | 49.868
2024-10-02 | 13:08 | 49.868
2024-10-02 | 13:08 | 49.868
2024-10-02 | 13:08 | 49.869
2024-10-02 | 13:08 | 49.864
2024-10-02 | 13:08 | 49.864
2024-10-02 | 13:08 | 49.862
2024-10-02 | 13:08 | 49.863
2024-10-02 | 13:08 | 49.866
2024-10-02 | 13:08 | 49.864
2024-10-02 | 13:08 | 49.869
2024-10-02 | 13:08 | 49.866
2024-10-02 | 13:08 | 49.867
2024-10-02 | 13:08 | 49.868
2024-10-02 | 13:09 | 49.873
2024-10-02 | 13:09 | 49.875
2024-10-02 | 13:09 | 49.881
2024-10-02 | 13:09 | 49.88
2024-10-02 | 13:09 | 49.881
2024-10-02 | 13:09 | 49.883
2024-10-02 | 13:09 | 49.882
2024-10-02 | 13:09 | 49.879
2024-10-02 | 13:09 | 49.878
2024-10-02 | 13:09 | 49.879
2024-10-02 | 13:09 | 49.876
2024-10-02 | 13:09 | 49.877
2024-10-02 | 13:09 | 49.883
2024-10-02 | 13:09 | 49.881
2024-10-02 | 13:09 | 49.884
2024-10-02 | 13:09 | 49.881
2024-10-02 | 13:09 | 49.881
2024-10-02 | 13:09 | 49.877
2024-10-02 | 13:09 | 49.878
2024-10-02 | 13:09 | 49.877
2024-10-02 | 13:09 | 49.878
2024-10-02 | 13:09 | 49.872
2024-10-02 | 13:09 | 49.873
2024-10-02 | 13:09 | 49.868
2024-10-02 | 13:09 | 49.87
2024-10-02 | 13:09 | 49.865
2024-10-02 | 13:09 | 49.865
2024-10-02 | 13:09 | 49.864
2024-10-02 | 13:09 | 49.864
2024-10-02 | 13:09 | 49.864
2024-10-02 | 13:09 | 49.86
2024-10-02 | 13:09 | 49.862
2024-10-02 | 13:09 | 49.859
2024-10-02 | 13:09 | 49.858
2024-10-02 | 13:09 | 49.862
2024-10-02 | 13:09 | 49.863
2024-10-02 | 13:09 | 49.863
2024-10-02 | 13:09 | 49.864
2024-10-02 | 13:09 | 49.865
2024-10-02 | 13:09 | 49.868
2024-10-02 | 13:09 | 49.868
2024-10-02 | 13:09 | 49.871
2024-10-02 | 13:09 | 49.873
2024-10-02 | 13:09 | 49.877
2024-10-02 | 13:09 | 49.877
2024-10-02 | 13:09 | 49.879
2024-10-02 | 13:09 | 49.879
2024-10-02 | 13:09 | 49.88
2024-10-02 | 13:09 | 49.878
2024-10-02 | 13:09 | 49.878
2024-10-02 | 13:09 | 49.881
2024-10-02 | 13:09 | 49.876
2024-10-02 | 13:09 | 49.876
2024-10-02 | 13:09 | 49.877
2024-10-02 | 13:09 | 49.879
2024-10-02 | 13:09 | 49.879
2024-10-02 | 13:09 | 49.877
2024-10-02 | 13:09 | 49.875
2024-10-02 | 13:09 | 49.875
2024-10-02 | 13:10 | 49.874
2024-10-02 | 13:10 | 49.877
2024-10-02 | 13:10 | 49.875
2024-10-02 | 13:10 | 49.879
2024-10-02 | 13:10 | 49.877
2024-10-02 | 13:10 | 49.877
2024-10-02 | 13:10 | 49.876
2024-10-02 | 13:10 | 49.88
2024-10-02 | 13:10 | 49.88
2024-10-02 | 13:10 | 49.879
2024-10-02 | 13:10 | 49.881
2024-10-02 | 13:10 | 49.88
2024-10-02 | 13:10 | 49.88
2024-10-02 | 13:10 | 49.879
2024-10-02 | 13:10 | 49.88
2024-10-02 | 13:10 | 49.882
2024-10-02 | 13:10 | 49.884
2024-10-02 | 13:10 | 49.883
2024-10-02 | 13:10 | 49.881
2024-10-02 | 13:10 | 49.883
2024-10-02 | 13:10 | 49.88
2024-10-02 | 13:10 | 49.879
2024-10-02 | 13:10 | 49.879
2024-10-02 | 13:10 | 49.878
2024-10-02 | 13:10 | 49.874
2024-10-02 | 13:10 | 49.874
2024-10-02 | 13:10 | 49.875
2024-10-02 | 13:10 | 49.876
2024-10-02 | 13:10 | 49.877
2024-10-02 | 13:10 | 49.879
2024-10-02 | 13:10 | 49.878
2024-10-02 | 13:10 | 49.876
2024-10-02 | 13:10 | 49.874
2024-10-02 | 13:10 | 49.869
2024-10-02 | 13:10 | 49.869
2024-10-02 | 13:10 | 49.872
2024-10-02 | 13:10 | 49.87
2024-10-02 | 13:10 | 49.867
2024-10-02 | 13:10 | 49.864
2024-10-02 | 13:10 | 49.862
2024-10-02 | 13:10 | 49.865
2024-10-02 | 13:10 | 49.862
2024-10-02 | 13:10 | 49.862
2024-10-02 | 13:10 | 49.864
2024-10-02 | 13:10 | 49.864
2024-10-02 | 13:10 | 49.861
2024-10-02 | 13:10 | 49.868
2024-10-02 | 13:10 | 49.866
2024-10-02 | 13:10 | 49.867
2024-10-02 | 13:10 | 49.87
2024-10-02 | 13:10 | 49.873
2024-10-02 | 13:10 | 49.877
2024-10-02 | 13:10 | 49.88
2024-10-02 | 13:10 | 49.88
2024-10-02 | 13:10 | 49.881
2024-10-02 | 13:10 | 49.881
2024-10-02 | 13:10 | 49.882
2024-10-02 | 13:10 | 49.885
2024-10-02 | 13:10 | 49.885
2024-10-02 | 13:10 | 49.884
2024-10-02 | 13:10 | 49.885
2024-10-02 | 13:11 | 49.888
2024-10-02 | 13:11 | 49.888
2024-10-02 | 13:11 | 49.889
2024-10-02 | 13:11 | 49.89
2024-10-02 | 13:11 | 49.891
2024-10-02 | 13:11 | 49.89
2024-10-02 | 13:11 | 49.889
2024-10-02 | 13:11 | 49.892
2024-10-02 | 13:11 | 49.894
2024-10-02 | 13:11 | 49.896
2024-10-02 | 13:11 | 49.898
2024-10-02 | 13:11 | 49.899
2024-10-02 | 13:11 | 49.898
2024-10-02 | 13:11 | 49.896
2024-10-02 | 13:11 | 49.896
2024-10-02 | 13:11 | 49.893
2024-10-02 | 13:11 | 49.89
2024-10-02 | 13:11 | 49.893
2024-10-02 | 13:11 | 49.891
2024-10-02 | 13:11 | 49.889
2024-10-02 | 13:11 | 49.891
2024-10-02 | 13:11 | 49.891
2024-10-02 | 13:11 | 49.894
2024-10-02 | 13:11 | 49.897
2024-10-02 | 13:11 | 49.897
2024-10-02 | 13:11 | 49.894
2024-10-02 | 13:11 | 49.892
2024-10-02 | 13:11 | 49.894
2024-10-02 | 13:11 | 49.893
2024-10-02 | 13:11 | 49.895
2024-10-02 | 13:11 | 49.892
2024-10-02 | 13:11 | 49.891
2024-10-02 | 13:11 | 49.895
2024-10-02 | 13:11 | 49.894
2024-10-02 | 13:11 | 49.894
2024-10-02 | 13:11 | 49.893
2024-10-02 | 13:11 | 49.893
2024-10-02 | 13:11 | 49.892
2024-10-02 | 13:11 | 49.891
2024-10-02 | 13:11 | 49.893
2024-10-02 | 13:11 | 49.892
2024-10-02 | 13:11 | 49.89
2024-10-02 | 13:11 | 49.892
2024-10-02 | 13:11 | 49.892
2024-10-02 | 13:11 | 49.891
2024-10-02 | 13:11 | 49.886
2024-10-02 | 13:11 | 49.884
2024-10-02 | 13:11 | 49.882
2024-10-02 | 13:11 | 49.879
2024-10-02 | 13:11 | 49.875
2024-10-02 | 13:11 | 49.873
2024-10-02 | 13:11 | 49.873
2024-10-02 | 13:11 | 49.871
2024-10-02 | 13:11 | 49.871
2024-10-02 | 13:11 | 49.871
2024-10-02 | 13:11 | 49.871
2024-10-02 | 13:11 | 49.873
2024-10-02 | 13:11 | 49.872
2024-10-02 | 13:11 | 49.871
2024-10-02 | 13:12 | 49.873
2024-10-02 | 13:12 | 49.874
2024-10-02 | 13:12 | 49.873
2024-10-02 | 13:12 | 49.874
2024-10-02 | 13:12 | 49.877
2024-10-02 | 13:12 | 49.879
2024-10-02 | 13:12 | 49.879
2024-10-02 | 13:12 | 49.879
2024-10-02 | 13:12 | 49.88
2024-10-02 | 13:12 | 49.879
2024-10-02 | 13:12 | 49.882
2024-10-02 | 13:12 | 49.878
2024-10-02 | 13:12 | 49.877
2024-10-02 | 13:12 | 49.875
2024-10-02 | 13:12 | 49.878
2024-10-02 | 13:12 | 49.879
2024-10-02 | 13:12 | 49.878
2024-10-02 | 13:12 | 49.876
2024-10-02 | 13:12 | 49.875
2024-10-02 | 13:12 | 49.875
2024-10-02 | 13:12 | 49.875
2024-10-02 | 13:12 | 49.875
2024-10-02 | 13:12 | 49.875
2024-10-02 | 13:12 | 49.875
2024-10-02 | 13:12 | 49.876
2024-10-02 | 13:12 | 49.877
2024-10-02 | 13:12 | 49.878
2024-10-02 | 13:12 | 49.88
2024-10-02 | 13:12 | 49.879
2024-10-02 | 13:12 | 49.879
2024-10-02 | 13:12 | 49.877
2024-10-02 | 13:12 | 49.879
2024-10-02 | 13:12 | 49.876
2024-10-02 | 13:12 | 49.877
2024-10-02 | 13:12 | 49.878
2024-10-02 | 13:12 | 49.875
2024-10-02 | 13:12 | 49.877
2024-10-02 | 13:12 | 49.879
2024-10-02 | 13:12 | 49.882
2024-10-02 | 13:12 | 49.882
2024-10-02 | 13:12 | 49.882
2024-10-02 | 13:12 | 49.885
2024-10-02 | 13:12 | 49.885
2024-10-02 | 13:12 | 49.886
2024-10-02 | 13:12 | 49.888
2024-10-02 | 13:12 | 49.887
2024-10-02 | 13:12 | 49.887
2024-10-02 | 13:12 | 49.889
2024-10-02 | 13:12 | 49.89
2024-10-02 | 13:12 | 49.889
2024-10-02 | 13:12 | 49.884
2024-10-02 | 13:12 | 49.882
2024-10-02 | 13:12 | 49.883
2024-10-02 | 13:12 | 49.883
2024-10-02 | 13:12 | 49.884
2024-10-02 | 13:12 | 49.885
2024-10-02 | 13:12 | 49.885
2024-10-02 | 13:12 | 49.889
2024-10-02 | 13:12 | 49.89
2024-10-02 | 13:12 | 49.89
2024-10-02 | 13:12 | 49.891
2024-10-02 | 13:13 | 49.892
2024-10-02 | 13:13 | 49.892
2024-10-02 | 13:13 | 49.892
2024-10-02 | 13:13 | 49.893
2024-10-02 | 13:13 | 49.894
2024-10-02 | 13:13 | 49.891
2024-10-02 | 13:13 | 49.894
2024-10-02 | 13:13 | 49.896
2024-10-02 | 13:13 | 49.895
2024-10-02 | 13:13 | 49.897
2024-10-02 | 13:13 | 49.9
2024-10-02 | 13:13 | 49.9
2024-10-02 | 13:13 | 49.9
2024-10-02 | 13:13 | 49.903
2024-10-02 | 13:13 | 49.904
2024-10-02 | 13:13 | 49.903
2024-10-02 | 13:13 | 49.905
2024-10-02 | 13:13 | 49.906
2024-10-02 | 13:13 | 49.908
2024-10-02 | 13:13 | 49.909
2024-10-02 | 13:13 | 49.911
2024-10-02 | 13:13 | 49.913
2024-10-02 | 13:13 | 49.917
2024-10-02 | 13:13 | 49.92
2024-10-02 | 13:13 | 49.92
2024-10-02 | 13:13 | 49.919
2024-10-02 | 13:13 | 49.918
2024-10-02 | 13:13 | 49.917
2024-10-02 | 13:13 | 49.919
2024-10-02 | 13:13 | 49.918
2024-10-02 | 13:13 | 49.918
2024-10-02 | 13:13 | 49.915
2024-10-02 | 13:13 | 49.913
2024-10-02 | 13:13 | 49.911
2024-10-02 | 13:13 | 49.91
2024-10-02 | 13:13 | 49.909
2024-10-02 | 13:13 | 49.91
2024-10-02 | 13:13 | 49.91
2024-10-02 | 13:13 | 49.907
2024-10-02 | 13:13 | 49.908
2024-10-02 | 13:13 | 49.911
2024-10-02 | 13:13 | 49.913
2024-10-02 | 13:13 | 49.91
2024-10-02 | 13:13 | 49.909
2024-10-02 | 13:13 | 49.906
2024-10-02 | 13:13 | 49.904
2024-10-02 | 13:13 | 49.904
2024-10-02 | 13:13 | 49.901
2024-10-02 | 13:13 | 49.902
2024-10-02 | 13:13 | 49.9
2024-10-02 | 13:13 | 49.903
2024-10-02 | 13:13 | 49.9
2024-10-02 | 13:13 | 49.903
2024-10-02 | 13:13 | 49.904
2024-10-02 | 13:13 | 49.905
2024-10-02 | 13:13 | 49.909
2024-10-02 | 13:13 | 49.913
2024-10-02 | 13:13 | 49.913
2024-10-02 | 13:13 | 49.913
2024-10-02 | 13:14 | 49.914
2024-10-02 | 13:14 | 49.916
2024-10-02 | 13:14 | 49.914
2024-10-02 | 13:14 | 49.915
2024-10-02 | 13:14 | 49.914
2024-10-02 | 13:14 | 49.914
2024-10-02 | 13:14 | 49.912
2024-10-02 | 13:14 | 49.914
2024-10-02 | 13:14 | 49.913
2024-10-02 | 13:14 | 49.913
2024-10-02 | 13:14 | 49.914
2024-10-02 | 13:14 | 49.914
2024-10-02 | 13:14 | 49.914
2024-10-02 | 13:14 | 49.915
2024-10-02 | 13:14 | 49.913
2024-10-02 | 13:14 | 49.911
2024-10-02 | 13:14 | 49.91
2024-10-02 | 13:14 | 49.91
2024-10-02 | 13:14 | 49.912
2024-10-02 | 13:14 | 49.91
2024-10-02 | 13:14 | 49.911
2024-10-02 | 13:14 | 49.913
2024-10-02 | 13:14 | 49.912
2024-10-02 | 13:14 | 49.909
2024-10-02 | 13:14 | 49.907
2024-10-02 | 13:14 | 49.906
2024-10-02 | 13:14 | 49.907
2024-10-02 | 13:14 | 49.91
2024-10-02 | 13:14 | 49.911
2024-10-02 | 13:14 | 49.91
2024-10-02 | 13:14 | 49.911
2024-10-02 | 13:14 | 49.908
2024-10-02 | 13:14 | 49.905
2024-10-02 | 13:14 | 49.905
2024-10-02 | 13:14 | 49.901
2024-10-02 | 13:14 | 49.901
2024-10-02 | 13:14 | 49.901
2024-10-02 | 13:14 | 49.903
2024-10-02 | 13:14 | 49.903
2024-10-02 | 13:14 | 49.904
2024-10-02 | 13:14 | 49.901
2024-10-02 | 13:14 | 49.902
2024-10-02 | 13:14 | 49.904
2024-10-02 | 13:14 | 49.905
2024-10-02 | 13:14 | 49.906
2024-10-02 | 13:14 | 49.908
2024-10-02 | 13:14 | 49.912
2024-10-02 | 13:14 | 49.913
2024-10-02 | 13:14 | 49.913
2024-10-02 | 13:14 | 49.915
2024-10-02 | 13:14 | 49.915
2024-10-02 | 13:14 | 49.916
2024-10-02 | 13:14 | 49.916
2024-10-02 | 13:14 | 49.917
2024-10-02 | 13:14 | 49.917
2024-10-02 | 13:14 | 49.917
2024-10-02 | 13:14 | 49.916
2024-10-02 | 13:14 | 49.915
2024-10-02 | 13:14 | 49.913
2024-10-02 | 13:14 | 49.913
2024-10-02 | 13:14 | 49.91
2024-10-02 | 13:15 | 49.91
2024-10-02 | 13:15 | 49.91
2024-10-02 | 13:15 | 49.911
2024-10-02 | 13:15 | 49.911
2024-10-02 | 13:15 | 49.911
2024-10-02 | 13:15 | 49.916
2024-10-02 | 13:15 | 49.92
2024-10-02 | 13:15 | 49.922
2024-10-02 | 13:15 | 49.921
2024-10-02 | 13:15 | 49.924
2024-10-02 | 13:15 | 49.926
2024-10-02 | 13:15 | 49.927
2024-10-02 | 13:15 | 49.926
2024-10-02 | 13:15 | 49.927
2024-10-02 | 13:15 | 49.926
2024-10-02 | 13:15 | 49.926
2024-10-02 | 13:15 | 49.927
2024-10-02 | 13:15 | 49.929
2024-10-02 | 13:15 | 49.93
2024-10-02 | 13:15 | 49.93
2024-10-02 | 13:15 | 49.931
2024-10-02 | 13:15 | 49.934
2024-10-02 | 13:15 | 49.933
2024-10-02 | 13:15 | 49.933
2024-10-02 | 13:15 | 49.937
2024-10-02 | 13:15 | 49.937
2024-10-02 | 13:15 | 49.938
2024-10-02 | 13:15 | 49.938
2024-10-02 | 13:15 | 49.935
2024-10-02 | 13:15 | 49.934
2024-10-02 | 13:15 | 49.928
2024-10-02 | 13:15 | 49.924
2024-10-02 | 13:15 | 49.924
2024-10-02 | 13:15 | 49.919
2024-10-02 | 13:15 | 49.92
2024-10-02 | 13:15 | 49.921
2024-10-02 | 13:15 | 49.923
2024-10-02 | 13:15 | 49.923
2024-10-02 | 13:15 | 49.921
2024-10-02 | 13:15 | 49.923
2024-10-02 | 13:15 | 49.924
2024-10-02 | 13:15 | 49.924
2024-10-02 | 13:15 | 49.925
2024-10-02 | 13:15 | 49.926
2024-10-02 | 13:15 | 49.926
2024-10-02 | 13:15 | 49.927
2024-10-02 | 13:15 | 49.927
2024-10-02 | 13:15 | 49.929
2024-10-02 | 13:15 | 49.928
2024-10-02 | 13:15 | 49.929
2024-10-02 | 13:15 | 49.929
2024-10-02 | 13:15 | 49.927
2024-10-02 | 13:15 | 49.924
2024-10-02 | 13:15 | 49.923
2024-10-02 | 13:15 | 49.92
2024-10-02 | 13:15 | 49.919
2024-10-02 | 13:15 | 49.917
2024-10-02 | 13:15 | 49.914
2024-10-02 | 13:15 | 49.91
2024-10-02 | 13:16 | 49.908
2024-10-02 | 13:16 | 49.906
2024-10-02 | 13:16 | 49.903
2024-10-02 | 13:16 | 49.903
2024-10-02 | 13:16 | 49.899
2024-10-02 | 13:16 | 49.898
2024-10-02 | 13:16 | 49.897
2024-10-02 | 13:16 | 49.895
2024-10-02 | 13:16 | 49.896
2024-10-02 | 13:16 | 49.899
2024-10-02 | 13:16 | 49.902
2024-10-02 | 13:16 | 49.901
2024-10-02 | 13:16 | 49.903
2024-10-02 | 13:16 | 49.9
2024-10-02 | 13:16 | 49.897
2024-10-02 | 13:16 | 49.894
2024-10-02 | 13:16 | 49.892
2024-10-02 | 13:16 | 49.896
2024-10-02 | 13:16 | 49.901
2024-10-02 | 13:16 | 49.907
2024-10-02 | 13:16 | 49.909
2024-10-02 | 13:16 | 49.914
2024-10-02 | 13:16 | 49.918
2024-10-02 | 13:16 | 49.92
2024-10-02 | 13:16 | 49.92
2024-10-02 | 13:16 | 49.922
2024-10-02 | 13:16 | 49.924
2024-10-02 | 13:16 | 49.923
2024-10-02 | 13:16 | 49.925
2024-10-02 | 13:16 | 49.927
2024-10-02 | 13:16 | 49.925
2024-10-02 | 13:16 | 49.923
2024-10-02 | 13:16 | 49.92
2024-10-02 | 13:16 | 49.919
2024-10-02 | 13:16 | 49.918
2024-10-02 | 13:16 | 49.917
2024-10-02 | 13:16 | 49.917
2024-10-02 | 13:16 | 49.918
2024-10-02 | 13:16 | 49.919
2024-10-02 | 13:16 | 49.919
2024-10-02 | 13:16 | 49.917
2024-10-02 | 13:16 | 49.916
2024-10-02 | 13:16 | 49.914
2024-10-02 | 13:16 | 49.912
2024-10-02 | 13:16 | 49.91
2024-10-02 | 13:16 | 49.906
2024-10-02 | 13:16 | 49.904
2024-10-02 | 13:16 | 49.903
2024-10-02 | 13:16 | 49.903
2024-10-02 | 13:16 | 49.903
2024-10-02 | 13:16 | 49.903
2024-10-02 | 13:16 | 49.901
2024-10-02 | 13:16 | 49.901
2024-10-02 | 13:16 | 49.903
2024-10-02 | 13:16 | 49.904
2024-10-02 | 13:16 | 49.905
2024-10-02 | 13:16 | 49.906
2024-10-02 | 13:16 | 49.904
2024-10-02 | 13:16 | 49.905
2024-10-02 | 13:16 | 49.905
2024-10-02 | 13:16 | 49.905
2024-10-02 | 13:17 | 49.906
2024-10-02 | 13:17 | 49.909
2024-10-02 | 13:17 | 49.911
2024-10-02 | 13:17 | 49.914
2024-10-02 | 13:17 | 49.915
2024-10-02 | 13:17 | 49.919
2024-10-02 | 13:17 | 49.92
2024-10-02 | 13:17 | 49.922
2024-10-02 | 13:17 | 49.923
2024-10-02 | 13:17 | 49.924
2024-10-02 | 13:17 | 49.924
2024-10-02 | 13:17 | 49.924
2024-10-02 | 13:17 | 49.923
2024-10-02 | 13:17 | 49.925
2024-10-02 | 13:17 | 49.927
2024-10-02 | 13:17 | 49.931
2024-10-02 | 13:17 | 49.934
2024-10-02 | 13:17 | 49.935
2024-10-02 | 13:17 | 49.933
2024-10-02 | 13:17 | 49.93
2024-10-02 | 13:17 | 49.93
2024-10-02 | 13:17 | 49.93
2024-10-02 | 13:17 | 49.928
2024-10-02 | 13:17 | 49.93
2024-10-02 | 13:17 | 49.927
2024-10-02 | 13:17 | 49.929
2024-10-02 | 13:17 | 49.927
2024-10-02 | 13:17 | 49.925
2024-10-02 | 13:17 | 49.919
2024-10-02 | 13:17 | 49.916
2024-10-02 | 13:17 | 49.915
2024-10-02 | 13:17 | 49.912
2024-10-02 | 13:17 | 49.914
2024-10-02 | 13:17 | 49.913
2024-10-02 | 13:17 | 49.913
2024-10-02 | 13:17 | 49.913
2024-10-02 | 13:17 | 49.911
2024-10-02 | 13:17 | 49.909
2024-10-02 | 13:17 | 49.911
2024-10-02 | 13:17 | 49.916
2024-10-02 | 13:17 | 49.918
2024-10-02 | 13:17 | 49.918
2024-10-02 | 13:17 | 49.919
2024-10-02 | 13:17 | 49.921
2024-10-02 | 13:17 | 49.924
2024-10-02 | 13:17 | 49.928
2024-10-02 | 13:17 | 49.932
2024-10-02 | 13:17 | 49.938
2024-10-02 | 13:17 | 49.94
2024-10-02 | 13:17 | 49.94
2024-10-02 | 13:17 | 49.942
2024-10-02 | 13:17 | 49.945
2024-10-02 | 13:17 | 49.944
2024-10-02 | 13:17 | 49.947
2024-10-02 | 13:17 | 49.947
2024-10-02 | 13:17 | 49.949
2024-10-02 | 13:17 | 49.951
2024-10-02 | 13:17 | 49.953
2024-10-02 | 13:17 | 49.951
2024-10-02 | 13:17 | 49.949
2024-10-02 | 13:18 | 49.947
2024-10-02 | 13:18 | 49.949
2024-10-02 | 13:18 | 49.948
2024-10-02 | 13:18 | 49.951
2024-10-02 | 13:18 | 49.955
2024-10-02 | 13:18 | 49.958
2024-10-02 | 13:18 | 49.959
2024-10-02 | 13:18 | 49.962
2024-10-02 | 13:18 | 49.963
2024-10-02 | 13:18 | 49.964
2024-10-02 | 13:18 | 49.965
2024-10-02 | 13:18 | 49.963
2024-10-02 | 13:18 | 49.961
2024-10-02 | 13:18 | 49.96
2024-10-02 | 13:18 | 49.959
2024-10-02 | 13:18 | 49.958
2024-10-02 | 13:18 | 49.957
2024-10-02 | 13:18 | 49.955
2024-10-02 | 13:18 | 49.951
2024-10-02 | 13:18 | 49.948
2024-10-02 | 13:18 | 49.948
2024-10-02 | 13:18 | 49.95
2024-10-02 | 13:18 | 49.95
2024-10-02 | 13:18 | 49.95
2024-10-02 | 13:18 | 49.949
2024-10-02 | 13:18 | 49.947
2024-10-02 | 13:18 | 49.946
2024-10-02 | 13:18 | 49.946
2024-10-02 | 13:18 | 49.949
2024-10-02 | 13:18 | 49.952
2024-10-02 | 13:18 | 49.955
2024-10-02 | 13:18 | 49.956
2024-10-02 | 13:18 | 49.96
2024-10-02 | 13:18 | 49.961
2024-10-02 | 13:18 | 49.958
2024-10-02 | 13:18 | 49.956
2024-10-02 | 13:18 | 49.952
2024-10-02 | 13:18 | 49.951
2024-10-02 | 13:18 | 49.949
2024-10-02 | 13:18 | 49.947
2024-10-02 | 13:18 | 49.944
2024-10-02 | 13:18 | 49.943
2024-10-02 | 13:18 | 49.942
2024-10-02 | 13:18 | 49.939
2024-10-02 | 13:18 | 49.938
2024-10-02 | 13:18 | 49.935
2024-10-02 | 13:18 | 49.94
2024-10-02 | 13:18 | 49.94
2024-10-02 | 13:18 | 49.943
2024-10-02 | 13:18 | 49.942
2024-10-02 | 13:18 | 49.943
2024-10-02 | 13:18 | 49.944
2024-10-02 | 13:18 | 49.949
2024-10-02 | 13:18 | 49.953
2024-10-02 | 13:18 | 49.955
2024-10-02 | 13:18 | 49.957
2024-10-02 | 13:18 | 49.956
2024-10-02 | 13:18 | 49.955
2024-10-02 | 13:18 | 49.953
2024-10-02 | 13:19 | 49.954
2024-10-02 | 13:19 | 49.954
2024-10-02 | 13:19 | 49.954
2024-10-02 | 13:19 | 49.953
2024-10-02 | 13:19 | 49.953
2024-10-02 | 13:19 | 49.953
2024-10-02 | 13:19 | 49.953
2024-10-02 | 13:19 | 49.953
2024-10-02 | 13:19 | 49.953
2024-10-02 | 13:19 | 49.953
2024-10-02 | 13:19 | 49.954
2024-10-02 | 13:19 | 49.953
2024-10-02 | 13:19 | 49.952
2024-10-02 | 13:19 | 49.952
2024-10-02 | 13:19 | 49.95
2024-10-02 | 13:19 | 49.948
2024-10-02 | 13:19 | 49.95
2024-10-02 | 13:19 | 49.947
2024-10-02 | 13:19 | 49.944
2024-10-02 | 13:19 | 49.945
2024-10-02 | 13:19 | 49.944
2024-10-02 | 13:19 | 49.944
2024-10-02 | 13:19 | 49.945
2024-10-02 | 13:19 | 49.946
2024-10-02 | 13:19 | 49.947
2024-10-02 | 13:19 | 49.949
2024-10-02 | 13:19 | 49.951
2024-10-02 | 13:19 | 49.952
2024-10-02 | 13:19 | 49.952
2024-10-02 | 13:19 | 49.951
2024-10-02 | 13:19 | 49.952
2024-10-02 | 13:19 | 49.954
2024-10-02 | 13:19 | 49.953
2024-10-02 | 13:19 | 49.949
2024-10-02 | 13:19 | 49.943
2024-10-02 | 13:19 | 49.937
2024-10-02 | 13:19 | 49.934
2024-10-02 | 13:19 | 49.93
2024-10-02 | 13:19 | 49.927
2024-10-02 | 13:19 | 49.926
2024-10-02 | 13:19 | 49.926
2024-10-02 | 13:19 | 49.927
2024-10-02 | 13:19 | 49.929
2024-10-02 | 13:19 | 49.93
2024-10-02 | 13:19 | 49.933
2024-10-02 | 13:19 | 49.934
2024-10-02 | 13:19 | 49.936
2024-10-02 | 13:19 | 49.935
2024-10-02 | 13:19 | 49.934
2024-10-02 | 13:19 | 49.933
2024-10-02 | 13:19 | 49.931
2024-10-02 | 13:19 | 49.932
2024-10-02 | 13:19 | 49.935
2024-10-02 | 13:19 | 49.937
2024-10-02 | 13:19 | 49.941
2024-10-02 | 13:19 | 49.942
2024-10-02 | 13:19 | 49.943
2024-10-02 | 13:19 | 49.943
2024-10-02 | 13:19 | 49.947
2024-10-02 | 13:19 | 49.947
2024-10-02 | 13:19 | 49.949
2024-10-02 | 13:20 | 49.951
2024-10-02 | 13:20 | 49.952
2024-10-02 | 13:20 | 49.954
2024-10-02 | 13:20 | 49.956
2024-10-02 | 13:20 | 49.959
2024-10-02 | 13:20 | 49.961
2024-10-02 | 13:20 | 49.962
2024-10-02 | 13:20 | 49.962
2024-10-02 | 13:20 | 49.96
2024-10-02 | 13:20 | 49.959
2024-10-02 | 13:20 | 49.958
2024-10-02 | 13:20 | 49.956
2024-10-02 | 13:20 | 49.957
2024-10-02 | 13:20 | 49.959
2024-10-02 | 13:20 | 49.957
2024-10-02 | 13:20 | 49.955
2024-10-02 | 13:20 | 49.956
2024-10-02 | 13:20 | 49.953
2024-10-02 | 13:20 | 49.955
2024-10-02 | 13:20 | 49.956
2024-10-02 | 13:20 | 49.958
2024-10-02 | 13:20 | 49.959
2024-10-02 | 13:20 | 49.96
2024-10-02 | 13:20 | 49.957
2024-10-02 | 13:20 | 49.955
2024-10-02 | 13:20 | 49.952
2024-10-02 | 13:20 | 49.949
2024-10-02 | 13:20 | 49.946
2024-10-02 | 13:20 | 49.946
2024-10-02 | 13:20 | 49.945
2024-10-02 | 13:20 | 49.942
2024-10-02 | 13:20 | 49.942
2024-10-02 | 13:20 | 49.941
2024-10-02 | 13:20 | 49.946
2024-10-02 | 13:20 | 49.947
2024-10-02 | 13:20 | 49.95
2024-10-02 | 13:20 | 49.949
2024-10-02 | 13:20 | 49.949
2024-10-02 | 13:20 | 49.949
2024-10-02 | 13:20 | 49.948
2024-10-02 | 13:20 | 49.946
2024-10-02 | 13:20 | 49.944
2024-10-02 | 13:20 | 49.944
2024-10-02 | 13:20 | 49.941
2024-10-02 | 13:20 | 49.941
2024-10-02 | 13:20 | 49.939
2024-10-02 | 13:20 | 49.936
2024-10-02 | 13:20 | 49.933
2024-10-02 | 13:20 | 49.934
2024-10-02 | 13:20 | 49.933
2024-10-02 | 13:20 | 49.934
2024-10-02 | 13:20 | 49.931
2024-10-02 | 13:20 | 49.927
2024-10-02 | 13:20 | 49.927
2024-10-02 | 13:20 | 49.925
2024-10-02 | 13:20 | 49.928
2024-10-02 | 13:20 | 49.929
2024-10-02 | 13:20 | 49.931
2024-10-02 | 13:20 | 49.935
2024-10-02 | 13:21 | 49.938
2024-10-02 | 13:21 | 49.941
2024-10-02 | 13:21 | 49.939
2024-10-02 | 13:21 | 49.94
2024-10-02 | 13:21 | 49.939
2024-10-02 | 13:21 | 49.943
2024-10-02 | 13:21 | 49.943
2024-10-02 | 13:21 | 49.945
2024-10-02 | 13:21 | 49.943
2024-10-02 | 13:21 | 49.946
2024-10-02 | 13:21 | 49.946
2024-10-02 | 13:21 | 49.947
2024-10-02 | 13:21 | 49.948
2024-10-02 | 13:21 | 49.952
2024-10-02 | 13:21 | 49.955
2024-10-02 | 13:21 | 49.955
2024-10-02 | 13:21 | 49.956
2024-10-02 | 13:21 | 49.956
2024-10-02 | 13:21 | 49.955
2024-10-02 | 13:21 | 49.953
2024-10-02 | 13:21 | 49.951
2024-10-02 | 13:21 | 49.95
2024-10-02 | 13:21 | 49.948
2024-10-02 | 13:21 | 49.948
2024-10-02 | 13:21 | 49.946
2024-10-02 | 13:21 | 49.944
2024-10-02 | 13:21 | 49.946
2024-10-02 | 13:21 | 49.944
2024-10-02 | 13:21 | 49.943
2024-10-02 | 13:21 | 49.94
2024-10-02 | 13:21 | 49.938
2024-10-02 | 13:21 | 49.935
2024-10-02 | 13:21 | 49.933
2024-10-02 | 13:21 | 49.932
2024-10-02 | 13:21 | 49.931
2024-10-02 | 13:21 | 49.933
2024-10-02 | 13:21 | 49.935
2024-10-02 | 13:21 | 49.933
2024-10-02 | 13:21 | 49.935
2024-10-02 | 13:21 | 49.934
2024-10-02 | 13:21 | 49.935
2024-10-02 | 13:21 | 49.938
2024-10-02 | 13:21 | 49.936
2024-10-02 | 13:21 | 49.936
2024-10-02 | 13:21 | 49.935
2024-10-02 | 13:21 | 49.935
2024-10-02 | 13:21 | 49.932
2024-10-02 | 13:21 | 49.935
2024-10-02 | 13:21 | 49.935
2024-10-02 | 13:21 | 49.937
2024-10-02 | 13:21 | 49.938
2024-10-02 | 13:21 | 49.939
2024-10-02 | 13:21 | 49.935
2024-10-02 | 13:21 | 49.935
2024-10-02 | 13:21 | 49.934
2024-10-02 | 13:21 | 49.935
2024-10-02 | 13:21 | 49.937
2024-10-02 | 13:21 | 49.937
2024-10-02 | 13:21 | 49.937
2024-10-02 | 13:21 | 49.936
2024-10-02 | 13:21 | 49.94
2024-10-02 | 13:22 | 49.944
2024-10-02 | 13:22 | 49.951
2024-10-02 | 13:22 | 49.952
2024-10-02 | 13:22 | 49.955
2024-10-02 | 13:22 | 49.956
2024-10-02 | 13:22 | 49.956
2024-10-02 | 13:22 | 49.954
2024-10-02 | 13:22 | 49.953
2024-10-02 | 13:22 | 49.949
2024-10-02 | 13:22 | 49.947
2024-10-02 | 13:22 | 49.948
2024-10-02 | 13:22 | 49.946
2024-10-02 | 13:22 | 49.947
2024-10-02 | 13:22 | 49.948
2024-10-02 | 13:22 | 49.947
2024-10-02 | 13:22 | 49.949
2024-10-02 | 13:22 | 49.951
2024-10-02 | 13:22 | 49.95
2024-10-02 | 13:22 | 49.95
2024-10-02 | 13:22 | 49.951
2024-10-02 | 13:22 | 49.95
2024-10-02 | 13:22 | 49.949
2024-10-02 | 13:22 | 49.948
2024-10-02 | 13:22 | 49.949
2024-10-02 | 13:22 | 49.949
2024-10-02 | 13:22 | 49.949
2024-10-02 | 13:22 | 49.951
2024-10-02 | 13:22 | 49.954
2024-10-02 | 13:22 | 49.956
2024-10-02 | 13:22 | 49.958
2024-10-02 | 13:22 | 49.958
2024-10-02 | 13:22 | 49.958
2024-10-02 | 13:22 | 49.962
2024-10-02 | 13:22 | 49.966
2024-10-02 | 13:22 | 49.965
2024-10-02 | 13:22 | 49.964
2024-10-02 | 13:22 | 49.965
2024-10-02 | 13:22 | 49.963
2024-10-02 | 13:22 | 49.961
2024-10-02 | 13:22 | 49.959
2024-10-02 | 13:22 | 49.957
2024-10-02 | 13:22 | 49.958
2024-10-02 | 13:22 | 49.957
2024-10-02 | 13:22 | 49.957
2024-10-02 | 13:22 | 49.955
2024-10-02 | 13:22 | 49.955
2024-10-02 | 13:22 | 49.954
2024-10-02 | 13:22 | 49.949
2024-10-02 | 13:22 | 49.948
2024-10-02 | 13:22 | 49.944
2024-10-02 | 13:22 | 49.94
2024-10-02 | 13:22 | 49.94
2024-10-02 | 13:22 | 49.941
2024-10-02 | 13:22 | 49.942
2024-10-02 | 13:22 | 49.942
2024-10-02 | 13:22 | 49.942
2024-10-02 | 13:22 | 49.946
2024-10-02 | 13:22 | 49.949
2024-10-02 | 13:22 | 49.95
2024-10-02 | 13:23 | 49.952
2024-10-02 | 13:23 | 49.954
2024-10-02 | 13:23 | 49.953
2024-10-02 | 13:23 | 49.953
2024-10-02 | 13:23 | 49.954
2024-10-02 | 13:23 | 49.954
2024-10-02 | 13:23 | 49.956
2024-10-02 | 13:23 | 49.957
2024-10-02 | 13:23 | 49.96
2024-10-02 | 13:23 | 49.964
2024-10-02 | 13:23 | 49.966
2024-10-02 | 13:23 | 49.966
2024-10-02 | 13:23 | 49.966
2024-10-02 | 13:23 | 49.967
2024-10-02 | 13:23 | 49.966
2024-10-02 | 13:23 | 49.967
2024-10-02 | 13:23 | 49.969
2024-10-02 | 13:23 | 49.968
2024-10-02 | 13:23 | 49.97
2024-10-02 | 13:23 | 49.967
2024-10-02 | 13:23 | 49.966
2024-10-02 | 13:23 | 49.965
2024-10-02 | 13:23 | 49.963
2024-10-02 | 13:23 | 49.962
2024-10-02 | 13:23 | 49.96
2024-10-02 | 13:23 | 49.959
2024-10-02 | 13:23 | 49.956
2024-10-02 | 13:23 | 49.952
2024-10-02 | 13:23 | 49.952
2024-10-02 | 13:23 | 49.953
2024-10-02 | 13:23 | 49.952
2024-10-02 | 13:23 | 49.948
2024-10-02 | 13:23 | 49.946
2024-10-02 | 13:23 | 49.943
2024-10-02 | 13:23 | 49.94
2024-10-02 | 13:23 | 49.937
2024-10-02 | 13:23 | 49.936
2024-10-02 | 13:23 | 49.936
2024-10-02 | 13:23 | 49.936
2024-10-02 | 13:23 | 49.934
2024-10-02 | 13:23 | 49.932
2024-10-02 | 13:23 | 49.93
2024-10-02 | 13:23 | 49.929
2024-10-02 | 13:23 | 49.929
2024-10-02 | 13:23 | 49.929
2024-10-02 | 13:23 | 49.93
2024-10-02 | 13:23 | 49.93
2024-10-02 | 13:23 | 49.929
2024-10-02 | 13:23 | 49.929
2024-10-02 | 13:23 | 49.931
2024-10-02 | 13:23 | 49.934
2024-10-02 | 13:23 | 49.936
2024-10-02 | 13:23 | 49.94
2024-10-02 | 13:23 | 49.945
2024-10-02 | 13:23 | 49.949
2024-10-02 | 13:23 | 49.949
2024-10-02 | 13:23 | 49.95
2024-10-02 | 13:23 | 49.95
2024-10-02 | 13:23 | 49.95
2024-10-02 | 13:23 | 49.952
2024-10-02 | 13:23 | 49.952
2024-10-02 | 13:24 | 49.952
2024-10-02 | 13:24 | 49.951
2024-10-02 | 13:24 | 49.949
2024-10-02 | 13:24 | 49.948
2024-10-02 | 13:24 | 49.95
2024-10-02 | 13:24 | 49.953
2024-10-02 | 13:24 | 49.954
2024-10-02 | 13:24 | 49.955
2024-10-02 | 13:24 | 49.959
2024-10-02 | 13:24 | 49.961
2024-10-02 | 13:24 | 49.962
2024-10-02 | 13:24 | 49.964
2024-10-02 | 13:24 | 49.964
2024-10-02 | 13:24 | 49.964
2024-10-02 | 13:24 | 49.963
2024-10-02 | 13:24 | 49.959
2024-10-02 | 13:24 | 49.957
2024-10-02 | 13:24 | 49.955
2024-10-02 | 13:24 | 49.955
2024-10-02 | 13:24 | 49.956
2024-10-02 | 13:24 | 49.959
2024-10-02 | 13:24 | 49.96
2024-10-02 | 13:24 | 49.962
2024-10-02 | 13:24 | 49.963
2024-10-02 | 13:24 | 49.962
2024-10-02 | 13:24 | 49.962
2024-10-02 | 13:24 | 49.962
2024-10-02 | 13:24 | 49.96
2024-10-02 | 13:24 | 49.957
2024-10-02 | 13:24 | 49.953
2024-10-02 | 13:24 | 49.949
2024-10-02 | 13:24 | 49.946
2024-10-02 | 13:24 | 49.946
2024-10-02 | 13:24 | 49.945
2024-10-02 | 13:24 | 49.945
2024-10-02 | 13:24 | 49.946
2024-10-02 | 13:24 | 49.949
2024-10-02 | 13:24 | 49.952
2024-10-02 | 13:24 | 49.952
2024-10-02 | 13:24 | 49.953
2024-10-02 | 13:24 | 49.953
2024-10-02 | 13:24 | 49.952
2024-10-02 | 13:24 | 49.951
2024-10-02 | 13:24 | 49.952
2024-10-02 | 13:24 | 49.952
2024-10-02 | 13:24 | 49.952
2024-10-02 | 13:24 | 49.95
2024-10-02 | 13:24 | 49.947
2024-10-02 | 13:24 | 49.942
2024-10-02 | 13:24 | 49.941
2024-10-02 | 13:24 | 49.942
2024-10-02 | 13:24 | 49.941
2024-10-02 | 13:24 | 49.941
2024-10-02 | 13:24 | 49.94
2024-10-02 | 13:24 | 49.942
2024-10-02 | 13:24 | 49.943
2024-10-02 | 13:24 | 49.942
2024-10-02 | 13:24 | 49.942
2024-10-02 | 13:24 | 49.942
2024-10-02 | 13:25 | 49.942
2024-10-02 | 13:25 | 49.942
2024-10-02 | 13:25 | 49.942
2024-10-02 | 13:25 | 49.941
2024-10-02 | 13:25 | 49.944
2024-10-02 | 13:25 | 49.948
2024-10-02 | 13:25 | 49.952
2024-10-02 | 13:25 | 49.957
2024-10-02 | 13:25 | 49.959
2024-10-02 | 13:25 | 49.962
2024-10-02 | 13:25 | 49.964
2024-10-02 | 13:25 | 49.966
2024-10-02 | 13:25 | 49.966
2024-10-02 | 13:25 | 49.966
2024-10-02 | 13:25 | 49.965
2024-10-02 | 13:25 | 49.965
2024-10-02 | 13:25 | 49.965
2024-10-02 | 13:25 | 49.967
2024-10-02 | 13:25 | 49.969
2024-10-02 | 13:25 | 49.97
2024-10-02 | 13:25 | 49.971
2024-10-02 | 13:25 | 49.971
2024-10-02 | 13:25 | 49.971
2024-10-02 | 13:25 | 49.969
2024-10-02 | 13:25 | 49.968
2024-10-02 | 13:25 | 49.967
2024-10-02 | 13:25 | 49.963
2024-10-02 | 13:25 | 49.959
2024-10-02 | 13:25 | 49.958
2024-10-02 | 13:25 | 49.958
2024-10-02 | 13:25 | 49.957
2024-10-02 | 13:25 | 49.953
2024-10-02 | 13:25 | 49.951
2024-10-02 | 13:25 | 49.954
2024-10-02 | 13:25 | 49.955
2024-10-02 | 13:25 | 49.956
2024-10-02 | 13:25 | 49.957
2024-10-02 | 13:25 | 49.96
2024-10-02 | 13:25 | 49.967
2024-10-02 | 13:25 | 49.971
2024-10-02 | 13:25 | 49.976
2024-10-02 | 13:25 | 49.978
2024-10-02 | 13:25 | 49.981
2024-10-02 | 13:25 | 49.982
2024-10-02 | 13:25 | 49.984
2024-10-02 | 13:25 | 49.986
2024-10-02 | 13:25 | 49.99
2024-10-02 | 13:25 | 49.995
2024-10-02 | 13:25 | 50
2024-10-02 | 13:25 | 50.005
2024-10-02 | 13:25 | 50.011
2024-10-02 | 13:25 | 50.017
2024-10-02 | 13:25 | 50.022
2024-10-02 | 13:25 | 50.023
2024-10-02 | 13:25 | 50.026
2024-10-02 | 13:25 | 50.027
2024-10-02 | 13:25 | 50.027
2024-10-02 | 13:25 | 50.027
2024-10-02 | 13:25 | 50.025
2024-10-02 | 13:25 | 50.022
2024-10-02 | 13:25 | 50.018
2024-10-02 | 13:26 | 50.017
2024-10-02 | 13:26 | 50.018
2024-10-02 | 13:26 | 50.017
2024-10-02 | 13:26 | 50.019
2024-10-02 | 13:26 | 50.02
2024-10-02 | 13:26 | 50.021
2024-10-02 | 13:26 | 50.024
2024-10-02 | 13:26 | 50.028
2024-10-02 | 13:26 | 50.029
2024-10-02 | 13:26 | 50.031
2024-10-02 | 13:26 | 50.029
2024-10-02 | 13:26 | 50.028
2024-10-02 | 13:26 | 50.025
2024-10-02 | 13:26 | 50.02
2024-10-02 | 13:26 | 50.016
2024-10-02 | 13:26 | 50.011
2024-10-02 | 13:26 | 50.01
2024-10-02 | 13:26 | 50.01
2024-10-02 | 13:26 | 50.01
2024-10-02 | 13:26 | 50.008
2024-10-02 | 13:26 | 50.009
2024-10-02 | 13:26 | 50.01
2024-10-02 | 13:26 | 50.009
2024-10-02 | 13:26 | 50.007
2024-10-02 | 13:26 | 50.003
2024-10-02 | 13:26 | 49.999
2024-10-02 | 13:26 | 49.997
2024-10-02 | 13:26 | 49.993
2024-10-02 | 13:26 | 49.99
2024-10-02 | 13:26 | 49.988
2024-10-02 | 13:26 | 49.984
2024-10-02 | 13:26 | 49.984
2024-10-02 | 13:26 | 49.984
2024-10-02 | 13:26 | 49.987
2024-10-02 | 13:26 | 49.992
2024-10-02 | 13:26 | 49.995
2024-10-02 | 13:26 | 49.999
2024-10-02 | 13:26 | 50.006
2024-10-02 | 13:26 | 50.012
2024-10-02 | 13:26 | 50.018
2024-10-02 | 13:26 | 50.025
2024-10-02 | 13:26 | 50.027
2024-10-02 | 13:26 | 50.028
2024-10-02 | 13:26 | 50.03
2024-10-02 | 13:26 | 50.029

## 20241008-1
In GMT
Date | Time | Freq
2024-10-08 | 7:47 | 49.919 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-10-08 | 7:47 | 49.917 | 222 | BRITNED | 676.211
2024-10-08 | 7:47 | 49.916 | 268 | WBURB-2 | 428.156
2024-10-08 | 7:47 | 49.915 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-10-08 | 7:47 | 49.913 |  | Viking Link | -648.9
2024-10-08 | 7:47 | 49.911 |  | Viking Link | 1398.96
2024-10-08 | 7:47 | 49.909 | 209 | DRAXX-3 | 626.95
2024-10-08 | 7:47 | 49.905 | 154 | CDCL-1 | 391.57
2024-10-08 | 7:47 | 49.902 | 268 | ROCK-1 | 468.495
2024-10-08 | 7:47 | 49.901 | 148 | IFA Bipole1 | 945.473
2024-10-08 | 7:47 | 49.9 | 132 | IFA Bipole1 | 999.1
2024-10-08 | 7:47 | 49.897 | 141 | IFA Bipole2 | 1000
2024-10-08 | 7:47 | 49.893 | 135 | IFA Bipole1 | 996.75
2024-10-08 | 7:47 | 49.89 |  | Viking Link | -780.3
2024-10-08 | 7:47 | 49.891
2024-10-08 | 7:47 | 49.891
2024-10-08 | 7:47 | 49.888
2024-10-08 | 7:47 | 49.887
2024-10-08 | 7:47 | 49.886
2024-10-08 | 7:47 | 49.884 | 130 | HEYM12 | 271.908
2024-10-08 | 7:47 | 49.882 | 228 | HUMR-1 | 303.75
2024-10-08 | 7:47 | 49.885
2024-10-08 | 7:47 | 49.887
2024-10-08 | 7:47 | 49.888
2024-10-08 | 7:47 | 49.893
2024-10-08 | 7:47 | 49.894
2024-10-08 | 7:47 | 49.896
2024-10-08 | 7:47 | 49.896
2024-10-08 | 7:47 | 49.895
2024-10-08 | 7:47 | 49.893
2024-10-08 | 7:48 | 49.893 | 211 | CDCL-1 | 291.5
2024-10-08 | 7:48 | 49.892 | 199 | STAY-2 | 413.125
2024-10-08 | 7:48 | 49.893 | 173 | CDCL-1 | 397.375
2024-10-08 | 7:48 | 49.894 | 248 | SEAB-2 | 361.25
2024-10-08 | 7:48 | 49.894 | 255 | FRANCE | 995.65
2024-10-08 | 7:48 | 49.892 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-10-08 | 7:48 | 49.891
2024-10-08 | 7:48 | 49.89
2024-10-08 | 7:48 | 49.891
2024-10-08 | 7:48 | 49.891
2024-10-08 | 7:48 | 49.893
2024-10-08 | 7:48 | 49.892
2024-10-08 | 7:48 | 49.894
2024-10-08 | 7:48 | 49.894
2024-10-08 | 7:48 | 49.894
2024-10-08 | 7:48 | 49.895
2024-10-08 | 7:48 | 49.895
2024-10-08 | 7:48 | 49.896
2024-10-08 | 7:48 | 49.895
2024-10-08 | 7:48 | 49.895
2024-10-08 | 7:48 | 49.895
2024-10-08 | 7:48 | 49.895
2024-10-08 | 7:48 | 49.895
2024-10-08 | 7:48 | 49.895
2024-10-08 | 7:48 | 49.897
2024-10-08 | 7:48 | 49.897
2024-10-08 | 7:48 | 49.897
2024-10-08 | 7:48 | 49.896
2024-10-08 | 7:48 | 49.862
2024-10-08 | 7:48 | 49.725
2024-10-08 | 7:48 | 49.648
2024-10-08 | 7:48 | 49.621
2024-10-08 | 7:48 | 49.615
2024-10-08 | 7:48 | 49.614
2024-10-08 | 7:48 | 49.615
2024-10-08 | 7:48 | 49.616
2024-10-08 | 7:48 | 49.615
2024-10-08 | 7:48 | 49.612
2024-10-08 | 7:48 | 49.609
2024-10-08 | 7:48 | 49.611
2024-10-08 | 7:48 | 49.612
2024-10-08 | 7:48 | 49.609
2024-10-08 | 7:48 | 49.608
2024-10-08 | 7:48 | 49.605
2024-10-08 | 7:48 | 49.604
2024-10-08 | 7:48 | 49.6
2024-10-08 | 7:48 | 49.597
2024-10-08 | 7:48 | 49.595
2024-10-08 | 7:48 | 49.594
2024-10-08 | 7:48 | 49.596
2024-10-08 | 7:48 | 49.6
2024-10-08 | 7:48 | 49.606
2024-10-08 | 7:48 | 49.613
2024-10-08 | 7:48 | 49.62
2024-10-08 | 7:48 | 49.627
2024-10-08 | 7:48 | 49.634
2024-10-08 | 7:48 | 49.638
2024-10-08 | 7:48 | 49.638
2024-10-08 | 7:48 | 49.64
2024-10-08 | 7:48 | 49.639
2024-10-08 | 7:48 | 49.638
2024-10-08 | 7:49 | 49.636
2024-10-08 | 7:49 | 49.635
2024-10-08 | 7:49 | 49.632
2024-10-08 | 7:49 | 49.63
2024-10-08 | 7:49 | 49.631
2024-10-08 | 7:49 | 49.634
2024-10-08 | 7:49 | 49.635
2024-10-08 | 7:49 | 49.636
2024-10-08 | 7:49 | 49.635
2024-10-08 | 7:49 | 49.632
2024-10-08 | 7:49 | 49.632
2024-10-08 | 7:49 | 49.632
2024-10-08 | 7:49 | 49.632
2024-10-08 | 7:49 | 49.633
2024-10-08 | 7:49 | 49.633
2024-10-08 | 7:49 | 49.635
2024-10-08 | 7:49 | 49.635
2024-10-08 | 7:49 | 49.634
2024-10-08 | 7:49 | 49.633
2024-10-08 | 7:49 | 49.638
2024-10-08 | 7:49 | 49.643
2024-10-08 | 7:49 | 49.643
2024-10-08 | 7:49 | 49.644
2024-10-08 | 7:49 | 49.646
2024-10-08 | 7:49 | 49.645
2024-10-08 | 7:49 | 49.645
2024-10-08 | 7:49 | 49.644
2024-10-08 | 7:49 | 49.643
2024-10-08 | 7:49 | 49.64
2024-10-08 | 7:49 | 49.64
2024-10-08 | 7:49 | 49.638
2024-10-08 | 7:49 | 49.637
2024-10-08 | 7:49 | 49.639
2024-10-08 | 7:49 | 49.64
2024-10-08 | 7:49 | 49.643
2024-10-08 | 7:49 | 49.643
2024-10-08 | 7:49 | 49.641
2024-10-08 | 7:49 | 49.638
2024-10-08 | 7:49 | 49.637
2024-10-08 | 7:49 | 49.637
2024-10-08 | 7:49 | 49.64
2024-10-08 | 7:49 | 49.642
2024-10-08 | 7:49 | 49.645
2024-10-08 | 7:49 | 49.647
2024-10-08 | 7:49 | 49.647
2024-10-08 | 7:49 | 49.651
2024-10-08 | 7:49 | 49.652
2024-10-08 | 7:49 | 49.655
2024-10-08 | 7:49 | 49.654
2024-10-08 | 7:49 | 49.654
2024-10-08 | 7:49 | 49.659
2024-10-08 | 7:49 | 49.661
2024-10-08 | 7:49 | 49.666
2024-10-08 | 7:49 | 49.67
2024-10-08 | 7:49 | 49.672
2024-10-08 | 7:49 | 49.678
2024-10-08 | 7:49 | 49.681
2024-10-08 | 7:49 | 49.686
2024-10-08 | 7:49 | 49.688
2024-10-08 | 7:50 | 49.691
2024-10-08 | 7:50 | 49.696
2024-10-08 | 7:50 | 49.699
2024-10-08 | 7:50 | 49.705
2024-10-08 | 7:50 | 49.71
2024-10-08 | 7:50 | 49.712
2024-10-08 | 7:50 | 49.712
2024-10-08 | 7:50 | 49.712
2024-10-08 | 7:50 | 49.714
2024-10-08 | 7:50 | 49.715
2024-10-08 | 7:50 | 49.714
2024-10-08 | 7:50 | 49.715
2024-10-08 | 7:50 | 49.717
2024-10-08 | 7:50 | 49.717
2024-10-08 | 7:50 | 49.72
2024-10-08 | 7:50 | 49.723
2024-10-08 | 7:50 | 49.723
2024-10-08 | 7:50 | 49.724
2024-10-08 | 7:50 | 49.727
2024-10-08 | 7:50 | 49.73
2024-10-08 | 7:50 | 49.737
2024-10-08 | 7:50 | 49.742
2024-10-08 | 7:50 | 49.746
2024-10-08 | 7:50 | 49.749
2024-10-08 | 7:50 | 49.753
2024-10-08 | 7:50 | 49.755
2024-10-08 | 7:50 | 49.758
2024-10-08 | 7:50 | 49.764
2024-10-08 | 7:50 | 49.77
2024-10-08 | 7:50 | 49.775
2024-10-08 | 7:50 | 49.779
2024-10-08 | 7:50 | 49.779
2024-10-08 | 7:50 | 49.781
2024-10-08 | 7:50 | 49.787
2024-10-08 | 7:50 | 49.792
2024-10-08 | 7:50 | 49.793
2024-10-08 | 7:50 | 49.794
2024-10-08 | 7:50 | 49.794
2024-10-08 | 7:50 | 49.793
2024-10-08 | 7:50 | 49.792
2024-10-08 | 7:50 | 49.789
2024-10-08 | 7:50 | 49.786
2024-10-08 | 7:50 | 49.781
2024-10-08 | 7:50 | 49.777
2024-10-08 | 7:50 | 49.775
2024-10-08 | 7:50 | 49.773
2024-10-08 | 7:50 | 49.774
2024-10-08 | 7:50 | 49.776
2024-10-08 | 7:50 | 49.779
2024-10-08 | 7:50 | 49.783
2024-10-08 | 7:50 | 49.786
2024-10-08 | 7:50 | 49.789
2024-10-08 | 7:50 | 49.79
2024-10-08 | 7:50 | 49.79
2024-10-08 | 7:50 | 49.795
2024-10-08 | 7:50 | 49.796
2024-10-08 | 7:50 | 49.798
2024-10-08 | 7:50 | 49.797
2024-10-08 | 7:50 | 49.798
2024-10-08 | 7:50 | 49.799
2024-10-08 | 7:50 | 49.8
2024-10-08 | 7:51 | 49.804
2024-10-08 | 7:51 | 49.807
2024-10-08 | 7:51 | 49.813
2024-10-08 | 7:51 | 49.815
2024-10-08 | 7:51 | 49.82
2024-10-08 | 7:51 | 49.822
2024-10-08 | 7:51 | 49.825
2024-10-08 | 7:51 | 49.826
2024-10-08 | 7:51 | 49.831
2024-10-08 | 7:51 | 49.833
2024-10-08 | 7:51 | 49.838
2024-10-08 | 7:51 | 49.84
2024-10-08 | 7:51 | 49.843
2024-10-08 | 7:51 | 49.845
2024-10-08 | 7:51 | 49.846
2024-10-08 | 7:51 | 49.845
2024-10-08 | 7:51 | 49.843
2024-10-08 | 7:51 | 49.846
2024-10-08 | 7:51 | 49.848
2024-10-08 | 7:51 | 49.849
2024-10-08 | 7:51 | 49.848
2024-10-08 | 7:51 | 49.852
2024-10-08 | 7:51 | 49.852
2024-10-08 | 7:51 | 49.853
2024-10-08 | 7:51 | 49.851
2024-10-08 | 7:51 | 49.851
2024-10-08 | 7:51 | 49.85
2024-10-08 | 7:51 | 49.85
2024-10-08 | 7:51 | 49.851
2024-10-08 | 7:51 | 49.851
2024-10-08 | 7:51 | 49.85
2024-10-08 | 7:51 | 49.853
2024-10-08 | 7:51 | 49.851
2024-10-08 | 7:51 | 49.853
2024-10-08 | 7:51 | 49.852
2024-10-08 | 7:51 | 49.854
2024-10-08 | 7:51 | 49.853
2024-10-08 | 7:51 | 49.853
2024-10-08 | 7:51 | 49.853
2024-10-08 | 7:51 | 49.852
2024-10-08 | 7:51 | 49.852
2024-10-08 | 7:51 | 49.851
2024-10-08 | 7:51 | 49.849
2024-10-08 | 7:51 | 49.845
2024-10-08 | 7:51 | 49.846
2024-10-08 | 7:51 | 49.845
2024-10-08 | 7:51 | 49.846
2024-10-08 | 7:51 | 49.845
2024-10-08 | 7:51 | 49.843
2024-10-08 | 7:51 | 49.845
2024-10-08 | 7:51 | 49.844
2024-10-08 | 7:51 | 49.843
2024-10-08 | 7:51 | 49.844
2024-10-08 | 7:51 | 49.848
2024-10-08 | 7:51 | 49.848
2024-10-08 | 7:51 | 49.846
2024-10-08 | 7:51 | 49.844
2024-10-08 | 7:51 | 49.846
2024-10-08 | 7:51 | 49.849
2024-10-08 | 7:52 | 49.85
2024-10-08 | 7:52 | 49.852
2024-10-08 | 7:52 | 49.852
2024-10-08 | 7:52 | 49.853
2024-10-08 | 7:52 | 49.853
2024-10-08 | 7:52 | 49.853
2024-10-08 | 7:52 | 49.854
2024-10-08 | 7:52 | 49.852
2024-10-08 | 7:52 | 49.853
2024-10-08 | 7:52 | 49.85
2024-10-08 | 7:52 | 49.849
2024-10-08 | 7:52 | 49.849
2024-10-08 | 7:52 | 49.849
2024-10-08 | 7:52 | 49.852
2024-10-08 | 7:52 | 49.849
2024-10-08 | 7:52 | 49.849
2024-10-08 | 7:52 | 49.848
2024-10-08 | 7:52 | 49.843
2024-10-08 | 7:52 | 49.844
2024-10-08 | 7:52 | 49.842
2024-10-08 | 7:52 | 49.847
2024-10-08 | 7:52 | 49.845
2024-10-08 | 7:52 | 49.843
2024-10-08 | 7:52 | 49.846
2024-10-08 | 7:52 | 49.846
2024-10-08 | 7:52 | 49.844
2024-10-08 | 7:52 | 49.844
2024-10-08 | 7:52 | 49.844
2024-10-08 | 7:52 | 49.847
2024-10-08 | 7:52 | 49.85
2024-10-08 | 7:52 | 49.847
2024-10-08 | 7:52 | 49.849
2024-10-08 | 7:52 | 49.851
2024-10-08 | 7:52 | 49.852
2024-10-08 | 7:52 | 49.854
2024-10-08 | 7:52 | 49.857
2024-10-08 | 7:52 | 49.856
2024-10-08 | 7:52 | 49.856
2024-10-08 | 7:52 | 49.858
2024-10-08 | 7:52 | 49.86
2024-10-08 | 7:52 | 49.865
2024-10-08 | 7:52 | 49.867
2024-10-08 | 7:52 | 49.869
2024-10-08 | 7:52 | 49.867
2024-10-08 | 7:52 | 49.87
2024-10-08 | 7:52 | 49.869
2024-10-08 | 7:52 | 49.874
2024-10-08 | 7:52 | 49.877
2024-10-08 | 7:52 | 49.88
2024-10-08 | 7:52 | 49.882
2024-10-08 | 7:52 | 49.888
2024-10-08 | 7:52 | 49.891
2024-10-08 | 7:52 | 49.894
2024-10-08 | 7:52 | 49.894
2024-10-08 | 7:52 | 49.888
2024-10-08 | 7:52 | 49.887
2024-10-08 | 7:52 | 49.889
2024-10-08 | 7:52 | 49.888
2024-10-08 | 7:52 | 49.892
2024-10-08 | 7:52 | 49.891
2024-10-08 | 7:52 | 49.889
2024-10-08 | 7:53 | 49.888
2024-10-08 | 7:53 | 49.888
2024-10-08 | 7:53 | 49.885
2024-10-08 | 7:53 | 49.884
2024-10-08 | 7:53 | 49.88
2024-10-08 | 7:53 | 49.882
2024-10-08 | 7:53 | 49.882
2024-10-08 | 7:53 | 49.886
2024-10-08 | 7:53 | 49.89
2024-10-08 | 7:53 | 49.892
2024-10-08 | 7:53 | 49.897
2024-10-08 | 7:53 | 49.9
2024-10-08 | 7:53 | 49.903
2024-10-08 | 7:53 | 49.904
2024-10-08 | 7:53 | 49.902
2024-10-08 | 7:53 | 49.903
2024-10-08 | 7:53 | 49.901
2024-10-08 | 7:53 | 49.903
2024-10-08 | 7:53 | 49.901
2024-10-08 | 7:53 | 49.897
2024-10-08 | 7:53 | 49.896
2024-10-08 | 7:53 | 49.893
2024-10-08 | 7:53 | 49.895
2024-10-08 | 7:53 | 49.894
2024-10-08 | 7:53 | 49.896
2024-10-08 | 7:53 | 49.895
2024-10-08 | 7:53 | 49.891
2024-10-08 | 7:53 | 49.892
2024-10-08 | 7:53 | 49.891
2024-10-08 | 7:53 | 49.889
2024-10-08 | 7:53 | 49.888
2024-10-08 | 7:53 | 49.886
2024-10-08 | 7:53 | 49.885
2024-10-08 | 7:53 | 49.884
2024-10-08 | 7:53 | 49.884
2024-10-08 | 7:53 | 49.882
2024-10-08 | 7:53 | 49.88
2024-10-08 | 7:53 | 49.877
2024-10-08 | 7:53 | 49.875
2024-10-08 | 7:53 | 49.877
2024-10-08 | 7:53 | 49.877
2024-10-08 | 7:53 | 49.876
2024-10-08 | 7:53 | 49.873
2024-10-08 | 7:53 | 49.876
2024-10-08 | 7:53 | 49.877
2024-10-08 | 7:53 | 49.876
2024-10-08 | 7:53 | 49.875
2024-10-08 | 7:53 | 49.877
2024-10-08 | 7:53 | 49.879
2024-10-08 | 7:53 | 49.878
2024-10-08 | 7:53 | 49.878
2024-10-08 | 7:53 | 49.882
2024-10-08 | 7:53 | 49.881
2024-10-08 | 7:53 | 49.888
2024-10-08 | 7:53 | 49.891
2024-10-08 | 7:53 | 49.895
2024-10-08 | 7:53 | 49.896
2024-10-08 | 7:53 | 49.897
2024-10-08 | 7:53 | 49.899
2024-10-08 | 7:53 | 49.902
2024-10-08 | 7:54 | 49.902
2024-10-08 | 7:54 | 49.905
2024-10-08 | 7:54 | 49.904
2024-10-08 | 7:54 | 49.907
2024-10-08 | 7:54 | 49.906
2024-10-08 | 7:54 | 49.906
2024-10-08 | 7:54 | 49.903
2024-10-08 | 7:54 | 49.901
2024-10-08 | 7:54 | 49.902
2024-10-08 | 7:54 | 49.902
2024-10-08 | 7:54 | 49.901
2024-10-08 | 7:54 | 49.904
2024-10-08 | 7:54 | 49.907
2024-10-08 | 7:54 | 49.907
2024-10-08 | 7:54 | 49.909
2024-10-08 | 7:54 | 49.913
2024-10-08 | 7:54 | 49.914
2024-10-08 | 7:54 | 49.917
2024-10-08 | 7:54 | 49.919
2024-10-08 | 7:54 | 49.923
2024-10-08 | 7:54 | 49.925
2024-10-08 | 7:54 | 49.925
2024-10-08 | 7:54 | 49.926
2024-10-08 | 7:54 | 49.932
2024-10-08 | 7:54 | 49.934
2024-10-08 | 7:54 | 49.932
2024-10-08 | 7:54 | 49.932
2024-10-08 | 7:54 | 49.93
2024-10-08 | 7:54 | 49.931
2024-10-08 | 7:54 | 49.934
2024-10-08 | 7:54 | 49.934
2024-10-08 | 7:54 | 49.938
2024-10-08 | 7:54 | 49.94
2024-10-08 | 7:54 | 49.941
2024-10-08 | 7:54 | 49.94
2024-10-08 | 7:54 | 49.939
2024-10-08 | 7:54 | 49.936
2024-10-08 | 7:54 | 49.929
2024-10-08 | 7:54 | 49.924
2024-10-08 | 7:54 | 49.922
2024-10-08 | 7:54 | 49.921
2024-10-08 | 7:54 | 49.921
2024-10-08 | 7:54 | 49.921
2024-10-08 | 7:54 | 49.921
2024-10-08 | 7:54 | 49.92
2024-10-08 | 7:54 | 49.918
2024-10-08 | 7:54 | 49.917
2024-10-08 | 7:54 | 49.918
2024-10-08 | 7:54 | 49.92
2024-10-08 | 7:54 | 49.921
2024-10-08 | 7:54 | 49.926
2024-10-08 | 7:54 | 49.929
2024-10-08 | 7:54 | 49.928
2024-10-08 | 7:54 | 49.93
2024-10-08 | 7:54 | 49.927
2024-10-08 | 7:54 | 49.93
2024-10-08 | 7:54 | 49.927
2024-10-08 | 7:54 | 49.92
2024-10-08 | 7:54 | 49.917
2024-10-08 | 7:55 | 49.911
2024-10-08 | 7:55 | 49.905
2024-10-08 | 7:55 | 49.902
2024-10-08 | 7:55 | 49.902
2024-10-08 | 7:55 | 49.904
2024-10-08 | 7:55 | 49.902
2024-10-08 | 7:55 | 49.903
2024-10-08 | 7:55 | 49.905
2024-10-08 | 7:55 | 49.909
2024-10-08 | 7:55 | 49.911
2024-10-08 | 7:55 | 49.914
2024-10-08 | 7:55 | 49.916
2024-10-08 | 7:55 | 49.919
2024-10-08 | 7:55 | 49.922
2024-10-08 | 7:55 | 49.922
2024-10-08 | 7:55 | 49.922
2024-10-08 | 7:55 | 49.922
2024-10-08 | 7:55 | 49.921
2024-10-08 | 7:55 | 49.921
2024-10-08 | 7:55 | 49.918
2024-10-08 | 7:55 | 49.917
2024-10-08 | 7:55 | 49.919
2024-10-08 | 7:55 | 49.922
2024-10-08 | 7:55 | 49.924
2024-10-08 | 7:55 | 49.923
2024-10-08 | 7:55 | 49.925
2024-10-08 | 7:55 | 49.924
2024-10-08 | 7:55 | 49.924
2024-10-08 | 7:55 | 49.926
2024-10-08 | 7:55 | 49.926
2024-10-08 | 7:55 | 49.925
2024-10-08 | 7:55 | 49.925
2024-10-08 | 7:55 | 49.928
2024-10-08 | 7:55 | 49.927
2024-10-08 | 7:55 | 49.932
2024-10-08 | 7:55 | 49.938
2024-10-08 | 7:55 | 49.945
2024-10-08 | 7:55 | 49.947
2024-10-08 | 7:55 | 49.948
2024-10-08 | 7:55 | 49.946
2024-10-08 | 7:55 | 49.945
2024-10-08 | 7:55 | 49.944
2024-10-08 | 7:55 | 49.941
2024-10-08 | 7:55 | 49.941
2024-10-08 | 7:55 | 49.944
2024-10-08 | 7:55 | 49.945
2024-10-08 | 7:55 | 49.946
2024-10-08 | 7:55 | 49.946
2024-10-08 | 7:55 | 49.946
2024-10-08 | 7:55 | 49.944
2024-10-08 | 7:55 | 49.942
2024-10-08 | 7:55 | 49.939
2024-10-08 | 7:55 | 49.934
2024-10-08 | 7:55 | 49.93
2024-10-08 | 7:55 | 49.928
2024-10-08 | 7:55 | 49.923
2024-10-08 | 7:55 | 49.922
2024-10-08 | 7:55 | 49.918
2024-10-08 | 7:55 | 49.916
2024-10-08 | 7:55 | 49.914
2024-10-08 | 7:55 | 49.912
2024-10-08 | 7:56 | 49.91
2024-10-08 | 7:56 | 49.912
2024-10-08 | 7:56 | 49.918
2024-10-08 | 7:56 | 49.929
2024-10-08 | 7:56 | 49.938
2024-10-08 | 7:56 | 49.943
2024-10-08 | 7:56 | 49.945
2024-10-08 | 7:56 | 49.947
2024-10-08 | 7:56 | 49.946
2024-10-08 | 7:56 | 49.946
2024-10-08 | 7:56 | 49.946
2024-10-08 | 7:56 | 49.943
2024-10-08 | 7:56 | 49.945
2024-10-08 | 7:56 | 49.944
2024-10-08 | 7:56 | 49.942
2024-10-08 | 7:56 | 49.942
2024-10-08 | 7:56 | 49.946
2024-10-08 | 7:56 | 49.948
2024-10-08 | 7:56 | 49.951
2024-10-08 | 7:56 | 49.954
2024-10-08 | 7:56 | 49.958
2024-10-08 | 7:56 | 49.965
2024-10-08 | 7:56 | 49.966
2024-10-08 | 7:56 | 49.966
2024-10-08 | 7:56 | 49.966
2024-10-08 | 7:56 | 49.964
2024-10-08 | 7:56 | 49.964
2024-10-08 | 7:56 | 49.965
2024-10-08 | 7:56 | 49.967
2024-10-08 | 7:56 | 49.971
2024-10-08 | 7:56 | 49.97
2024-10-08 | 7:56 | 49.969
2024-10-08 | 7:56 | 49.964
2024-10-08 | 7:56 | 49.963
2024-10-08 | 7:56 | 49.962
2024-10-08 | 7:56 | 49.962
2024-10-08 | 7:56 | 49.961
2024-10-08 | 7:56 | 49.958
2024-10-08 | 7:56 | 49.955
2024-10-08 | 7:56 | 49.954
2024-10-08 | 7:56 | 49.956
2024-10-08 | 7:56 | 49.957
2024-10-08 | 7:56 | 49.959
2024-10-08 | 7:56 | 49.957
2024-10-08 | 7:56 | 49.957
2024-10-08 | 7:56 | 49.955
2024-10-08 | 7:56 | 49.955
2024-10-08 | 7:56 | 49.956
2024-10-08 | 7:56 | 49.957
2024-10-08 | 7:56 | 49.958
2024-10-08 | 7:56 | 49.959
2024-10-08 | 7:56 | 49.96
2024-10-08 | 7:56 | 49.963
2024-10-08 | 7:56 | 49.962
2024-10-08 | 7:56 | 49.96
2024-10-08 | 7:56 | 49.959
2024-10-08 | 7:56 | 49.961
2024-10-08 | 7:56 | 49.963
2024-10-08 | 7:56 | 49.964
2024-10-08 | 7:57 | 49.963
2024-10-08 | 7:57 | 49.961
2024-10-08 | 7:57 | 49.961
2024-10-08 | 7:57 | 49.963
2024-10-08 | 7:57 | 49.965
2024-10-08 | 7:57 | 49.966
2024-10-08 | 7:57 | 49.969
2024-10-08 | 7:57 | 49.97
2024-10-08 | 7:57 | 49.972
2024-10-08 | 7:57 | 49.971
2024-10-08 | 7:57 | 49.974
2024-10-08 | 7:57 | 49.974
2024-10-08 | 7:57 | 49.974
2024-10-08 | 7:57 | 49.973
2024-10-08 | 7:57 | 49.973
2024-10-08 | 7:57 | 49.971
2024-10-08 | 7:57 | 49.971
2024-10-08 | 7:57 | 49.97
2024-10-08 | 7:57 | 49.966
2024-10-08 | 7:57 | 49.962
2024-10-08 | 7:57 | 49.955
2024-10-08 | 7:57 | 49.954
2024-10-08 | 7:57 | 49.95
2024-10-08 | 7:57 | 49.951
2024-10-08 | 7:57 | 49.953
2024-10-08 | 7:57 | 49.956
2024-10-08 | 7:57 | 49.96
2024-10-08 | 7:57 | 49.962
2024-10-08 | 7:57 | 49.965
2024-10-08 | 7:57 | 49.967
2024-10-08 | 7:57 | 49.967
2024-10-08 | 7:57 | 49.967
2024-10-08 | 7:57 | 49.969
2024-10-08 | 7:57 | 49.968
2024-10-08 | 7:57 | 49.972
2024-10-08 | 7:57 | 49.976
2024-10-08 | 7:57 | 49.977
2024-10-08 | 7:57 | 49.979
2024-10-08 | 7:57 | 49.978
2024-10-08 | 7:57 | 49.977
2024-10-08 | 7:57 | 49.979
2024-10-08 | 7:57 | 49.977
2024-10-08 | 7:57 | 49.976
2024-10-08 | 7:57 | 49.976
2024-10-08 | 7:57 | 49.976
2024-10-08 | 7:57 | 49.978
2024-10-08 | 7:57 | 49.98
2024-10-08 | 7:57 | 49.98
2024-10-08 | 7:57 | 49.981
2024-10-08 | 7:57 | 49.982
2024-10-08 | 7:57 | 49.986
2024-10-08 | 7:57 | 49.987
2024-10-08 | 7:57 | 49.986
2024-10-08 | 7:57 | 49.986
2024-10-08 | 7:57 | 49.986
2024-10-08 | 7:57 | 49.984
2024-10-08 | 7:57 | 49.982
2024-10-08 | 7:57 | 49.976
2024-10-08 | 7:57 | 49.975
2024-10-08 | 7:57 | 49.978
2024-10-08 | 7:57 | 49.977
2024-10-08 | 7:58 | 49.978
2024-10-08 | 7:58 | 49.982
2024-10-08 | 7:58 | 49.983
2024-10-08 | 7:58 | 49.984
2024-10-08 | 7:58 | 49.984
2024-10-08 | 7:58 | 49.981
2024-10-08 | 7:58 | 49.982
2024-10-08 | 7:58 | 49.982
2024-10-08 | 7:58 | 49.985
2024-10-08 | 7:58 | 49.985
2024-10-08 | 7:58 | 49.986
2024-10-08 | 7:58 | 49.985
2024-10-08 | 7:58 | 49.984
2024-10-08 | 7:58 | 49.982
2024-10-08 | 7:58 | 49.977
2024-10-08 | 7:58 | 49.974
2024-10-08 | 7:58 | 49.973
2024-10-08 | 7:58 | 49.971
2024-10-08 | 7:58 | 49.971
2024-10-08 | 7:58 | 49.969
2024-10-08 | 7:58 | 49.97
2024-10-08 | 7:58 | 49.971
2024-10-08 | 7:58 | 49.973
2024-10-08 | 7:58 | 49.974
2024-10-08 | 7:58 | 49.974
2024-10-08 | 7:58 | 49.973
2024-10-08 | 7:58 | 49.974
2024-10-08 | 7:58 | 49.975
2024-10-08 | 7:58 | 49.973
2024-10-08 | 7:58 | 49.973
2024-10-08 | 7:58 | 49.97
2024-10-08 | 7:58 | 49.97
2024-10-08 | 7:58 | 49.971
2024-10-08 | 7:58 | 49.971
2024-10-08 | 7:58 | 49.971
2024-10-08 | 7:58 | 49.969
2024-10-08 | 7:58 | 49.971
2024-10-08 | 7:58 | 49.973
2024-10-08 | 7:58 | 49.974
2024-10-08 | 7:58 | 49.976
2024-10-08 | 7:58 | 49.976
2024-10-08 | 7:58 | 49.975
2024-10-08 | 7:58 | 49.974
2024-10-08 | 7:58 | 49.973
2024-10-08 | 7:58 | 49.972
2024-10-08 | 7:58 | 49.975
2024-10-08 | 7:58 | 49.976
2024-10-08 | 7:58 | 49.976
2024-10-08 | 7:58 | 49.98
2024-10-08 | 7:58 | 49.98
2024-10-08 | 7:58 | 49.98
2024-10-08 | 7:58 | 49.979
2024-10-08 | 7:58 | 49.977
2024-10-08 | 7:58 | 49.975
2024-10-08 | 7:58 | 49.974
2024-10-08 | 7:58 | 49.973
2024-10-08 | 7:58 | 49.973
2024-10-08 | 7:58 | 49.974
2024-10-08 | 7:58 | 49.974
2024-10-08 | 7:59 | 49.973
2024-10-08 | 7:59 | 49.975
2024-10-08 | 7:59 | 49.977
2024-10-08 | 7:59 | 49.978
2024-10-08 | 7:59 | 49.977
2024-10-08 | 7:59 | 49.978
2024-10-08 | 7:59 | 49.982
2024-10-08 | 7:59 | 49.983
2024-10-08 | 7:59 | 49.983
2024-10-08 | 7:59 | 49.986
2024-10-08 | 7:59 | 49.991
2024-10-08 | 7:59 | 49.994
2024-10-08 | 7:59 | 49.994
2024-10-08 | 7:59 | 49.991
2024-10-08 | 7:59 | 49.99
2024-10-08 | 7:59 | 49.99
2024-10-08 | 7:59 | 49.99
2024-10-08 | 7:59 | 49.989
2024-10-08 | 7:59 | 49.987
2024-10-08 | 7:59 | 49.987
2024-10-08 | 7:59 | 49.988
2024-10-08 | 7:59 | 49.988
2024-10-08 | 7:59 | 49.988
2024-10-08 | 7:59 | 49.985
2024-10-08 | 7:59 | 49.985
2024-10-08 | 7:59 | 49.986
2024-10-08 | 7:59 | 49.985
2024-10-08 | 7:59 | 49.983
2024-10-08 | 7:59 | 49.983
2024-10-08 | 7:59 | 49.983
2024-10-08 | 7:59 | 49.987
2024-10-08 | 7:59 | 49.986
2024-10-08 | 7:59 | 49.987
2024-10-08 | 7:59 | 49.99
2024-10-08 | 7:59 | 49.993
2024-10-08 | 7:59 | 49.999
2024-10-08 | 7:59 | 50.005
2024-10-08 | 7:59 | 50.008
2024-10-08 | 7:59 | 50.011
2024-10-08 | 7:59 | 50.014
2024-10-08 | 7:59 | 50.017
2024-10-08 | 7:59 | 50.019
2024-10-08 | 7:59 | 50.02
2024-10-08 | 7:59 | 50.021
2024-10-08 | 7:59 | 50.022
2024-10-08 | 7:59 | 50.024
2024-10-08 | 7:59 | 50.026
2024-10-08 | 7:59 | 50.026
2024-10-08 | 7:59 | 50.025
2024-10-08 | 7:59 | 50.027
2024-10-08 | 7:59 | 50.027
2024-10-08 | 7:59 | 50.025
2024-10-08 | 7:59 | 50.025
2024-10-08 | 7:59 | 50.024
2024-10-08 | 7:59 | 50.025
2024-10-08 | 7:59 | 50.025
2024-10-08 | 7:59 | 50.028
2024-10-08 | 7:59 | 50.028
2024-10-08 | 7:59 | 50.029
2024-10-08 | 7:59 | 50.03
2024-10-08 | 7:59 | 50.031
2024-10-08 | 8:00 | 50.032
2024-10-08 | 8:00 | 50.031
2024-10-08 | 8:00 | 50.031
2024-10-08 | 8:00 | 50.033
2024-10-08 | 8:00 | 50.039
2024-10-08 | 8:00 | 50.041
2024-10-08 | 8:00 | 50.045
2024-10-08 | 8:00 | 50.048
2024-10-08 | 8:00 | 50.053
2024-10-08 | 8:00 | 50.058
2024-10-08 | 8:00 | 50.061
2024-10-08 | 8:00 | 50.065
2024-10-08 | 8:00 | 50.066
2024-10-08 | 8:00 | 50.071
2024-10-08 | 8:00 | 50.074
2024-10-08 | 8:00 | 50.079
2024-10-08 | 8:00 | 50.084
2024-10-08 | 8:00 | 50.09
2024-10-08 | 8:00 | 50.095
2024-10-08 | 8:00 | 50.1
2024-10-08 | 8:00 | 50.101
2024-10-08 | 8:00 | 50.101
2024-10-08 | 8:00 | 50.102
2024-10-08 | 8:00 | 50.102
2024-10-08 | 8:00 | 50.102
2024-10-08 | 8:00 | 50.1
2024-10-08 | 8:00 | 50.102
2024-10-08 | 8:00 | 50.102
2024-10-08 | 8:00 | 50.101
2024-10-08 | 8:00 | 50.097
2024-10-08 | 8:00 | 50.095
2024-10-08 | 8:00 | 50.09
2024-10-08 | 8:00 | 50.084
2024-10-08 | 8:00 | 50.088
2024-10-08 | 8:00 | 50.081
2024-10-08 | 8:00 | 50.079

## 20241010-1
In GMT
Date | Time | Freq
2024-10-10 | 9:14 | 50.115 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-10-10 | 9:14 | 50.116 | 222 | BRITNED | 676.211
2024-10-10 | 9:14 | 50.118 | 268 | WBURB-2 | 428.156
2024-10-10 | 9:14 | 50.117 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-10-10 | 9:14 | 50.116 |  | Viking Link | -648.9
2024-10-10 | 9:14 | 50.116 |  | Viking Link | 1398.96
2024-10-10 | 9:14 | 50.115 | 209 | DRAXX-3 | 626.95
2024-10-10 | 9:14 | 50.117 | 154 | CDCL-1 | 391.57
2024-10-10 | 9:14 | 50.117 | 268 | ROCK-1 | 468.495
2024-10-10 | 9:14 | 50.116 | 148 | IFA Bipole1 | 945.473
2024-10-10 | 9:14 | 50.116 | 132 | IFA Bipole1 | 999.1
2024-10-10 | 9:14 | 50.115 | 141 | IFA Bipole2 | 1000
2024-10-10 | 9:14 | 50.113 | 135 | IFA Bipole1 | 996.75
2024-10-10 | 9:14 | 50.109 |  | Viking Link | -780.3
2024-10-10 | 9:14 | 50.107
2024-10-10 | 9:14 | 50.107
2024-10-10 | 9:14 | 50.11
2024-10-10 | 9:14 | 50.111
2024-10-10 | 9:14 | 50.11
2024-10-10 | 9:14 | 50.109 | 130 | HEYM12 | 271.908
2024-10-10 | 9:14 | 50.109 | 228 | HUMR-1 | 303.75
2024-10-10 | 9:14 | 50.107
2024-10-10 | 9:14 | 50.105
2024-10-10 | 9:14 | 50.105
2024-10-10 | 9:14 | 50.104
2024-10-10 | 9:14 | 50.104
2024-10-10 | 9:14 | 50.108
2024-10-10 | 9:14 | 50.108
2024-10-10 | 9:14 | 50.108
2024-10-10 | 9:14 | 50.11
2024-10-10 | 9:14 | 50.111 | 211 | CDCL-1 | 291.5
2024-10-10 | 9:14 | 50.11 | 199 | STAY-2 | 413.125
2024-10-10 | 9:14 | 50.115 | 173 | CDCL-1 | 397.375
2024-10-10 | 9:14 | 50.113 | 248 | SEAB-2 | 361.25
2024-10-10 | 9:14 | 50.114 | 255 | FRANCE | 995.65
2024-10-10 | 9:14 | 50.117 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-10-10 | 9:14 | 50.117
2024-10-10 | 9:14 | 50.117
2024-10-10 | 9:14 | 50.116
2024-10-10 | 9:14 | 50.118
2024-10-10 | 9:14 | 50.114
2024-10-10 | 9:14 | 50.115
2024-10-10 | 9:14 | 50.111
2024-10-10 | 9:14 | 50.112
2024-10-10 | 9:14 | 50.114
2024-10-10 | 9:14 | 50.113
2024-10-10 | 9:14 | 50.114
2024-10-10 | 9:14 | 50.116
2024-10-10 | 9:14 | 50.117
2024-10-10 | 9:14 | 50.118
2024-10-10 | 9:14 | 50.12
2024-10-10 | 9:14 | 50.12
2024-10-10 | 9:14 | 50.122
2024-10-10 | 9:14 | 50.124
2024-10-10 | 9:14 | 50.121
2024-10-10 | 9:14 | 50.119
2024-10-10 | 9:14 | 50.119
2024-10-10 | 9:14 | 50.119
2024-10-10 | 9:14 | 50.118
2024-10-10 | 9:14 | 50.121
2024-10-10 | 9:14 | 50.12
2024-10-10 | 9:15 | 50.121
2024-10-10 | 9:15 | 50.122
2024-10-10 | 9:15 | 50.125
2024-10-10 | 9:15 | 50.124
2024-10-10 | 9:15 | 50.125
2024-10-10 | 9:15 | 50.124
2024-10-10 | 9:15 | 50.122
2024-10-10 | 9:15 | 50.122
2024-10-10 | 9:15 | 50.12
2024-10-10 | 9:15 | 50.122
2024-10-10 | 9:15 | 50.122
2024-10-10 | 9:15 | 50.121
2024-10-10 | 9:15 | 50.101
2024-10-10 | 9:15 | 50.087
2024-10-10 | 9:15 | 50.082
2024-10-10 | 9:15 | 50.076
2024-10-10 | 9:15 | 50.075
2024-10-10 | 9:15 | 50.075
2024-10-10 | 9:15 | 50.075
2024-10-10 | 9:15 | 50.079
2024-10-10 | 9:15 | 50.079
2024-10-10 | 9:15 | 50.078
2024-10-10 | 9:15 | 50.076
2024-10-10 | 9:15 | 50.075
2024-10-10 | 9:15 | 50.072
2024-10-10 | 9:15 | 50.07
2024-10-10 | 9:15 | 50.067
2024-10-10 | 9:15 | 50.066
2024-10-10 | 9:15 | 50.064
2024-10-10 | 9:15 | 50.061
2024-10-10 | 9:15 | 50.056
2024-10-10 | 9:15 | 50.052
2024-10-10 | 9:15 | 50.05
2024-10-10 | 9:15 | 50.048
2024-10-10 | 9:15 | 50.047
2024-10-10 | 9:15 | 50.046
2024-10-10 | 9:15 | 50.043
2024-10-10 | 9:15 | 50.043
2024-10-10 | 9:15 | 50.039
2024-10-10 | 9:15 | 50.039
2024-10-10 | 9:15 | 50.038
2024-10-10 | 9:15 | 50.036
2024-10-10 | 9:15 | 50.038
2024-10-10 | 9:15 | 50.039
2024-10-10 | 9:15 | 50.04
2024-10-10 | 9:15 | 50.04
2024-10-10 | 9:15 | 50.038
2024-10-10 | 9:15 | 50.042
2024-10-10 | 9:15 | 50.042
2024-10-10 | 9:15 | 50.047
2024-10-10 | 9:15 | 50.046
2024-10-10 | 9:15 | 50.044
2024-10-10 | 9:15 | 50.045
2024-10-10 | 9:15 | 50.045
2024-10-10 | 9:15 | 50.044
2024-10-10 | 9:15 | 50.046
2024-10-10 | 9:15 | 50.047
2024-10-10 | 9:15 | 50.051
2024-10-10 | 9:15 | 50.051
2024-10-10 | 9:16 | 50.048
2024-10-10 | 9:16 | 50.045
2024-10-10 | 9:16 | 50.047
2024-10-10 | 9:16 | 50.046
2024-10-10 | 9:16 | 50.049
2024-10-10 | 9:16 | 50.051
2024-10-10 | 9:16 | 50.052
2024-10-10 | 9:16 | 50.051
2024-10-10 | 9:16 | 50.05
2024-10-10 | 9:16 | 50.05
2024-10-10 | 9:16 | 50.054
2024-10-10 | 9:16 | 50.056
2024-10-10 | 9:16 | 50.056
2024-10-10 | 9:16 | 50.057
2024-10-10 | 9:16 | 50.061
2024-10-10 | 9:16 | 50.062
2024-10-10 | 9:16 | 50.064
2024-10-10 | 9:16 | 50.065
2024-10-10 | 9:16 | 50.067
2024-10-10 | 9:16 | 50.067
2024-10-10 | 9:16 | 50.07
2024-10-10 | 9:16 | 50.068
2024-10-10 | 9:16 | 50.068
2024-10-10 | 9:16 | 50.067
2024-10-10 | 9:16 | 50.063
2024-10-10 | 9:16 | 50.063
2024-10-10 | 9:16 | 50.063
2024-10-10 | 9:16 | 50.063
2024-10-10 | 9:16 | 50.062
2024-10-10 | 9:16 | 50.064
2024-10-10 | 9:16 | 50.066
2024-10-10 | 9:16 | 50.065
2024-10-10 | 9:16 | 50.065
2024-10-10 | 9:16 | 50.065
2024-10-10 | 9:16 | 50.063
2024-10-10 | 9:16 | 50.067
2024-10-10 | 9:16 | 50.072
2024-10-10 | 9:16 | 50.074
2024-10-10 | 9:16 | 50.074
2024-10-10 | 9:16 | 50.075
2024-10-10 | 9:16 | 50.078
2024-10-10 | 9:16 | 50.078
2024-10-10 | 9:16 | 50.081
2024-10-10 | 9:16 | 50.082
2024-10-10 | 9:16 | 50.079
2024-10-10 | 9:16 | 50.075
2024-10-10 | 9:16 | 50.073
2024-10-10 | 9:16 | 50.069
2024-10-10 | 9:16 | 50.067
2024-10-10 | 9:16 | 50.067
2024-10-10 | 9:16 | 50.069
2024-10-10 | 9:16 | 50.072
2024-10-10 | 9:16 | 50.075
2024-10-10 | 9:16 | 50.074
2024-10-10 | 9:16 | 50.074
2024-10-10 | 9:16 | 50.073
2024-10-10 | 9:16 | 50.072
2024-10-10 | 9:16 | 50.073
2024-10-10 | 9:16 | 50.073
2024-10-10 | 9:16 | 50.077
2024-10-10 | 9:16 | 50.076
2024-10-10 | 9:17 | 50.078
2024-10-10 | 9:17 | 50.081
2024-10-10 | 9:17 | 50.082
2024-10-10 | 9:17 | 50.086
2024-10-10 | 9:17 | 50.091
2024-10-10 | 9:17 | 50.089
2024-10-10 | 9:17 | 50.09
2024-10-10 | 9:17 | 50.094
2024-10-10 | 9:17 | 50.093
2024-10-10 | 9:17 | 50.095
2024-10-10 | 9:17 | 50.096
2024-10-10 | 9:17 | 50.094
2024-10-10 | 9:17 | 50.092
2024-10-10 | 9:17 | 50.088
2024-10-10 | 9:17 | 50.087
2024-10-10 | 9:17 | 50.088
2024-10-10 | 9:17 | 50.087
2024-10-10 | 9:17 | 50.088
2024-10-10 | 9:17 | 50.093
2024-10-10 | 9:17 | 50.099
2024-10-10 | 9:17 | 50.104
2024-10-10 | 9:17 | 50.108
2024-10-10 | 9:17 | 50.108
2024-10-10 | 9:17 | 50.108
2024-10-10 | 9:17 | 50.11
2024-10-10 | 9:17 | 50.111
2024-10-10 | 9:17 | 50.111
2024-10-10 | 9:17 | 50.109
2024-10-10 | 9:17 | 50.11
2024-10-10 | 9:17 | 50.114
2024-10-10 | 9:17 | 50.117
2024-10-10 | 9:17 | 50.117
2024-10-10 | 9:17 | 50.118
2024-10-10 | 9:17 | 50.118
2024-10-10 | 9:17 | 50.115
2024-10-10 | 9:17 | 50.113
2024-10-10 | 9:17 | 50.114
2024-10-10 | 9:17 | 50.116
2024-10-10 | 9:17 | 50.12
2024-10-10 | 9:17 | 50.122
2024-10-10 | 9:17 | 50.122
2024-10-10 | 9:17 | 50.121
2024-10-10 | 9:17 | 50.121
2024-10-10 | 9:17 | 50.121
2024-10-10 | 9:17 | 50.122
2024-10-10 | 9:17 | 50.123
2024-10-10 | 9:17 | 50.124
2024-10-10 | 9:17 | 50.125
2024-10-10 | 9:17 | 50.126
2024-10-10 | 9:17 | 50.128
2024-10-10 | 9:17 | 50.128
2024-10-10 | 9:17 | 50.129
2024-10-10 | 9:17 | 50.127
2024-10-10 | 9:17 | 50.126
2024-10-10 | 9:17 | 50.126
2024-10-10 | 9:17 | 50.126
2024-10-10 | 9:17 | 50.126
2024-10-10 | 9:17 | 50.13
2024-10-10 | 9:17 | 50.131
2024-10-10 | 9:18 | 50.132
2024-10-10 | 9:18 | 50.129
2024-10-10 | 9:18 | 50.126
2024-10-10 | 9:18 | 50.125
2024-10-10 | 9:18 | 50.123
2024-10-10 | 9:18 | 50.122
2024-10-10 | 9:18 | 50.122
2024-10-10 | 9:18 | 50.12
2024-10-10 | 9:18 | 50.119
2024-10-10 | 9:18 | 50.117
2024-10-10 | 9:18 | 50.113
2024-10-10 | 9:18 | 50.114
2024-10-10 | 9:18 | 50.116
2024-10-10 | 9:18 | 50.116
2024-10-10 | 9:18 | 50.12
2024-10-10 | 9:18 | 50.12
2024-10-10 | 9:18 | 50.12
2024-10-10 | 9:18 | 50.119
2024-10-10 | 9:18 | 50.116
2024-10-10 | 9:18 | 50.12
2024-10-10 | 9:18 | 50.119
2024-10-10 | 9:18 | 50.121
2024-10-10 | 9:18 | 50.121
2024-10-10 | 9:18 | 50.123
2024-10-10 | 9:18 | 50.122
2024-10-10 | 9:18 | 50.122
2024-10-10 | 9:18 | 50.122
2024-10-10 | 9:18 | 50.122
2024-10-10 | 9:18 | 50.127
2024-10-10 | 9:18 | 50.124
2024-10-10 | 9:18 | 50.127
2024-10-10 | 9:18 | 50.126
2024-10-10 | 9:18 | 50.123
2024-10-10 | 9:18 | 50.124
2024-10-10 | 9:18 | 50.125
2024-10-10 | 9:18 | 50.125
2024-10-10 | 9:18 | 50.127
2024-10-10 | 9:18 | 50.127
2024-10-10 | 9:18 | 50.13
2024-10-10 | 9:18 | 50.13
2024-10-10 | 9:18 | 50.128
2024-10-10 | 9:18 | 50.125
2024-10-10 | 9:18 | 50.123
2024-10-10 | 9:18 | 50.123
2024-10-10 | 9:18 | 50.125
2024-10-10 | 9:18 | 50.123
2024-10-10 | 9:18 | 50.125
2024-10-10 | 9:18 | 50.126
2024-10-10 | 9:18 | 50.127
2024-10-10 | 9:18 | 50.127
2024-10-10 | 9:18 | 50.129
2024-10-10 | 9:18 | 50.128
2024-10-10 | 9:18 | 50.126
2024-10-10 | 9:18 | 50.122
2024-10-10 | 9:18 | 50.12
2024-10-10 | 9:18 | 50.121
2024-10-10 | 9:18 | 50.12
2024-10-10 | 9:18 | 50.12
2024-10-10 | 9:18 | 50.12
2024-10-10 | 9:18 | 50.121
2024-10-10 | 9:18 | 50.12
2024-10-10 | 9:19 | 50.12
2024-10-10 | 9:19 | 50.119
2024-10-10 | 9:19 | 50.118
2024-10-10 | 9:19 | 50.118
2024-10-10 | 9:19 | 50.115
2024-10-10 | 9:19 | 50.116
2024-10-10 | 9:19 | 50.115
2024-10-10 | 9:19 | 50.118
2024-10-10 | 9:19 | 50.118
2024-10-10 | 9:19 | 50.117
2024-10-10 | 9:19 | 50.118
2024-10-10 | 9:19 | 50.119
2024-10-10 | 9:19 | 50.121
2024-10-10 | 9:19 | 50.124
2024-10-10 | 9:19 | 50.123
2024-10-10 | 9:19 | 50.126
2024-10-10 | 9:19 | 50.125
2024-10-10 | 9:19 | 50.129
2024-10-10 | 9:19 | 50.126
2024-10-10 | 9:19 | 50.127
2024-10-10 | 9:19 | 50.124
2024-10-10 | 9:19 | 50.12
2024-10-10 | 9:19 | 50.124
2024-10-10 | 9:19 | 50.122
2024-10-10 | 9:19 | 50.125
2024-10-10 | 9:19 | 50.125
2024-10-10 | 9:19 | 50.127
2024-10-10 | 9:19 | 50.122
2024-10-10 | 9:19 | 50.121
2024-10-10 | 9:19 | 50.122
2024-10-10 | 9:19 | 50.122
2024-10-10 | 9:19 | 50.124
2024-10-10 | 9:19 | 50.123
2024-10-10 | 9:19 | 50.124
2024-10-10 | 9:19 | 50.128
2024-10-10 | 9:19 | 50.129
2024-10-10 | 9:19 | 50.129
2024-10-10 | 9:19 | 50.131
2024-10-10 | 9:19 | 50.133
2024-10-10 | 9:19 | 50.133
2024-10-10 | 9:19 | 50.136
2024-10-10 | 9:19 | 50.135
2024-10-10 | 9:19 | 50.136
2024-10-10 | 9:19 | 50.138
2024-10-10 | 9:19 | 50.135
2024-10-10 | 9:19 | 50.138
2024-10-10 | 9:19 | 50.138
2024-10-10 | 9:19 | 50.137
2024-10-10 | 9:19 | 50.138
2024-10-10 | 9:19 | 50.138
2024-10-10 | 9:19 | 50.134
2024-10-10 | 9:19 | 50.132
2024-10-10 | 9:19 | 50.13
2024-10-10 | 9:19 | 50.129
2024-10-10 | 9:19 | 50.13
2024-10-10 | 9:19 | 50.126
2024-10-10 | 9:19 | 50.128
2024-10-10 | 9:19 | 50.126
2024-10-10 | 9:19 | 50.128
2024-10-10 | 9:20 | 50.128
2024-10-10 | 9:20 | 50.13
2024-10-10 | 9:20 | 50.128
2024-10-10 | 9:20 | 50.129
2024-10-10 | 9:20 | 50.127
2024-10-10 | 9:20 | 50.128
2024-10-10 | 9:20 | 50.127
2024-10-10 | 9:20 | 50.129
2024-10-10 | 9:20 | 50.127
2024-10-10 | 9:20 | 50.127
2024-10-10 | 9:20 | 50.123
2024-10-10 | 9:20 | 50.125
2024-10-10 | 9:20 | 50.121
2024-10-10 | 9:20 | 50.126
2024-10-10 | 9:20 | 50.125
2024-10-10 | 9:20 | 50.126
2024-10-10 | 9:20 | 50.126
2024-10-10 | 9:20 | 50.125
2024-10-10 | 9:20 | 50.128
2024-10-10 | 9:20 | 50.126
2024-10-10 | 9:20 | 50.126
2024-10-10 | 9:20 | 50.122
2024-10-10 | 9:20 | 50.121
2024-10-10 | 9:20 | 50.12
2024-10-10 | 9:20 | 50.122
2024-10-10 | 9:20 | 50.121
2024-10-10 | 9:20 | 50.124
2024-10-10 | 9:20 | 50.125
2024-10-10 | 9:20 | 50.123
2024-10-10 | 9:20 | 50.126
2024-10-10 | 9:20 | 50.126
2024-10-10 | 9:20 | 50.125
2024-10-10 | 9:20 | 50.125
2024-10-10 | 9:20 | 50.124
2024-10-10 | 9:20 | 50.122
2024-10-10 | 9:20 | 50.127
2024-10-10 | 9:20 | 50.131
2024-10-10 | 9:20 | 50.135
2024-10-10 | 9:20 | 50.136
2024-10-10 | 9:20 | 50.133
2024-10-10 | 9:20 | 50.129
2024-10-10 | 9:20 | 50.128
2024-10-10 | 9:20 | 50.128
2024-10-10 | 9:20 | 50.127
2024-10-10 | 9:20 | 50.13
2024-10-10 | 9:20 | 50.131
2024-10-10 | 9:20 | 50.136
2024-10-10 | 9:20 | 50.139
2024-10-10 | 9:20 | 50.142
2024-10-10 | 9:20 | 50.144
2024-10-10 | 9:20 | 50.143
2024-10-10 | 9:20 | 50.144
2024-10-10 | 9:20 | 50.144
2024-10-10 | 9:20 | 50.143
2024-10-10 | 9:20 | 50.147
2024-10-10 | 9:20 | 50.147
2024-10-10 | 9:20 | 50.146
2024-10-10 | 9:20 | 50.147
2024-10-10 | 9:20 | 50.143
2024-10-10 | 9:20 | 50.141
2024-10-10 | 9:20 | 50.142
2024-10-10 | 9:21 | 50.142
2024-10-10 | 9:21 | 50.139
2024-10-10 | 9:21 | 50.137
2024-10-10 | 9:21 | 50.136
2024-10-10 | 9:21 | 50.135
2024-10-10 | 9:21 | 50.134
2024-10-10 | 9:21 | 50.137
2024-10-10 | 9:21 | 50.14
2024-10-10 | 9:21 | 50.141
2024-10-10 | 9:21 | 50.142
2024-10-10 | 9:21 | 50.143
2024-10-10 | 9:21 | 50.142
2024-10-10 | 9:21 | 50.144
2024-10-10 | 9:21 | 50.142
2024-10-10 | 9:21 | 50.144
2024-10-10 | 9:21 | 50.143
2024-10-10 | 9:21 | 50.145
2024-10-10 | 9:21 | 50.149
2024-10-10 | 9:21 | 50.149
2024-10-10 | 9:21 | 50.152
2024-10-10 | 9:21 | 50.157
2024-10-10 | 9:21 | 50.158
2024-10-10 | 9:21 | 50.158
2024-10-10 | 9:21 | 50.159
2024-10-10 | 9:21 | 50.162
2024-10-10 | 9:21 | 50.16
2024-10-10 | 9:21 | 50.158
2024-10-10 | 9:21 | 50.159
2024-10-10 | 9:21 | 50.158
2024-10-10 | 9:21 | 50.157
2024-10-10 | 9:21 | 50.156
2024-10-10 | 9:21 | 50.156
2024-10-10 | 9:21 | 50.156
2024-10-10 | 9:21 | 50.159
2024-10-10 | 9:21 | 50.159
2024-10-10 | 9:21 | 50.159
2024-10-10 | 9:21 | 50.158
2024-10-10 | 9:21 | 50.159
2024-10-10 | 9:21 | 50.161
2024-10-10 | 9:21 | 50.161
2024-10-10 | 9:21 | 50.164
2024-10-10 | 9:21 | 50.163
2024-10-10 | 9:21 | 50.163
2024-10-10 | 9:21 | 50.164
2024-10-10 | 9:21 | 50.161
2024-10-10 | 9:21 | 50.157
2024-10-10 | 9:21 | 50.157
2024-10-10 | 9:21 | 50.159
2024-10-10 | 9:21 | 50.16
2024-10-10 | 9:21 | 50.163
2024-10-10 | 9:21 | 50.163
2024-10-10 | 9:21 | 50.162
2024-10-10 | 9:21 | 50.164
2024-10-10 | 9:21 | 50.167
2024-10-10 | 9:21 | 50.17
2024-10-10 | 9:21 | 50.168
2024-10-10 | 9:21 | 50.167
2024-10-10 | 9:21 | 50.168
2024-10-10 | 9:21 | 50.171
2024-10-10 | 9:22 | 50.173
2024-10-10 | 9:22 | 50.174
2024-10-10 | 9:22 | 50.173
2024-10-10 | 9:22 | 50.173
2024-10-10 | 9:22 | 50.175
2024-10-10 | 9:22 | 50.176
2024-10-10 | 9:22 | 50.175
2024-10-10 | 9:22 | 50.175
2024-10-10 | 9:22 | 50.178
2024-10-10 | 9:22 | 50.182
2024-10-10 | 9:22 | 50.183
2024-10-10 | 9:22 | 50.184
2024-10-10 | 9:22 | 50.185
2024-10-10 | 9:22 | 50.185
2024-10-10 | 9:22 | 50.185
2024-10-10 | 9:22 | 50.184
2024-10-10 | 9:22 | 50.184
2024-10-10 | 9:22 | 50.185
2024-10-10 | 9:22 | 50.184
2024-10-10 | 9:22 | 50.186
2024-10-10 | 9:22 | 50.187
2024-10-10 | 9:22 | 50.185
2024-10-10 | 9:22 | 50.181
2024-10-10 | 9:22 | 50.183
2024-10-10 | 9:22 | 50.182
2024-10-10 | 9:22 | 50.186
2024-10-10 | 9:22 | 50.183
2024-10-10 | 9:22 | 50.184
2024-10-10 | 9:22 | 50.182
2024-10-10 | 9:22 | 50.185
2024-10-10 | 9:22 | 50.181
2024-10-10 | 9:22 | 50.175
2024-10-10 | 9:22 | 50.171
2024-10-10 | 9:22 | 50.165
2024-10-10 | 9:22 | 50.166
2024-10-10 | 9:22 | 50.167
2024-10-10 | 9:22 | 50.167
2024-10-10 | 9:22 | 50.17
2024-10-10 | 9:22 | 50.17
2024-10-10 | 9:22 | 50.171
2024-10-10 | 9:22 | 50.17
2024-10-10 | 9:22 | 50.166
2024-10-10 | 9:22 | 50.165
2024-10-10 | 9:22 | 50.166
2024-10-10 | 9:22 | 50.163
2024-10-10 | 9:22 | 50.162
2024-10-10 | 9:22 | 50.163
2024-10-10 | 9:22 | 50.167
2024-10-10 | 9:22 | 50.165
2024-10-10 | 9:22 | 50.163
2024-10-10 | 9:22 | 50.163
2024-10-10 | 9:22 | 50.162
2024-10-10 | 9:22 | 50.162
2024-10-10 | 9:22 | 50.161
2024-10-10 | 9:22 | 50.158
2024-10-10 | 9:22 | 50.155
2024-10-10 | 9:22 | 50.155
2024-10-10 | 9:22 | 50.154
2024-10-10 | 9:22 | 50.151
2024-10-10 | 9:22 | 50.149
2024-10-10 | 9:22 | 50.149
2024-10-10 | 9:23 | 50.15
2024-10-10 | 9:23 | 50.15
2024-10-10 | 9:23 | 50.152
2024-10-10 | 9:23 | 50.154
2024-10-10 | 9:23 | 50.156
2024-10-10 | 9:23 | 50.158
2024-10-10 | 9:23 | 50.16
2024-10-10 | 9:23 | 50.162
2024-10-10 | 9:23 | 50.164
2024-10-10 | 9:23 | 50.163
2024-10-10 | 9:23 | 50.16
2024-10-10 | 9:23 | 50.158
2024-10-10 | 9:23 | 50.155
2024-10-10 | 9:23 | 50.156
2024-10-10 | 9:23 | 50.155
2024-10-10 | 9:23 | 50.158
2024-10-10 | 9:23 | 50.16
2024-10-10 | 9:23 | 50.161
2024-10-10 | 9:23 | 50.161
2024-10-10 | 9:23 | 50.161
2024-10-10 | 9:23 | 50.162
2024-10-10 | 9:23 | 50.164
2024-10-10 | 9:23 | 50.164
2024-10-10 | 9:23 | 50.161
2024-10-10 | 9:23 | 50.16
2024-10-10 | 9:23 | 50.161
2024-10-10 | 9:23 | 50.161
2024-10-10 | 9:23 | 50.16
2024-10-10 | 9:23 | 50.157
2024-10-10 | 9:23 | 50.155
2024-10-10 | 9:23 | 50.153
2024-10-10 | 9:23 | 50.154
2024-10-10 | 9:23 | 50.157
2024-10-10 | 9:23 | 50.157
2024-10-10 | 9:23 | 50.159
2024-10-10 | 9:23 | 50.16
2024-10-10 | 9:23 | 50.158
2024-10-10 | 9:23 | 50.156
2024-10-10 | 9:23 | 50.154
2024-10-10 | 9:23 | 50.153
2024-10-10 | 9:23 | 50.153
2024-10-10 | 9:23 | 50.153
2024-10-10 | 9:23 | 50.154
2024-10-10 | 9:23 | 50.155
2024-10-10 | 9:23 | 50.157
2024-10-10 | 9:23 | 50.155
2024-10-10 | 9:23 | 50.155
2024-10-10 | 9:23 | 50.155
2024-10-10 | 9:23 | 50.155
2024-10-10 | 9:23 | 50.154
2024-10-10 | 9:23 | 50.153
2024-10-10 | 9:23 | 50.155
2024-10-10 | 9:23 | 50.156
2024-10-10 | 9:23 | 50.157
2024-10-10 | 9:23 | 50.161
2024-10-10 | 9:23 | 50.165
2024-10-10 | 9:23 | 50.17
2024-10-10 | 9:23 | 50.171
2024-10-10 | 9:23 | 50.169
2024-10-10 | 9:24 | 50.167

## 20241013-1
In GMT
Date | Time | Freq
2024-10-13 | 12:02 | 50.124 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-10-13 | 12:02 | 50.117 | 222 | BRITNED | 676.211
2024-10-13 | 12:02 | 50.108 | 268 | WBURB-2 | 428.156
2024-10-13 | 12:02 | 50.104 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-10-13 | 12:02 | 50.102 |  | Viking Link | -648.9
2024-10-13 | 12:02 | 50.099 |  | Viking Link | 1398.96
2024-10-13 | 12:02 | 50.098 | 209 | DRAXX-3 | 626.95
2024-10-13 | 12:02 | 50.101 | 154 | CDCL-1 | 391.57
2024-10-13 | 12:02 | 50.107 | 268 | ROCK-1 | 468.495
2024-10-13 | 12:02 | 50.112 | 148 | IFA Bipole1 | 945.473
2024-10-13 | 12:02 | 50.117 | 132 | IFA Bipole1 | 999.1
2024-10-13 | 12:02 | 50.12 | 141 | IFA Bipole2 | 1000
2024-10-13 | 12:02 | 50.122 | 135 | IFA Bipole1 | 996.75
2024-10-13 | 12:02 | 50.122 |  | Viking Link | -780.3
2024-10-13 | 12:02 | 50.126
2024-10-13 | 12:02 | 50.128
2024-10-13 | 12:02 | 50.127
2024-10-13 | 12:02 | 50.126
2024-10-13 | 12:02 | 50.126
2024-10-13 | 12:02 | 50.127 | 130 | HEYM12 | 271.908
2024-10-13 | 12:02 | 50.126 | 228 | HUMR-1 | 303.75
2024-10-13 | 12:02 | 50.128
2024-10-13 | 12:02 | 50.13
2024-10-13 | 12:02 | 50.129
2024-10-13 | 12:02 | 50.128
2024-10-13 | 12:02 | 50.129
2024-10-13 | 12:02 | 50.129
2024-10-13 | 12:02 | 50.13
2024-10-13 | 12:02 | 50.129
2024-10-13 | 12:02 | 50.128
2024-10-13 | 12:02 | 50.126 | 211 | CDCL-1 | 291.5
2024-10-13 | 12:03 | 50.125 | 199 | STAY-2 | 413.125
2024-10-13 | 12:03 | 50.125 | 173 | CDCL-1 | 397.375
2024-10-13 | 12:03 | 50.125 | 248 | SEAB-2 | 361.25
2024-10-13 | 12:03 | 50.125 | 255 | FRANCE | 995.65
2024-10-13 | 12:03 | 50.125 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-10-13 | 12:03 | 50.124
2024-10-13 | 12:03 | 50.123
2024-10-13 | 12:03 | 50.123
2024-10-13 | 12:03 | 50.124
2024-10-13 | 12:03 | 50.125
2024-10-13 | 12:03 | 50.125
2024-10-13 | 12:03 | 50.123
2024-10-13 | 12:03 | 50.124
2024-10-13 | 12:03 | 50.123
2024-10-13 | 12:03 | 50.122
2024-10-13 | 12:03 | 50.122
2024-10-13 | 12:03 | 50.123
2024-10-13 | 12:03 | 50.121
2024-10-13 | 12:03 | 50.12
2024-10-13 | 12:03 | 50.119
2024-10-13 | 12:03 | 50.12
2024-10-13 | 12:03 | 50.119
2024-10-13 | 12:03 | 50.123
2024-10-13 | 12:03 | 50.123
2024-10-13 | 12:03 | 50.126
2024-10-13 | 12:03 | 50.128
2024-10-13 | 12:03 | 50.128
2024-10-13 | 12:03 | 50.128
2024-10-13 | 12:03 | 50.126
2024-10-13 | 12:03 | 50.126
2024-10-13 | 12:03 | 50.125
2024-10-13 | 12:03 | 50.122
2024-10-13 | 12:03 | 50.124
2024-10-13 | 12:03 | 50.12
2024-10-13 | 12:03 | 50.121
2024-10-13 | 12:03 | 50.117
2024-10-13 | 12:03 | 50.113
2024-10-13 | 12:03 | 50.111
2024-10-13 | 12:03 | 50.108
2024-10-13 | 12:03 | 50.106
2024-10-13 | 12:03 | 50.104
2024-10-13 | 12:03 | 50.104
2024-10-13 | 12:03 | 50.103
2024-10-13 | 12:03 | 50.102
2024-10-13 | 12:03 | 50.102
2024-10-13 | 12:03 | 50.101
2024-10-13 | 12:03 | 50.1
2024-10-13 | 12:03 | 50.1
2024-10-13 | 12:03 | 50.099
2024-10-13 | 12:03 | 50.099
2024-10-13 | 12:03 | 50.102
2024-10-13 | 12:03 | 50.104
2024-10-13 | 12:03 | 50.105
2024-10-13 | 12:03 | 50.106
2024-10-13 | 12:03 | 50.106
2024-10-13 | 12:03 | 50.108
2024-10-13 | 12:03 | 50.107
2024-10-13 | 12:03 | 50.108
2024-10-13 | 12:03 | 50.107
2024-10-13 | 12:04 | 50.107
2024-10-13 | 12:04 | 50.106
2024-10-13 | 12:04 | 50.107
2024-10-13 | 12:04 | 50.105
2024-10-13 | 12:04 | 50.104
2024-10-13 | 12:04 | 50.105
2024-10-13 | 12:04 | 50.105
2024-10-13 | 12:04 | 50.103
2024-10-13 | 12:04 | 50.105
2024-10-13 | 12:04 | 50.101
2024-10-13 | 12:04 | 50.055
2024-10-13 | 12:04 | 50.021
2024-10-13 | 12:04 | 50.009
2024-10-13 | 12:04 | 49.993
2024-10-13 | 12:04 | 49.981
2024-10-13 | 12:04 | 49.972
2024-10-13 | 12:04 | 49.962
2024-10-13 | 12:04 | 49.957
2024-10-13 | 12:04 | 49.955
2024-10-13 | 12:04 | 49.955
2024-10-13 | 12:04 | 49.955
2024-10-13 | 12:04 | 49.955
2024-10-13 | 12:04 | 49.956
2024-10-13 | 12:04 | 49.959
2024-10-13 | 12:04 | 49.961
2024-10-13 | 12:04 | 49.962
2024-10-13 | 12:04 | 49.961
2024-10-13 | 12:04 | 49.962
2024-10-13 | 12:04 | 49.961
2024-10-13 | 12:04 | 49.962
2024-10-13 | 12:04 | 49.961
2024-10-13 | 12:04 | 49.959
2024-10-13 | 12:04 | 49.958
2024-10-13 | 12:04 | 49.956
2024-10-13 | 12:04 | 49.956
2024-10-13 | 12:04 | 49.956
2024-10-13 | 12:04 | 49.958
2024-10-13 | 12:04 | 49.958
2024-10-13 | 12:04 | 49.958
2024-10-13 | 12:04 | 49.959
2024-10-13 | 12:04 | 49.958
2024-10-13 | 12:04 | 49.956
2024-10-13 | 12:04 | 49.956
2024-10-13 | 12:04 | 49.955
2024-10-13 | 12:04 | 49.954
2024-10-13 | 12:04 | 49.955
2024-10-13 | 12:04 | 49.953
2024-10-13 | 12:04 | 49.952
2024-10-13 | 12:04 | 49.954
2024-10-13 | 12:04 | 49.955
2024-10-13 | 12:04 | 49.953
2024-10-13 | 12:04 | 49.951
2024-10-13 | 12:04 | 49.951
2024-10-13 | 12:04 | 49.951
2024-10-13 | 12:04 | 49.952
2024-10-13 | 12:04 | 49.95
2024-10-13 | 12:04 | 49.951
2024-10-13 | 12:04 | 49.95
2024-10-13 | 12:04 | 49.948
2024-10-13 | 12:04 | 49.947
2024-10-13 | 12:05 | 49.947
2024-10-13 | 12:05 | 49.946
2024-10-13 | 12:05 | 49.946
2024-10-13 | 12:05 | 49.947
2024-10-13 | 12:05 | 49.947
2024-10-13 | 12:05 | 49.948
2024-10-13 | 12:05 | 49.95
2024-10-13 | 12:05 | 49.949
2024-10-13 | 12:05 | 49.951
2024-10-13 | 12:05 | 49.949
2024-10-13 | 12:05 | 49.949
2024-10-13 | 12:05 | 49.947
2024-10-13 | 12:05 | 49.945
2024-10-13 | 12:05 | 49.944
2024-10-13 | 12:05 | 49.942
2024-10-13 | 12:05 | 49.939
2024-10-13 | 12:05 | 49.938
2024-10-13 | 12:05 | 49.933
2024-10-13 | 12:05 | 49.931
2024-10-13 | 12:05 | 49.93
2024-10-13 | 12:05 | 49.93
2024-10-13 | 12:05 | 49.927
2024-10-13 | 12:05 | 49.926
2024-10-13 | 12:05 | 49.928
2024-10-13 | 12:05 | 49.927
2024-10-13 | 12:05 | 49.928
2024-10-13 | 12:05 | 49.934
2024-10-13 | 12:05 | 49.936
2024-10-13 | 12:05 | 49.939
2024-10-13 | 12:05 | 49.942
2024-10-13 | 12:05 | 49.947
2024-10-13 | 12:05 | 49.947
2024-10-13 | 12:05 | 49.948
2024-10-13 | 12:05 | 49.946
2024-10-13 | 12:05 | 49.942
2024-10-13 | 12:05 | 49.942
2024-10-13 | 12:05 | 49.939
2024-10-13 | 12:05 | 49.939
2024-10-13 | 12:05 | 49.939
2024-10-13 | 12:05 | 49.937
2024-10-13 | 12:05 | 49.938
2024-10-13 | 12:05 | 49.935
2024-10-13 | 12:05 | 49.935
2024-10-13 | 12:05 | 49.933
2024-10-13 | 12:05 | 49.937
2024-10-13 | 12:05 | 49.936
2024-10-13 | 12:05 | 49.938
2024-10-13 | 12:05 | 49.937
2024-10-13 | 12:05 | 49.938
2024-10-13 | 12:05 | 49.936
2024-10-13 | 12:05 | 49.937
2024-10-13 | 12:05 | 49.935
2024-10-13 | 12:05 | 49.934
2024-10-13 | 12:05 | 49.934
2024-10-13 | 12:05 | 49.937
2024-10-13 | 12:05 | 49.938
2024-10-13 | 12:05 | 49.938
2024-10-13 | 12:05 | 49.941
2024-10-13 | 12:05 | 49.942
2024-10-13 | 12:05 | 49.946
2024-10-13 | 12:06 | 49.947
2024-10-13 | 12:06 | 49.949
2024-10-13 | 12:06 | 49.949
2024-10-13 | 12:06 | 49.954
2024-10-13 | 12:06 | 49.955
2024-10-13 | 12:06 | 49.957
2024-10-13 | 12:06 | 49.962
2024-10-13 | 12:06 | 49.962
2024-10-13 | 12:06 | 49.965
2024-10-13 | 12:06 | 49.965
2024-10-13 | 12:06 | 49.963
2024-10-13 | 12:06 | 49.962
2024-10-13 | 12:06 | 49.965
2024-10-13 | 12:06 | 49.962
2024-10-13 | 12:06 | 49.962
2024-10-13 | 12:06 | 49.966
2024-10-13 | 12:06 | 49.964
2024-10-13 | 12:06 | 49.963
2024-10-13 | 12:06 | 49.965
2024-10-13 | 12:06 | 49.963
2024-10-13 | 12:06 | 49.962
2024-10-13 | 12:06 | 49.963
2024-10-13 | 12:06 | 49.962
2024-10-13 | 12:06 | 49.962
2024-10-13 | 12:06 | 49.961
2024-10-13 | 12:06 | 49.959
2024-10-13 | 12:06 | 49.961
2024-10-13 | 12:06 | 49.957
2024-10-13 | 12:06 | 49.96
2024-10-13 | 12:06 | 49.96
2024-10-13 | 12:06 | 49.959
2024-10-13 | 12:06 | 49.958
2024-10-13 | 12:06 | 49.955
2024-10-13 | 12:06 | 49.955
2024-10-13 | 12:06 | 49.952
2024-10-13 | 12:06 | 49.953
2024-10-13 | 12:06 | 49.95
2024-10-13 | 12:06 | 49.949
2024-10-13 | 12:06 | 49.951
2024-10-13 | 12:06 | 49.953
2024-10-13 | 12:06 | 49.954
2024-10-13 | 12:06 | 49.958
2024-10-13 | 12:06 | 49.959
2024-10-13 | 12:06 | 49.961
2024-10-13 | 12:06 | 49.964
2024-10-13 | 12:06 | 49.962
2024-10-13 | 12:06 | 49.962
2024-10-13 | 12:06 | 49.962
2024-10-13 | 12:06 | 49.963
2024-10-13 | 12:06 | 49.963
2024-10-13 | 12:06 | 49.962
2024-10-13 | 12:06 | 49.961
2024-10-13 | 12:06 | 49.962
2024-10-13 | 12:06 | 49.962
2024-10-13 | 12:06 | 49.962
2024-10-13 | 12:06 | 49.96
2024-10-13 | 12:06 | 49.962
2024-10-13 | 12:06 | 49.965
2024-10-13 | 12:06 | 49.969
2024-10-13 | 12:06 | 49.973
2024-10-13 | 12:07 | 49.976
2024-10-13 | 12:07 | 49.977
2024-10-13 | 12:07 | 49.982
2024-10-13 | 12:07 | 49.986
2024-10-13 | 12:07 | 49.985
2024-10-13 | 12:07 | 49.989
2024-10-13 | 12:07 | 49.985
2024-10-13 | 12:07 | 49.986
2024-10-13 | 12:07 | 49.982
2024-10-13 | 12:07 | 49.982
2024-10-13 | 12:07 | 49.98
2024-10-13 | 12:07 | 49.981
2024-10-13 | 12:07 | 49.978
2024-10-13 | 12:07 | 49.978
2024-10-13 | 12:07 | 49.973
2024-10-13 | 12:07 | 49.976
2024-10-13 | 12:07 | 49.973
2024-10-13 | 12:07 | 49.973
2024-10-13 | 12:07 | 49.973
2024-10-13 | 12:07 | 49.971
2024-10-13 | 12:07 | 49.972
2024-10-13 | 12:07 | 49.97
2024-10-13 | 12:07 | 49.972
2024-10-13 | 12:07 | 49.976
2024-10-13 | 12:07 | 49.975
2024-10-13 | 12:07 | 49.977
2024-10-13 | 12:07 | 49.98
2024-10-13 | 12:07 | 49.979
2024-10-13 | 12:07 | 49.977
2024-10-13 | 12:07 | 49.978
2024-10-13 | 12:07 | 49.98
2024-10-13 | 12:07 | 49.98
2024-10-13 | 12:07 | 49.981
2024-10-13 | 12:07 | 49.98
2024-10-13 | 12:07 | 49.981
2024-10-13 | 12:07 | 49.982
2024-10-13 | 12:07 | 49.984
2024-10-13 | 12:07 | 49.984
2024-10-13 | 12:07 | 49.985
2024-10-13 | 12:07 | 49.983
2024-10-13 | 12:07 | 49.981
2024-10-13 | 12:07 | 49.984
2024-10-13 | 12:07 | 49.984
2024-10-13 | 12:07 | 49.984
2024-10-13 | 12:07 | 49.988
2024-10-13 | 12:07 | 49.988
2024-10-13 | 12:07 | 49.991
2024-10-13 | 12:07 | 49.996
2024-10-13 | 12:07 | 49.998
2024-10-13 | 12:07 | 50.001
2024-10-13 | 12:07 | 50.004
2024-10-13 | 12:07 | 50.005
2024-10-13 | 12:07 | 50.009
2024-10-13 | 12:07 | 50.011
2024-10-13 | 12:07 | 50.012
2024-10-13 | 12:07 | 50.015
2024-10-13 | 12:07 | 50.015
2024-10-13 | 12:07 | 50.012
2024-10-13 | 12:07 | 50.011
2024-10-13 | 12:07 | 50.009
2024-10-13 | 12:07 | 50.013
2024-10-13 | 12:08 | 50.014
2024-10-13 | 12:08 | 50.014
2024-10-13 | 12:08 | 50.017
2024-10-13 | 12:08 | 50.019
2024-10-13 | 12:08 | 50.021
2024-10-13 | 12:08 | 50.024
2024-10-13 | 12:08 | 50.023
2024-10-13 | 12:08 | 50.022
2024-10-13 | 12:08 | 50.024
2024-10-13 | 12:08 | 50.023
2024-10-13 | 12:08 | 50.021
2024-10-13 | 12:08 | 50.021
2024-10-13 | 12:08 | 50.021
2024-10-13 | 12:08 | 50.019
2024-10-13 | 12:08 | 50.021
2024-10-13 | 12:08 | 50.02
2024-10-13 | 12:08 | 50.018
2024-10-13 | 12:08 | 50.016
2024-10-13 | 12:08 | 50.015
2024-10-13 | 12:08 | 50.016
2024-10-13 | 12:08 | 50.017
2024-10-13 | 12:08 | 50.021
2024-10-13 | 12:08 | 50.022
2024-10-13 | 12:08 | 50.022
2024-10-13 | 12:08 | 50.022
2024-10-13 | 12:08 | 50.02
2024-10-13 | 12:08 | 50.02
2024-10-13 | 12:08 | 50.019
2024-10-13 | 12:08 | 50.018
2024-10-13 | 12:08 | 50.015
2024-10-13 | 12:08 | 50.015
2024-10-13 | 12:08 | 50.013
2024-10-13 | 12:08 | 50.011
2024-10-13 | 12:08 | 50.014
2024-10-13 | 12:08 | 50.013
2024-10-13 | 12:08 | 50.015
2024-10-13 | 12:08 | 50.015
2024-10-13 | 12:08 | 50.015
2024-10-13 | 12:08 | 50.018
2024-10-13 | 12:08 | 50.02
2024-10-13 | 12:08 | 50.02
2024-10-13 | 12:08 | 50.024
2024-10-13 | 12:08 | 50.026
2024-10-13 | 12:08 | 50.029
2024-10-13 | 12:08 | 50.036
2024-10-13 | 12:08 | 50.037
2024-10-13 | 12:08 | 50.042
2024-10-13 | 12:08 | 50.043
2024-10-13 | 12:08 | 50.041
2024-10-13 | 12:08 | 50.042
2024-10-13 | 12:08 | 50.041
2024-10-13 | 12:08 | 50.039
2024-10-13 | 12:08 | 50.038
2024-10-13 | 12:08 | 50.038
2024-10-13 | 12:08 | 50.036
2024-10-13 | 12:08 | 50.035
2024-10-13 | 12:08 | 50.035
2024-10-13 | 12:08 | 50.036
2024-10-13 | 12:08 | 50.036
2024-10-13 | 12:09 | 50.036
2024-10-13 | 12:09 | 50.036
2024-10-13 | 12:09 | 50.036
2024-10-13 | 12:09 | 50.038
2024-10-13 | 12:09 | 50.04
2024-10-13 | 12:09 | 50.04
2024-10-13 | 12:09 | 50.037
2024-10-13 | 12:09 | 50.036
2024-10-13 | 12:09 | 50.034
2024-10-13 | 12:09 | 50.032
2024-10-13 | 12:09 | 50.031
2024-10-13 | 12:09 | 50.03
2024-10-13 | 12:09 | 50.028
2024-10-13 | 12:09 | 50.028
2024-10-13 | 12:09 | 50.028
2024-10-13 | 12:09 | 50.029
2024-10-13 | 12:09 | 50.028
2024-10-13 | 12:09 | 50.027
2024-10-13 | 12:09 | 50.026
2024-10-13 | 12:09 | 50.028
2024-10-13 | 12:09 | 50.025
2024-10-13 | 12:09 | 50.024
2024-10-13 | 12:09 | 50.026
2024-10-13 | 12:09 | 50.025
2024-10-13 | 12:09 | 50.025
2024-10-13 | 12:09 | 50.026
2024-10-13 | 12:09 | 50.026
2024-10-13 | 12:09 | 50.025
2024-10-13 | 12:09 | 50.025
2024-10-13 | 12:09 | 50.026
2024-10-13 | 12:09 | 50.028

## 20241017-1
In GMT
Date | Time | Freq
2024-10-17 | 17:10 | 50.017 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-10-17 | 17:10 | 50.01 | 222 | BRITNED | 676.211
2024-10-17 | 17:10 | 50.009 | 268 | WBURB-2 | 428.156
2024-10-17 | 17:10 | 50.005 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-10-17 | 17:10 | 50.002 |  | Viking Link | -648.9
2024-10-17 | 17:10 | 50.003 |  | Viking Link | 1398.96
2024-10-17 | 17:10 | 49.996 | 209 | DRAXX-3 | 626.95
2024-10-17 | 17:10 | 49.996 | 154 | CDCL-1 | 391.57
2024-10-17 | 17:10 | 49.991 | 268 | ROCK-1 | 468.495
2024-10-17 | 17:10 | 49.99 | 148 | IFA Bipole1 | 945.473
2024-10-17 | 17:10 | 49.99 | 132 | IFA Bipole1 | 999.1
2024-10-17 | 17:10 | 49.988 | 141 | IFA Bipole2 | 1000
2024-10-17 | 17:10 | 49.988 | 135 | IFA Bipole1 | 996.75
2024-10-17 | 17:10 | 49.987 |  | Viking Link | -780.3
2024-10-17 | 17:10 | 49.992
2024-10-17 | 17:10 | 49.994
2024-10-17 | 17:10 | 50.002
2024-10-17 | 17:10 | 50.005
2024-10-17 | 17:10 | 50.012
2024-10-17 | 17:10 | 50.015 | 130 | HEYM12 | 271.908
2024-10-17 | 17:10 | 50.018 | 228 | HUMR-1 | 303.75
2024-10-17 | 17:10 | 50.022
2024-10-17 | 17:10 | 50.024
2024-10-17 | 17:10 | 50.023
2024-10-17 | 17:10 | 50.025
2024-10-17 | 17:10 | 50.023
2024-10-17 | 17:10 | 50.021
2024-10-17 | 17:10 | 50.023
2024-10-17 | 17:10 | 50.024
2024-10-17 | 17:10 | 50.022
2024-10-17 | 17:10 | 50.025 | 211 | CDCL-1 | 291.5
2024-10-17 | 17:11 | 50.028 | 199 | STAY-2 | 413.125
2024-10-17 | 17:11 | 50.03 | 173 | CDCL-1 | 397.375
2024-10-17 | 17:11 | 50.031 | 248 | SEAB-2 | 361.25
2024-10-17 | 17:11 | 50.033 | 255 | FRANCE | 995.65
2024-10-17 | 17:11 | 50.036 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-10-17 | 17:11 | 50.037
2024-10-17 | 17:11 | 50.037
2024-10-17 | 17:11 | 50.04
2024-10-17 | 17:11 | 50.039
2024-10-17 | 17:11 | 50.036
2024-10-17 | 17:11 | 50.033
2024-10-17 | 17:11 | 50.031
2024-10-17 | 17:11 | 50.03
2024-10-17 | 17:11 | 50.028
2024-10-17 | 17:11 | 50.027
2024-10-17 | 17:11 | 50.031
2024-10-17 | 17:11 | 50.029
2024-10-17 | 17:11 | 50.029
2024-10-17 | 17:11 | 50.031
2024-10-17 | 17:11 | 50.027
2024-10-17 | 17:11 | 50.027
2024-10-17 | 17:11 | 50.028
2024-10-17 | 17:11 | 50.024
2024-10-17 | 17:11 | 50.022
2024-10-17 | 17:11 | 50.021
2024-10-17 | 17:11 | 50.016
2024-10-17 | 17:11 | 50.015
2024-10-17 | 17:11 | 50.017
2024-10-17 | 17:11 | 50.017
2024-10-17 | 17:11 | 50.018
2024-10-17 | 17:11 | 50.021
2024-10-17 | 17:11 | 50.025
2024-10-17 | 17:11 | 50.027
2024-10-17 | 17:11 | 50.029
2024-10-17 | 17:11 | 50.03
2024-10-17 | 17:11 | 50.029
2024-10-17 | 17:11 | 50.029
2024-10-17 | 17:11 | 50.028
2024-10-17 | 17:11 | 50.026
2024-10-17 | 17:11 | 50.025
2024-10-17 | 17:11 | 50.023
2024-10-17 | 17:11 | 50.023
2024-10-17 | 17:11 | 50.023
2024-10-17 | 17:11 | 50.003
2024-10-17 | 17:11 | 49.99
2024-10-17 | 17:11 | 49.977
2024-10-17 | 17:11 | 49.967
2024-10-17 | 17:11 | 49.965
2024-10-17 | 17:11 | 49.964
2024-10-17 | 17:11 | 49.962
2024-10-17 | 17:11 | 49.96
2024-10-17 | 17:11 | 49.958
2024-10-17 | 17:11 | 49.956
2024-10-17 | 17:11 | 49.952
2024-10-17 | 17:11 | 49.946
2024-10-17 | 17:11 | 49.941
2024-10-17 | 17:11 | 49.936
2024-10-17 | 17:11 | 49.935
2024-10-17 | 17:11 | 49.934
2024-10-17 | 17:11 | 49.931
2024-10-17 | 17:12 | 49.929
2024-10-17 | 17:12 | 49.931
2024-10-17 | 17:12 | 49.93
2024-10-17 | 17:12 | 49.928
2024-10-17 | 17:12 | 49.924
2024-10-17 | 17:12 | 49.925
2024-10-17 | 17:12 | 49.927
2024-10-17 | 17:12 | 49.925
2024-10-17 | 17:12 | 49.923
2024-10-17 | 17:12 | 49.926
2024-10-17 | 17:12 | 49.928
2024-10-17 | 17:12 | 49.928
2024-10-17 | 17:12 | 49.929
2024-10-17 | 17:12 | 49.934
2024-10-17 | 17:12 | 49.936
2024-10-17 | 17:12 | 49.932
2024-10-17 | 17:12 | 49.931
2024-10-17 | 17:12 | 49.929
2024-10-17 | 17:12 | 49.929
2024-10-17 | 17:12 | 49.93
2024-10-17 | 17:12 | 49.93
2024-10-17 | 17:12 | 49.929
2024-10-17 | 17:12 | 49.928
2024-10-17 | 17:12 | 49.928
2024-10-17 | 17:12 | 49.926
2024-10-17 | 17:12 | 49.925
2024-10-17 | 17:12 | 49.925
2024-10-17 | 17:12 | 49.923
2024-10-17 | 17:12 | 49.92
2024-10-17 | 17:12 | 49.917
2024-10-17 | 17:12 | 49.915
2024-10-17 | 17:12 | 49.912
2024-10-17 | 17:12 | 49.913
2024-10-17 | 17:12 | 49.914
2024-10-17 | 17:12 | 49.916
2024-10-17 | 17:12 | 49.918
2024-10-17 | 17:12 | 49.922
2024-10-17 | 17:12 | 49.922
2024-10-17 | 17:12 | 49.922
2024-10-17 | 17:12 | 49.919
2024-10-17 | 17:12 | 49.917
2024-10-17 | 17:12 | 49.917
2024-10-17 | 17:12 | 49.913
2024-10-17 | 17:12 | 49.912
2024-10-17 | 17:12 | 49.91
2024-10-17 | 17:12 | 49.907
2024-10-17 | 17:12 | 49.906
2024-10-17 | 17:12 | 49.904
2024-10-17 | 17:12 | 49.904
2024-10-17 | 17:12 | 49.903
2024-10-17 | 17:12 | 49.903
2024-10-17 | 17:12 | 49.904
2024-10-17 | 17:12 | 49.905
2024-10-17 | 17:12 | 49.907
2024-10-17 | 17:12 | 49.907
2024-10-17 | 17:12 | 49.907
2024-10-17 | 17:12 | 49.908
2024-10-17 | 17:12 | 49.908
2024-10-17 | 17:12 | 49.909
2024-10-17 | 17:12 | 49.911
2024-10-17 | 17:13 | 49.911
2024-10-17 | 17:13 | 49.91
2024-10-17 | 17:13 | 49.909
2024-10-17 | 17:13 | 49.908
2024-10-17 | 17:13 | 49.906
2024-10-17 | 17:13 | 49.906
2024-10-17 | 17:13 | 49.907
2024-10-17 | 17:13 | 49.909
2024-10-17 | 17:13 | 49.907
2024-10-17 | 17:13 | 49.904
2024-10-17 | 17:13 | 49.906
2024-10-17 | 17:13 | 49.905
2024-10-17 | 17:13 | 49.907
2024-10-17 | 17:13 | 49.911
2024-10-17 | 17:13 | 49.912
2024-10-17 | 17:13 | 49.914
2024-10-17 | 17:13 | 49.916
2024-10-17 | 17:13 | 49.918
2024-10-17 | 17:13 | 49.92
2024-10-17 | 17:13 | 49.921
2024-10-17 | 17:13 | 49.921
2024-10-17 | 17:13 | 49.923
2024-10-17 | 17:13 | 49.925
2024-10-17 | 17:13 | 49.926
2024-10-17 | 17:13 | 49.925
2024-10-17 | 17:13 | 49.924
2024-10-17 | 17:13 | 49.922
2024-10-17 | 17:13 | 49.922
2024-10-17 | 17:13 | 49.922
2024-10-17 | 17:13 | 49.922
2024-10-17 | 17:13 | 49.92
2024-10-17 | 17:13 | 49.916
2024-10-17 | 17:13 | 49.912
2024-10-17 | 17:13 | 49.909
2024-10-17 | 17:13 | 49.908
2024-10-17 | 17:13 | 49.905
2024-10-17 | 17:13 | 49.904
2024-10-17 | 17:13 | 49.905
2024-10-17 | 17:13 | 49.9
2024-10-17 | 17:13 | 49.9
2024-10-17 | 17:13 | 49.897
2024-10-17 | 17:13 | 49.898
2024-10-17 | 17:13 | 49.896
2024-10-17 | 17:13 | 49.896
2024-10-17 | 17:13 | 49.894
2024-10-17 | 17:13 | 49.895
2024-10-17 | 17:13 | 49.893
2024-10-17 | 17:13 | 49.893
2024-10-17 | 17:13 | 49.894
2024-10-17 | 17:13 | 49.895
2024-10-17 | 17:13 | 49.895
2024-10-17 | 17:13 | 49.897
2024-10-17 | 17:13 | 49.9
2024-10-17 | 17:13 | 49.903
2024-10-17 | 17:13 | 49.906
2024-10-17 | 17:13 | 49.905
2024-10-17 | 17:13 | 49.905
2024-10-17 | 17:13 | 49.904
2024-10-17 | 17:13 | 49.903
2024-10-17 | 17:13 | 49.903
2024-10-17 | 17:14 | 49.901
2024-10-17 | 17:14 | 49.899
2024-10-17 | 17:14 | 49.899
2024-10-17 | 17:14 | 49.901
2024-10-17 | 17:14 | 49.898
2024-10-17 | 17:14 | 49.901
2024-10-17 | 17:14 | 49.903
2024-10-17 | 17:14 | 49.903
2024-10-17 | 17:14 | 49.907
2024-10-17 | 17:14 | 49.907
2024-10-17 | 17:14 | 49.908
2024-10-17 | 17:14 | 49.907
2024-10-17 | 17:14 | 49.909
2024-10-17 | 17:14 | 49.909
2024-10-17 | 17:14 | 49.906
2024-10-17 | 17:14 | 49.907
2024-10-17 | 17:14 | 49.903
2024-10-17 | 17:14 | 49.9
2024-10-17 | 17:14 | 49.898
2024-10-17 | 17:14 | 49.897
2024-10-17 | 17:14 | 49.893
2024-10-17 | 17:14 | 49.89
2024-10-17 | 17:14 | 49.89
2024-10-17 | 17:14 | 49.891
2024-10-17 | 17:14 | 49.894
2024-10-17 | 17:14 | 49.894
2024-10-17 | 17:14 | 49.894
2024-10-17 | 17:14 | 49.891
2024-10-17 | 17:14 | 49.889
2024-10-17 | 17:14 | 49.886
2024-10-17 | 17:14 | 49.886
2024-10-17 | 17:14 | 49.886
2024-10-17 | 17:14 | 49.888
2024-10-17 | 17:14 | 49.89
2024-10-17 | 17:14 | 49.888
2024-10-17 | 17:14 | 49.888
2024-10-17 | 17:14 | 49.892
2024-10-17 | 17:14 | 49.896
2024-10-17 | 17:14 | 49.898
2024-10-17 | 17:14 | 49.897
2024-10-17 | 17:14 | 49.897
2024-10-17 | 17:14 | 49.898
2024-10-17 | 17:14 | 49.894
2024-10-17 | 17:14 | 49.891
2024-10-17 | 17:14 | 49.893
2024-10-17 | 17:14 | 49.891
2024-10-17 | 17:14 | 49.892
2024-10-17 | 17:14 | 49.893
2024-10-17 | 17:14 | 49.892
2024-10-17 | 17:14 | 49.894
2024-10-17 | 17:14 | 49.896
2024-10-17 | 17:14 | 49.896
2024-10-17 | 17:14 | 49.899
2024-10-17 | 17:14 | 49.896
2024-10-17 | 17:14 | 49.893
2024-10-17 | 17:14 | 49.891
2024-10-17 | 17:14 | 49.888
2024-10-17 | 17:14 | 49.887
2024-10-17 | 17:14 | 49.888
2024-10-17 | 17:15 | 49.888
2024-10-17 | 17:15 | 49.89
2024-10-17 | 17:15 | 49.894
2024-10-17 | 17:15 | 49.895
2024-10-17 | 17:15 | 49.895
2024-10-17 | 17:15 | 49.895
2024-10-17 | 17:15 | 49.899
2024-10-17 | 17:15 | 49.902
2024-10-17 | 17:15 | 49.902
2024-10-17 | 17:15 | 49.903
2024-10-17 | 17:15 | 49.902
2024-10-17 | 17:15 | 49.899
2024-10-17 | 17:15 | 49.901
2024-10-17 | 17:15 | 49.901
2024-10-17 | 17:15 | 49.9
2024-10-17 | 17:15 | 49.9
2024-10-17 | 17:15 | 49.901
2024-10-17 | 17:15 | 49.902
2024-10-17 | 17:15 | 49.904
2024-10-17 | 17:15 | 49.905
2024-10-17 | 17:15 | 49.907
2024-10-17 | 17:15 | 49.91
2024-10-17 | 17:15 | 49.911
2024-10-17 | 17:15 | 49.914
2024-10-17 | 17:15 | 49.914
2024-10-17 | 17:15 | 49.914
2024-10-17 | 17:15 | 49.912
2024-10-17 | 17:15 | 49.912
2024-10-17 | 17:15 | 49.914
2024-10-17 | 17:15 | 49.914
2024-10-17 | 17:15 | 49.916
2024-10-17 | 17:15 | 49.915
2024-10-17 | 17:15 | 49.915
2024-10-17 | 17:15 | 49.912
2024-10-17 | 17:15 | 49.912
2024-10-17 | 17:15 | 49.909
2024-10-17 | 17:15 | 49.909
2024-10-17 | 17:15 | 49.904
2024-10-17 | 17:15 | 49.906
2024-10-17 | 17:15 | 49.902
2024-10-17 | 17:15 | 49.902
2024-10-17 | 17:15 | 49.898
2024-10-17 | 17:15 | 49.896
2024-10-17 | 17:15 | 49.894
2024-10-17 | 17:15 | 49.893
2024-10-17 | 17:15 | 49.894
2024-10-17 | 17:15 | 49.892
2024-10-17 | 17:15 | 49.892
2024-10-17 | 17:15 | 49.887
2024-10-17 | 17:15 | 49.885
2024-10-17 | 17:15 | 49.884
2024-10-17 | 17:15 | 49.879
2024-10-17 | 17:15 | 49.88
2024-10-17 | 17:15 | 49.877
2024-10-17 | 17:15 | 49.874
2024-10-17 | 17:15 | 49.874
2024-10-17 | 17:15 | 49.872
2024-10-17 | 17:15 | 49.875
2024-10-17 | 17:15 | 49.875
2024-10-17 | 17:15 | 49.875
2024-10-17 | 17:15 | 49.879
2024-10-17 | 17:16 | 49.88
2024-10-17 | 17:16 | 49.877
2024-10-17 | 17:16 | 49.878
2024-10-17 | 17:16 | 49.881
2024-10-17 | 17:16 | 49.88
2024-10-17 | 17:16 | 49.883
2024-10-17 | 17:16 | 49.884
2024-10-17 | 17:16 | 49.884
2024-10-17 | 17:16 | 49.886
2024-10-17 | 17:16 | 49.883
2024-10-17 | 17:16 | 49.885
2024-10-17 | 17:16 | 49.883
2024-10-17 | 17:16 | 49.888
2024-10-17 | 17:16 | 49.887
2024-10-17 | 17:16 | 49.89
2024-10-17 | 17:16 | 49.892
2024-10-17 | 17:16 | 49.89
2024-10-17 | 17:16 | 49.891
2024-10-17 | 17:16 | 49.887
2024-10-17 | 17:16 | 49.887
2024-10-17 | 17:16 | 49.887
2024-10-17 | 17:16 | 49.886
2024-10-17 | 17:16 | 49.882
2024-10-17 | 17:16 | 49.883
2024-10-17 | 17:16 | 49.88
2024-10-17 | 17:16 | 49.878
2024-10-17 | 17:16 | 49.878
2024-10-17 | 17:16 | 49.874
2024-10-17 | 17:16 | 49.877
2024-10-17 | 17:16 | 49.877
2024-10-17 | 17:16 | 49.881
2024-10-17 | 17:16 | 49.887
2024-10-17 | 17:16 | 49.891
2024-10-17 | 17:16 | 49.896
2024-10-17 | 17:16 | 49.9
2024-10-17 | 17:16 | 49.904
2024-10-17 | 17:16 | 49.909
2024-10-17 | 17:16 | 49.913
2024-10-17 | 17:16 | 49.917
2024-10-17 | 17:16 | 49.918
2024-10-17 | 17:16 | 49.922
2024-10-17 | 17:16 | 49.928
2024-10-17 | 17:16 | 49.928
2024-10-17 | 17:16 | 49.933
2024-10-17 | 17:16 | 49.935
2024-10-17 | 17:16 | 49.938
2024-10-17 | 17:16 | 49.942
2024-10-17 | 17:16 | 49.941
2024-10-17 | 17:16 | 49.945
2024-10-17 | 17:16 | 49.944
2024-10-17 | 17:16 | 49.947
2024-10-17 | 17:16 | 49.943
2024-10-17 | 17:16 | 49.944
2024-10-17 | 17:16 | 49.943
2024-10-17 | 17:16 | 49.943
2024-10-17 | 17:16 | 49.943
2024-10-17 | 17:16 | 49.94
2024-10-17 | 17:16 | 49.942
2024-10-17 | 17:16 | 49.94
2024-10-17 | 17:17 | 49.933
2024-10-17 | 17:17 | 49.934
2024-10-17 | 17:17 | 49.932
2024-10-17 | 17:17 | 49.932
2024-10-17 | 17:17 | 49.927
2024-10-17 | 17:17 | 49.926
2024-10-17 | 17:17 | 49.928
2024-10-17 | 17:17 | 49.923
2024-10-17 | 17:17 | 49.922
2024-10-17 | 17:17 | 49.921
2024-10-17 | 17:17 | 49.919
2024-10-17 | 17:17 | 49.92
2024-10-17 | 17:17 | 49.918
2024-10-17 | 17:17 | 49.92
2024-10-17 | 17:17 | 49.918
2024-10-17 | 17:17 | 49.92
2024-10-17 | 17:17 | 49.92
2024-10-17 | 17:17 | 49.92
2024-10-17 | 17:17 | 49.924
2024-10-17 | 17:17 | 49.928
2024-10-17 | 17:17 | 49.931
2024-10-17 | 17:17 | 49.935
2024-10-17 | 17:17 | 49.941
2024-10-17 | 17:17 | 49.944
2024-10-17 | 17:17 | 49.945
2024-10-17 | 17:17 | 49.945
2024-10-17 | 17:17 | 49.947
2024-10-17 | 17:17 | 49.942
2024-10-17 | 17:17 | 49.942
2024-10-17 | 17:17 | 49.943
2024-10-17 | 17:17 | 49.941
2024-10-17 | 17:17 | 49.941
2024-10-17 | 17:17 | 49.939
2024-10-17 | 17:17 | 49.94
2024-10-17 | 17:17 | 49.937
2024-10-17 | 17:17 | 49.94
2024-10-17 | 17:17 | 49.936
2024-10-17 | 17:17 | 49.938
2024-10-17 | 17:17 | 49.934
2024-10-17 | 17:17 | 49.933
2024-10-17 | 17:17 | 49.93
2024-10-17 | 17:17 | 49.927
2024-10-17 | 17:17 | 49.923
2024-10-17 | 17:17 | 49.917
2024-10-17 | 17:17 | 49.917
2024-10-17 | 17:17 | 49.918
2024-10-17 | 17:17 | 49.915
2024-10-17 | 17:17 | 49.916
2024-10-17 | 17:17 | 49.92
2024-10-17 | 17:17 | 49.92
2024-10-17 | 17:17 | 49.92
2024-10-17 | 17:17 | 49.921
2024-10-17 | 17:17 | 49.923
2024-10-17 | 17:17 | 49.92
2024-10-17 | 17:17 | 49.92
2024-10-17 | 17:17 | 49.922
2024-10-17 | 17:17 | 49.924
2024-10-17 | 17:17 | 49.923
2024-10-17 | 17:17 | 49.923
2024-10-17 | 17:17 | 49.927
2024-10-17 | 17:18 | 49.93
2024-10-17 | 17:18 | 49.931
2024-10-17 | 17:18 | 49.934
2024-10-17 | 17:18 | 49.937
2024-10-17 | 17:18 | 49.936
2024-10-17 | 17:18 | 49.937
2024-10-17 | 17:18 | 49.938
2024-10-17 | 17:18 | 49.937
2024-10-17 | 17:18 | 49.938
2024-10-17 | 17:18 | 49.941
2024-10-17 | 17:18 | 49.942
2024-10-17 | 17:18 | 49.943
2024-10-17 | 17:18 | 49.944
2024-10-17 | 17:18 | 49.946
2024-10-17 | 17:18 | 49.944
2024-10-17 | 17:18 | 49.946
2024-10-17 | 17:18 | 49.942
2024-10-17 | 17:18 | 49.943
2024-10-17 | 17:18 | 49.941
2024-10-17 | 17:18 | 49.938
2024-10-17 | 17:18 | 49.938
2024-10-17 | 17:18 | 49.935
2024-10-17 | 17:18 | 49.935
2024-10-17 | 17:18 | 49.933
2024-10-17 | 17:18 | 49.936
2024-10-17 | 17:18 | 49.934
2024-10-17 | 17:18 | 49.933
2024-10-17 | 17:18 | 49.932
2024-10-17 | 17:18 | 49.933
2024-10-17 | 17:18 | 49.933
2024-10-17 | 17:18 | 49.939
2024-10-17 | 17:18 | 49.939
2024-10-17 | 17:18 | 49.941
2024-10-17 | 17:18 | 49.94
2024-10-17 | 17:18 | 49.942
2024-10-17 | 17:18 | 49.94
2024-10-17 | 17:18 | 49.941
2024-10-17 | 17:18 | 49.939
2024-10-17 | 17:18 | 49.939
2024-10-17 | 17:18 | 49.941
2024-10-17 | 17:18 | 49.939
2024-10-17 | 17:18 | 49.939
2024-10-17 | 17:18 | 49.941
2024-10-17 | 17:18 | 49.94
2024-10-17 | 17:18 | 49.942
2024-10-17 | 17:18 | 49.944
2024-10-17 | 17:18 | 49.946
2024-10-17 | 17:18 | 49.943
2024-10-17 | 17:18 | 49.943
2024-10-17 | 17:18 | 49.945
2024-10-17 | 17:18 | 49.946
2024-10-17 | 17:18 | 49.946
2024-10-17 | 17:18 | 49.947
2024-10-17 | 17:18 | 49.945
2024-10-17 | 17:18 | 49.944
2024-10-17 | 17:18 | 49.945
2024-10-17 | 17:18 | 49.944
2024-10-17 | 17:18 | 49.944
2024-10-17 | 17:18 | 49.941
2024-10-17 | 17:18 | 49.941
2024-10-17 | 17:19 | 49.942
2024-10-17 | 17:19 | 49.94
2024-10-17 | 17:19 | 49.942
2024-10-17 | 17:19 | 49.941
2024-10-17 | 17:19 | 49.942
2024-10-17 | 17:19 | 49.943
2024-10-17 | 17:19 | 49.947
2024-10-17 | 17:19 | 49.948
2024-10-17 | 17:19 | 49.949
2024-10-17 | 17:19 | 49.948
2024-10-17 | 17:19 | 49.947
2024-10-17 | 17:19 | 49.947
2024-10-17 | 17:19 | 49.947
2024-10-17 | 17:19 | 49.946
2024-10-17 | 17:19 | 49.949
2024-10-17 | 17:19 | 49.947
2024-10-17 | 17:19 | 49.949
2024-10-17 | 17:19 | 49.951
2024-10-17 | 17:19 | 49.949
2024-10-17 | 17:19 | 49.951
2024-10-17 | 17:19 | 49.952
2024-10-17 | 17:19 | 49.951
2024-10-17 | 17:19 | 49.954
2024-10-17 | 17:19 | 49.957
2024-10-17 | 17:19 | 49.957
2024-10-17 | 17:19 | 49.956
2024-10-17 | 17:19 | 49.953
2024-10-17 | 17:19 | 49.953
2024-10-17 | 17:19 | 49.95
2024-10-17 | 17:19 | 49.947
2024-10-17 | 17:19 | 49.945
2024-10-17 | 17:19 | 49.944
2024-10-17 | 17:19 | 49.942
2024-10-17 | 17:19 | 49.938
2024-10-17 | 17:19 | 49.939
2024-10-17 | 17:19 | 49.942
2024-10-17 | 17:19 | 49.944
2024-10-17 | 17:19 | 49.942
2024-10-17 | 17:19 | 49.945
2024-10-17 | 17:19 | 49.944
2024-10-17 | 17:19 | 49.942
2024-10-17 | 17:19 | 49.942
2024-10-17 | 17:19 | 49.939
2024-10-17 | 17:19 | 49.94
2024-10-17 | 17:19 | 49.941
2024-10-17 | 17:19 | 49.941
2024-10-17 | 17:19 | 49.942
2024-10-17 | 17:19 | 49.94
2024-10-17 | 17:19 | 49.942
2024-10-17 | 17:19 | 49.941
2024-10-17 | 17:19 | 49.942
2024-10-17 | 17:19 | 49.941
2024-10-17 | 17:19 | 49.944
2024-10-17 | 17:19 | 49.942
2024-10-17 | 17:19 | 49.942
2024-10-17 | 17:19 | 49.941
2024-10-17 | 17:19 | 49.939
2024-10-17 | 17:19 | 49.942
2024-10-17 | 17:19 | 49.939
2024-10-17 | 17:19 | 49.94
2024-10-17 | 17:20 | 49.943
2024-10-17 | 17:20 | 49.943
2024-10-17 | 17:20 | 49.945
2024-10-17 | 17:20 | 49.946
2024-10-17 | 17:20 | 49.947
2024-10-17 | 17:20 | 49.944
2024-10-17 | 17:20 | 49.943
2024-10-17 | 17:20 | 49.941
2024-10-17 | 17:20 | 49.941
2024-10-17 | 17:20 | 49.941
2024-10-17 | 17:20 | 49.942
2024-10-17 | 17:20 | 49.944
2024-10-17 | 17:20 | 49.945
2024-10-17 | 17:20 | 49.947
2024-10-17 | 17:20 | 49.951
2024-10-17 | 17:20 | 49.952
2024-10-17 | 17:20 | 49.952
2024-10-17 | 17:20 | 49.955
2024-10-17 | 17:20 | 49.954
2024-10-17 | 17:20 | 49.955
2024-10-17 | 17:20 | 49.954
2024-10-17 | 17:20 | 49.957
2024-10-17 | 17:20 | 49.956
2024-10-17 | 17:20 | 49.959
2024-10-17 | 17:20 | 49.957
2024-10-17 | 17:20 | 49.958
2024-10-17 | 17:20 | 49.956
2024-10-17 | 17:20 | 49.953
2024-10-17 | 17:20 | 49.954
2024-10-17 | 17:20 | 49.951
2024-10-17 | 17:20 | 49.954
2024-10-17 | 17:20 | 49.951
2024-10-17 | 17:20 | 49.952
2024-10-17 | 17:20 | 49.948
2024-10-17 | 17:20 | 49.947
2024-10-17 | 17:20 | 49.942
2024-10-17 | 17:20 | 49.943
2024-10-17 | 17:20 | 49.941
2024-10-17 | 17:20 | 49.939
2024-10-17 | 17:20 | 49.939
2024-10-17 | 17:20 | 49.934
2024-10-17 | 17:20 | 49.933
2024-10-17 | 17:20 | 49.932
2024-10-17 | 17:20 | 49.934
2024-10-17 | 17:20 | 49.936
2024-10-17 | 17:20 | 49.938
2024-10-17 | 17:20 | 49.941
2024-10-17 | 17:20 | 49.94
2024-10-17 | 17:20 | 49.942
2024-10-17 | 17:20 | 49.943
2024-10-17 | 17:20 | 49.94
2024-10-17 | 17:20 | 49.936
2024-10-17 | 17:20 | 49.934
2024-10-17 | 17:20 | 49.932
2024-10-17 | 17:20 | 49.93
2024-10-17 | 17:20 | 49.927
2024-10-17 | 17:20 | 49.927
2024-10-17 | 17:20 | 49.927
2024-10-17 | 17:20 | 49.929
2024-10-17 | 17:20 | 49.934
2024-10-17 | 17:20 | 49.937
2024-10-17 | 17:21 | 49.94
2024-10-17 | 17:21 | 49.948
2024-10-17 | 17:21 | 49.954
2024-10-17 | 17:21 | 49.957
2024-10-17 | 17:21 | 49.962
2024-10-17 | 17:21 | 49.969
2024-10-17 | 17:21 | 49.97
2024-10-17 | 17:21 | 49.972
2024-10-17 | 17:21 | 49.976
2024-10-17 | 17:21 | 49.975
2024-10-17 | 17:21 | 49.976
2024-10-17 | 17:21 | 49.972
2024-10-17 | 17:21 | 49.971
2024-10-17 | 17:21 | 49.966
2024-10-17 | 17:21 | 49.963
2024-10-17 | 17:21 | 49.962
2024-10-17 | 17:21 | 49.961
2024-10-17 | 17:21 | 49.96
2024-10-17 | 17:21 | 49.957
2024-10-17 | 17:21 | 49.959
2024-10-17 | 17:21 | 49.956
2024-10-17 | 17:21 | 49.959
2024-10-17 | 17:21 | 49.96
2024-10-17 | 17:21 | 49.959
2024-10-17 | 17:21 | 49.963
2024-10-17 | 17:21 | 49.964
2024-10-17 | 17:21 | 49.965
2024-10-17 | 17:21 | 49.968
2024-10-17 | 17:21 | 49.971
2024-10-17 | 17:21 | 49.971
2024-10-17 | 17:21 | 49.97
2024-10-17 | 17:21 | 49.971
2024-10-17 | 17:21 | 49.969
2024-10-17 | 17:21 | 49.968
2024-10-17 | 17:21 | 49.967
2024-10-17 | 17:21 | 49.967
2024-10-17 | 17:21 | 49.967
2024-10-17 | 17:21 | 49.966
2024-10-17 | 17:21 | 49.966
2024-10-17 | 17:21 | 49.966
2024-10-17 | 17:21 | 49.965
2024-10-17 | 17:21 | 49.967
2024-10-17 | 17:21 | 49.967
2024-10-17 | 17:21 | 49.968
2024-10-17 | 17:21 | 49.968
2024-10-17 | 17:21 | 49.967
2024-10-17 | 17:21 | 49.964
2024-10-17 | 17:21 | 49.963
2024-10-17 | 17:21 | 49.96
2024-10-17 | 17:21 | 49.958
2024-10-17 | 17:21 | 49.956
2024-10-17 | 17:21 | 49.957
2024-10-17 | 17:21 | 49.959
2024-10-17 | 17:21 | 49.961
2024-10-17 | 17:21 | 49.964
2024-10-17 | 17:21 | 49.967
2024-10-17 | 17:21 | 49.97
2024-10-17 | 17:21 | 49.97
2024-10-17 | 17:21 | 49.973
2024-10-17 | 17:22 | 49.974
2024-10-17 | 17:22 | 49.972
2024-10-17 | 17:22 | 49.975
2024-10-17 | 17:22 | 49.974
2024-10-17 | 17:22 | 49.976
2024-10-17 | 17:22 | 49.974
2024-10-17 | 17:22 | 49.973
2024-10-17 | 17:22 | 49.973
2024-10-17 | 17:22 | 49.972
2024-10-17 | 17:22 | 49.969
2024-10-17 | 17:22 | 49.969
2024-10-17 | 17:22 | 49.968
2024-10-17 | 17:22 | 49.968
2024-10-17 | 17:22 | 49.967
2024-10-17 | 17:22 | 49.971
2024-10-17 | 17:22 | 49.973
2024-10-17 | 17:22 | 49.974
2024-10-17 | 17:22 | 49.975
2024-10-17 | 17:22 | 49.974
2024-10-17 | 17:22 | 49.975
2024-10-17 | 17:22 | 49.971
2024-10-17 | 17:22 | 49.974
2024-10-17 | 17:22 | 49.975
2024-10-17 | 17:22 | 49.978
2024-10-17 | 17:22 | 49.98
2024-10-17 | 17:22 | 49.978
2024-10-17 | 17:22 | 49.977
2024-10-17 | 17:22 | 49.977
2024-10-17 | 17:22 | 49.978
2024-10-17 | 17:22 | 49.978
2024-10-17 | 17:22 | 49.978
2024-10-17 | 17:22 | 49.978
2024-10-17 | 17:22 | 49.979
2024-10-17 | 17:22 | 49.981
2024-10-17 | 17:22 | 49.986
2024-10-17 | 17:22 | 49.989
2024-10-17 | 17:22 | 49.99
2024-10-17 | 17:22 | 49.993
2024-10-17 | 17:22 | 49.993
2024-10-17 | 17:22 | 49.995
2024-10-17 | 17:22 | 49.994
2024-10-17 | 17:22 | 49.993
2024-10-17 | 17:22 | 49.995
2024-10-17 | 17:22 | 49.992
2024-10-17 | 17:22 | 49.991
2024-10-17 | 17:22 | 49.992
2024-10-17 | 17:22 | 49.991
2024-10-17 | 17:22 | 49.993
2024-10-17 | 17:22 | 49.993
2024-10-17 | 17:22 | 49.994
2024-10-17 | 17:22 | 49.995
2024-10-17 | 17:22 | 49.993
2024-10-17 | 17:22 | 49.994
2024-10-17 | 17:22 | 49.99
2024-10-17 | 17:22 | 49.986
2024-10-17 | 17:22 | 49.986
2024-10-17 | 17:22 | 49.984
2024-10-17 | 17:22 | 49.981
2024-10-17 | 17:22 | 49.978
2024-10-17 | 17:22 | 49.977
2024-10-17 | 17:22 | 49.976
2024-10-17 | 17:23 | 49.974
2024-10-17 | 17:23 | 49.974
2024-10-17 | 17:23 | 49.977
2024-10-17 | 17:23 | 49.977
2024-10-17 | 17:23 | 49.979
2024-10-17 | 17:23 | 49.982
2024-10-17 | 17:23 | 49.986
2024-10-17 | 17:23 | 49.988
2024-10-17 | 17:23 | 49.989
2024-10-17 | 17:23 | 49.993
2024-10-17 | 17:23 | 49.998
2024-10-17 | 17:23 | 50.003
2024-10-17 | 17:23 | 50.006
2024-10-17 | 17:23 | 50.007
2024-10-17 | 17:23 | 50.01
2024-10-17 | 17:23 | 50.014
2024-10-17 | 17:23 | 50.016
2024-10-17 | 17:23 | 50.017
2024-10-17 | 17:23 | 50.018
2024-10-17 | 17:23 | 50.015
2024-10-17 | 17:23 | 50.014
2024-10-17 | 17:23 | 50.012
2024-10-17 | 17:23 | 50.008
2024-10-17 | 17:23 | 50.008
2024-10-17 | 17:23 | 50.006
2024-10-17 | 17:23 | 50.004
2024-10-17 | 17:23 | 50.004
2024-10-17 | 17:23 | 50.001
2024-10-17 | 17:23 | 50.001
2024-10-17 | 17:23 | 50.002
2024-10-17 | 17:23 | 50.001
2024-10-17 | 17:23 | 50
2024-10-17 | 17:23 | 50.002
2024-10-17 | 17:23 | 50.001
2024-10-17 | 17:23 | 50.003
2024-10-17 | 17:23 | 50.005
2024-10-17 | 17:23 | 50.008
2024-10-17 | 17:23 | 50.009
2024-10-17 | 17:23 | 50.008
2024-10-17 | 17:23 | 50.006
2024-10-17 | 17:23 | 50.002
2024-10-17 | 17:23 | 49.998
2024-10-17 | 17:23 | 49.996
2024-10-17 | 17:23 | 49.994
2024-10-17 | 17:23 | 49.991
2024-10-17 | 17:23 | 49.99
2024-10-17 | 17:23 | 49.988
2024-10-17 | 17:23 | 49.987
2024-10-17 | 17:23 | 49.984
2024-10-17 | 17:23 | 49.982
2024-10-17 | 17:23 | 49.982
2024-10-17 | 17:23 | 49.98
2024-10-17 | 17:23 | 49.981
2024-10-17 | 17:23 | 49.983
2024-10-17 | 17:23 | 49.983
2024-10-17 | 17:23 | 49.984
2024-10-17 | 17:23 | 49.989
2024-10-17 | 17:23 | 49.992
2024-10-17 | 17:23 | 49.995
2024-10-17 | 17:24 | 50
2024-10-17 | 17:24 | 50.001
2024-10-17 | 17:24 | 50.007
2024-10-17 | 17:24 | 50.007
2024-10-17 | 17:24 | 50.008
2024-10-17 | 17:24 | 50.009
2024-10-17 | 17:24 | 50.008
2024-10-17 | 17:24 | 50.007
2024-10-17 | 17:24 | 50.005
2024-10-17 | 17:24 | 50.003
2024-10-17 | 17:24 | 50.002
2024-10-17 | 17:24 | 50
2024-10-17 | 17:24 | 50
2024-10-17 | 17:24 | 50
2024-10-17 | 17:24 | 50
2024-10-17 | 17:24 | 50
2024-10-17 | 17:24 | 50
2024-10-17 | 17:24 | 49.998
2024-10-17 | 17:24 | 49.993
2024-10-17 | 17:24 | 49.992
2024-10-17 | 17:24 | 49.99
2024-10-17 | 17:24 | 49.985
2024-10-17 | 17:24 | 49.984
2024-10-17 | 17:24 | 49.98
2024-10-17 | 17:24 | 49.98
2024-10-17 | 17:24 | 49.983
2024-10-17 | 17:24 | 49.979
2024-10-17 | 17:24 | 49.979
2024-10-17 | 17:24 | 49.975
2024-10-17 | 17:24 | 49.973
2024-10-17 | 17:24 | 49.971

## 20241020-1
In GMT
Date | Time | Freq
2024-10-20 | 4:43 | 50.009 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-10-20 | 4:43 | 50.007 | 222 | BRITNED | 676.211
2024-10-20 | 4:43 | 50.006 | 268 | WBURB-2 | 428.156
2024-10-20 | 4:43 | 50.005 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-10-20 | 4:43 | 50.003 |  | Viking Link | -648.9
2024-10-20 | 4:43 | 50.001 |  | Viking Link | 1398.96
2024-10-20 | 4:43 | 49.999 | 209 | DRAXX-3 | 626.95
2024-10-20 | 4:43 | 50 | 154 | CDCL-1 | 391.57
2024-10-20 | 4:43 | 49.999 | 268 | ROCK-1 | 468.495
2024-10-20 | 4:43 | 50 | 148 | IFA Bipole1 | 945.473
2024-10-20 | 4:43 | 50.001 | 132 | IFA Bipole1 | 999.1
2024-10-20 | 4:43 | 50 | 141 | IFA Bipole2 | 1000
2024-10-20 | 4:43 | 49.999 | 135 | IFA Bipole1 | 996.75
2024-10-20 | 4:43 | 49.994 |  | Viking Link | -780.3
2024-10-20 | 4:43 | 49.989
2024-10-20 | 4:43 | 49.985
2024-10-20 | 4:43 | 49.98
2024-10-20 | 4:43 | 49.977
2024-10-20 | 4:43 | 49.973
2024-10-20 | 4:43 | 49.969 | 130 | HEYM12 | 271.908
2024-10-20 | 4:43 | 49.968 | 228 | HUMR-1 | 303.75
2024-10-20 | 4:43 | 49.964
2024-10-20 | 4:43 | 49.961
2024-10-20 | 4:43 | 49.958
2024-10-20 | 4:43 | 49.956
2024-10-20 | 4:43 | 49.953
2024-10-20 | 4:43 | 49.95
2024-10-20 | 4:43 | 49.948
2024-10-20 | 4:43 | 49.948
2024-10-20 | 4:43 | 49.946
2024-10-20 | 4:44 | 49.946 | 211 | CDCL-1 | 291.5
2024-10-20 | 4:44 | 49.946 | 199 | STAY-2 | 413.125
2024-10-20 | 4:44 | 49.947 | 173 | CDCL-1 | 397.375
2024-10-20 | 4:44 | 49.945 | 248 | SEAB-2 | 361.25
2024-10-20 | 4:44 | 49.943 | 255 | FRANCE | 995.65
2024-10-20 | 4:44 | 49.943 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-10-20 | 4:44 | 49.942
2024-10-20 | 4:44 | 49.941
2024-10-20 | 4:44 | 49.94
2024-10-20 | 4:44 | 49.939
2024-10-20 | 4:44 | 49.94
2024-10-20 | 4:44 | 49.938
2024-10-20 | 4:44 | 49.937
2024-10-20 | 4:44 | 49.937
2024-10-20 | 4:44 | 49.936
2024-10-20 | 4:44 | 49.933
2024-10-20 | 4:44 | 49.933
2024-10-20 | 4:44 | 49.936
2024-10-20 | 4:44 | 49.936
2024-10-20 | 4:44 | 49.936
2024-10-20 | 4:44 | 49.935
2024-10-20 | 4:44 | 49.933
2024-10-20 | 4:44 | 49.934
2024-10-20 | 4:44 | 49.933
2024-10-20 | 4:44 | 49.934
2024-10-20 | 4:44 | 49.933
2024-10-20 | 4:44 | 49.934
2024-10-20 | 4:44 | 49.933
2024-10-20 | 4:44 | 49.936
2024-10-20 | 4:44 | 49.936
2024-10-20 | 4:44 | 49.938
2024-10-20 | 4:44 | 49.938
2024-10-20 | 4:44 | 49.939
2024-10-20 | 4:44 | 49.937
2024-10-20 | 4:44 | 49.935
2024-10-20 | 4:44 | 49.936
2024-10-20 | 4:44 | 49.934
2024-10-20 | 4:44 | 49.933
2024-10-20 | 4:44 | 49.933
2024-10-20 | 4:44 | 49.928
2024-10-20 | 4:44 | 49.926
2024-10-20 | 4:44 | 49.927
2024-10-20 | 4:44 | 49.925
2024-10-20 | 4:44 | 49.923
2024-10-20 | 4:44 | 49.923
2024-10-20 | 4:44 | 49.923
2024-10-20 | 4:44 | 49.925
2024-10-20 | 4:44 | 49.923
2024-10-20 | 4:44 | 49.923
2024-10-20 | 4:44 | 49.92
2024-10-20 | 4:44 | 49.918
2024-10-20 | 4:44 | 49.917
2024-10-20 | 4:44 | 49.919
2024-10-20 | 4:44 | 49.92
2024-10-20 | 4:44 | 49.919
2024-10-20 | 4:44 | 49.916
2024-10-20 | 4:44 | 49.911
2024-10-20 | 4:44 | 49.909
2024-10-20 | 4:44 | 49.909
2024-10-20 | 4:44 | 49.908
2024-10-20 | 4:44 | 49.903
2024-10-20 | 4:45 | 49.899
2024-10-20 | 4:45 | 49.898
2024-10-20 | 4:45 | 49.896
2024-10-20 | 4:45 | 49.896
2024-10-20 | 4:45 | 49.896
2024-10-20 | 4:45 | 49.895
2024-10-20 | 4:45 | 49.893
2024-10-20 | 4:45 | 49.891
2024-10-20 | 4:45 | 49.89
2024-10-20 | 4:45 | 49.889
2024-10-20 | 4:45 | 49.89
2024-10-20 | 4:45 | 49.891
2024-10-20 | 4:45 | 49.89
2024-10-20 | 4:45 | 49.89
2024-10-20 | 4:45 | 49.889
2024-10-20 | 4:45 | 49.889
2024-10-20 | 4:45 | 49.889
2024-10-20 | 4:45 | 49.889
2024-10-20 | 4:45 | 49.887
2024-10-20 | 4:45 | 49.885
2024-10-20 | 4:45 | 49.882
2024-10-20 | 4:45 | 49.88
2024-10-20 | 4:45 | 49.881
2024-10-20 | 4:45 | 49.88
2024-10-20 | 4:45 | 49.876
2024-10-20 | 4:45 | 49.874
2024-10-20 | 4:45 | 49.871
2024-10-20 | 4:45 | 49.871
2024-10-20 | 4:45 | 49.87
2024-10-20 | 4:45 | 49.861
2024-10-20 | 4:45 | 49.847
2024-10-20 | 4:45 | 49.845
2024-10-20 | 4:45 | 49.844
2024-10-20 | 4:45 | 49.843
2024-10-20 | 4:45 | 49.844
2024-10-20 | 4:45 | 49.843
2024-10-20 | 4:45 | 49.846
2024-10-20 | 4:45 | 49.846
2024-10-20 | 4:45 | 49.842
2024-10-20 | 4:45 | 49.841
2024-10-20 | 4:45 | 49.84
2024-10-20 | 4:45 | 49.84
2024-10-20 | 4:45 | 49.838
2024-10-20 | 4:45 | 49.837
2024-10-20 | 4:45 | 49.834
2024-10-20 | 4:45 | 49.835
2024-10-20 | 4:45 | 49.836
2024-10-20 | 4:45 | 49.837
2024-10-20 | 4:45 | 49.834
2024-10-20 | 4:45 | 49.832
2024-10-20 | 4:45 | 49.829
2024-10-20 | 4:45 | 49.828
2024-10-20 | 4:45 | 49.821
2024-10-20 | 4:45 | 49.817
2024-10-20 | 4:45 | 49.82
2024-10-20 | 4:45 | 49.823
2024-10-20 | 4:45 | 49.824
2024-10-20 | 4:45 | 49.823
2024-10-20 | 4:45 | 49.822
2024-10-20 | 4:46 | 49.822
2024-10-20 | 4:46 | 49.822
2024-10-20 | 4:46 | 49.823
2024-10-20 | 4:46 | 49.825
2024-10-20 | 4:46 | 49.829
2024-10-20 | 4:46 | 49.829
2024-10-20 | 4:46 | 49.83
2024-10-20 | 4:46 | 49.831
2024-10-20 | 4:46 | 49.831
2024-10-20 | 4:46 | 49.831
2024-10-20 | 4:46 | 49.831
2024-10-20 | 4:46 | 49.83
2024-10-20 | 4:46 | 49.832
2024-10-20 | 4:46 | 49.831
2024-10-20 | 4:46 | 49.833
2024-10-20 | 4:46 | 49.834
2024-10-20 | 4:46 | 49.832
2024-10-20 | 4:46 | 49.832
2024-10-20 | 4:46 | 49.833
2024-10-20 | 4:46 | 49.834
2024-10-20 | 4:46 | 49.836
2024-10-20 | 4:46 | 49.837
2024-10-20 | 4:46 | 49.837
2024-10-20 | 4:46 | 49.837
2024-10-20 | 4:46 | 49.837
2024-10-20 | 4:46 | 49.838
2024-10-20 | 4:46 | 49.839
2024-10-20 | 4:46 | 49.839
2024-10-20 | 4:46 | 49.842
2024-10-20 | 4:46 | 49.843
2024-10-20 | 4:46 | 49.845
2024-10-20 | 4:46 | 49.846
2024-10-20 | 4:46 | 49.85
2024-10-20 | 4:46 | 49.852
2024-10-20 | 4:46 | 49.853
2024-10-20 | 4:46 | 49.853
2024-10-20 | 4:46 | 49.855
2024-10-20 | 4:46 | 49.857
2024-10-20 | 4:46 | 49.859
2024-10-20 | 4:46 | 49.859
2024-10-20 | 4:46 | 49.859
2024-10-20 | 4:46 | 49.859
2024-10-20 | 4:46 | 49.859
2024-10-20 | 4:46 | 49.857
2024-10-20 | 4:46 | 49.858
2024-10-20 | 4:46 | 49.858
2024-10-20 | 4:46 | 49.858
2024-10-20 | 4:46 | 49.858
2024-10-20 | 4:46 | 49.857
2024-10-20 | 4:46 | 49.856
2024-10-20 | 4:46 | 49.857
2024-10-20 | 4:46 | 49.857
2024-10-20 | 4:46 | 49.861
2024-10-20 | 4:46 | 49.86
2024-10-20 | 4:46 | 49.859
2024-10-20 | 4:46 | 49.862
2024-10-20 | 4:46 | 49.862
2024-10-20 | 4:46 | 49.861
2024-10-20 | 4:46 | 49.86
2024-10-20 | 4:46 | 49.859
2024-10-20 | 4:46 | 49.861
2024-10-20 | 4:47 | 49.86
2024-10-20 | 4:47 | 49.861
2024-10-20 | 4:47 | 49.861
2024-10-20 | 4:47 | 49.859
2024-10-20 | 4:47 | 49.855
2024-10-20 | 4:47 | 49.854
2024-10-20 | 4:47 | 49.853
2024-10-20 | 4:47 | 49.853
2024-10-20 | 4:47 | 49.855
2024-10-20 | 4:47 | 49.855
2024-10-20 | 4:47 | 49.855
2024-10-20 | 4:47 | 49.855
2024-10-20 | 4:47 | 49.857
2024-10-20 | 4:47 | 49.859
2024-10-20 | 4:47 | 49.858
2024-10-20 | 4:47 | 49.861
2024-10-20 | 4:47 | 49.862
2024-10-20 | 4:47 | 49.862
2024-10-20 | 4:47 | 49.861
2024-10-20 | 4:47 | 49.864
2024-10-20 | 4:47 | 49.862
2024-10-20 | 4:47 | 49.862
2024-10-20 | 4:47 | 49.862
2024-10-20 | 4:47 | 49.866
2024-10-20 | 4:47 | 49.866
2024-10-20 | 4:47 | 49.869
2024-10-20 | 4:47 | 49.868
2024-10-20 | 4:47 | 49.864
2024-10-20 | 4:47 | 49.863
2024-10-20 | 4:47 | 49.86
2024-10-20 | 4:47 | 49.861
2024-10-20 | 4:47 | 49.859
2024-10-20 | 4:47 | 49.859
2024-10-20 | 4:47 | 49.857
2024-10-20 | 4:47 | 49.855
2024-10-20 | 4:47 | 49.854
2024-10-20 | 4:47 | 49.853
2024-10-20 | 4:47 | 49.851
2024-10-20 | 4:47 | 49.851
2024-10-20 | 4:47 | 49.851
2024-10-20 | 4:47 | 49.855
2024-10-20 | 4:47 | 49.857
2024-10-20 | 4:47 | 49.857
2024-10-20 | 4:47 | 49.854
2024-10-20 | 4:47 | 49.853
2024-10-20 | 4:47 | 49.855
2024-10-20 | 4:47 | 49.854
2024-10-20 | 4:47 | 49.854
2024-10-20 | 4:47 | 49.854
2024-10-20 | 4:47 | 49.853
2024-10-20 | 4:47 | 49.851
2024-10-20 | 4:47 | 49.852
2024-10-20 | 4:47 | 49.852
2024-10-20 | 4:47 | 49.851
2024-10-20 | 4:47 | 49.85
2024-10-20 | 4:47 | 49.847
2024-10-20 | 4:47 | 49.849
2024-10-20 | 4:47 | 49.846
2024-10-20 | 4:47 | 49.847
2024-10-20 | 4:48 | 49.849
2024-10-20 | 4:48 | 49.852
2024-10-20 | 4:48 | 49.854
2024-10-20 | 4:48 | 49.853
2024-10-20 | 4:48 | 49.853
2024-10-20 | 4:48 | 49.852
2024-10-20 | 4:48 | 49.851
2024-10-20 | 4:48 | 49.852
2024-10-20 | 4:48 | 49.851
2024-10-20 | 4:48 | 49.849
2024-10-20 | 4:48 | 49.848
2024-10-20 | 4:48 | 49.847
2024-10-20 | 4:48 | 49.847
2024-10-20 | 4:48 | 49.845
2024-10-20 | 4:48 | 49.844
2024-10-20 | 4:48 | 49.841
2024-10-20 | 4:48 | 49.841
2024-10-20 | 4:48 | 49.84
2024-10-20 | 4:48 | 49.839
2024-10-20 | 4:48 | 49.842
2024-10-20 | 4:48 | 49.841
2024-10-20 | 4:48 | 49.839
2024-10-20 | 4:48 | 49.842
2024-10-20 | 4:48 | 49.842
2024-10-20 | 4:48 | 49.846
2024-10-20 | 4:48 | 49.847
2024-10-20 | 4:48 | 49.848
2024-10-20 | 4:48 | 49.845
2024-10-20 | 4:48 | 49.847
2024-10-20 | 4:48 | 49.848
2024-10-20 | 4:48 | 49.849
2024-10-20 | 4:48 | 49.851
2024-10-20 | 4:48 | 49.852
2024-10-20 | 4:48 | 49.853
2024-10-20 | 4:48 | 49.853
2024-10-20 | 4:48 | 49.852
2024-10-20 | 4:48 | 49.853
2024-10-20 | 4:48 | 49.856
2024-10-20 | 4:48 | 49.853
2024-10-20 | 4:48 | 49.854
2024-10-20 | 4:48 | 49.855
2024-10-20 | 4:48 | 49.851
2024-10-20 | 4:48 | 49.85
2024-10-20 | 4:48 | 49.853
2024-10-20 | 4:48 | 49.852
2024-10-20 | 4:48 | 49.853
2024-10-20 | 4:48 | 49.853
2024-10-20 | 4:48 | 49.853
2024-10-20 | 4:48 | 49.853
2024-10-20 | 4:48 | 49.854
2024-10-20 | 4:48 | 49.852
2024-10-20 | 4:48 | 49.851
2024-10-20 | 4:48 | 49.853
2024-10-20 | 4:48 | 49.856
2024-10-20 | 4:48 | 49.861
2024-10-20 | 4:48 | 49.864
2024-10-20 | 4:48 | 49.867
2024-10-20 | 4:48 | 49.869
2024-10-20 | 4:48 | 49.871
2024-10-20 | 4:48 | 49.874
2024-10-20 | 4:48 | 49.879
2024-10-20 | 4:49 | 49.886
2024-10-20 | 4:49 | 49.893
2024-10-20 | 4:49 | 49.898
2024-10-20 | 4:49 | 49.903
2024-10-20 | 4:49 | 49.906
2024-10-20 | 4:49 | 49.908
2024-10-20 | 4:49 | 49.912
2024-10-20 | 4:49 | 49.917
2024-10-20 | 4:49 | 49.914
2024-10-20 | 4:49 | 49.918
2024-10-20 | 4:49 | 49.919
2024-10-20 | 4:49 | 49.918
2024-10-20 | 4:49 | 49.923
2024-10-20 | 4:49 | 49.922
2024-10-20 | 4:49 | 49.926
2024-10-20 | 4:49 | 49.929
2024-10-20 | 4:49 | 49.925
2024-10-20 | 4:49 | 49.926
2024-10-20 | 4:49 | 49.931
2024-10-20 | 4:49 | 49.931
2024-10-20 | 4:49 | 49.931
2024-10-20 | 4:49 | 49.934
2024-10-20 | 4:49 | 49.932
2024-10-20 | 4:49 | 49.932
2024-10-20 | 4:49 | 49.934
2024-10-20 | 4:49 | 49.934
2024-10-20 | 4:49 | 49.932
2024-10-20 | 4:49 | 49.931
2024-10-20 | 4:49 | 49.93
2024-10-20 | 4:49 | 49.927
2024-10-20 | 4:49 | 49.924
2024-10-20 | 4:49 | 49.925
2024-10-20 | 4:49 | 49.928
2024-10-20 | 4:49 | 49.926
2024-10-20 | 4:49 | 49.926
2024-10-20 | 4:49 | 49.927
2024-10-20 | 4:49 | 49.926
2024-10-20 | 4:49 | 49.93
2024-10-20 | 4:49 | 49.926
2024-10-20 | 4:49 | 49.925
2024-10-20 | 4:49 | 49.926
2024-10-20 | 4:49 | 49.926
2024-10-20 | 4:49 | 49.926
2024-10-20 | 4:49 | 49.927
2024-10-20 | 4:49 | 49.927
2024-10-20 | 4:49 | 49.926
2024-10-20 | 4:49 | 49.926
2024-10-20 | 4:49 | 49.929
2024-10-20 | 4:49 | 49.93
2024-10-20 | 4:49 | 49.933
2024-10-20 | 4:49 | 49.938
2024-10-20 | 4:49 | 49.937
2024-10-20 | 4:49 | 49.936
2024-10-20 | 4:49 | 49.934
2024-10-20 | 4:49 | 49.939
2024-10-20 | 4:49 | 49.941
2024-10-20 | 4:49 | 49.943
2024-10-20 | 4:49 | 49.942
2024-10-20 | 4:49 | 49.939
2024-10-20 | 4:50 | 49.937
2024-10-20 | 4:50 | 49.936
2024-10-20 | 4:50 | 49.938
2024-10-20 | 4:50 | 49.941
2024-10-20 | 4:50 | 49.943
2024-10-20 | 4:50 | 49.945
2024-10-20 | 4:50 | 49.943
2024-10-20 | 4:50 | 49.941
2024-10-20 | 4:50 | 49.941
2024-10-20 | 4:50 | 49.94
2024-10-20 | 4:50 | 49.939
2024-10-20 | 4:50 | 49.941
2024-10-20 | 4:50 | 49.94
2024-10-20 | 4:50 | 49.94
2024-10-20 | 4:50 | 49.939
2024-10-20 | 4:50 | 49.94
2024-10-20 | 4:50 | 49.942
2024-10-20 | 4:50 | 49.945
2024-10-20 | 4:50 | 49.944
2024-10-20 | 4:50 | 49.945
2024-10-20 | 4:50 | 49.944
2024-10-20 | 4:50 | 49.945
2024-10-20 | 4:50 | 49.947
2024-10-20 | 4:50 | 49.95
2024-10-20 | 4:50 | 49.952
2024-10-20 | 4:50 | 49.95
2024-10-20 | 4:50 | 49.949
2024-10-20 | 4:50 | 49.949
2024-10-20 | 4:50 | 49.951
2024-10-20 | 4:50 | 49.955
2024-10-20 | 4:50 | 49.956
2024-10-20 | 4:50 | 49.954
2024-10-20 | 4:50 | 49.949
2024-10-20 | 4:50 | 49.947
2024-10-20 | 4:50 | 49.948
2024-10-20 | 4:50 | 49.95
2024-10-20 | 4:50 | 49.95
2024-10-20 | 4:50 | 49.95
2024-10-20 | 4:50 | 49.949
2024-10-20 | 4:50 | 49.948
2024-10-20 | 4:50 | 49.948
2024-10-20 | 4:50 | 49.95
2024-10-20 | 4:50 | 49.95
2024-10-20 | 4:50 | 49.95
2024-10-20 | 4:50 | 49.95
2024-10-20 | 4:50 | 49.95
2024-10-20 | 4:50 | 49.946
2024-10-20 | 4:50 | 49.95
2024-10-20 | 4:50 | 49.952
2024-10-20 | 4:50 | 49.953
2024-10-20 | 4:50 | 49.95
2024-10-20 | 4:50 | 49.951
2024-10-20 | 4:50 | 49.953
2024-10-20 | 4:50 | 49.955
2024-10-20 | 4:50 | 49.954
2024-10-20 | 4:50 | 49.959
2024-10-20 | 4:50 | 49.961
2024-10-20 | 4:50 | 49.961
2024-10-20 | 4:50 | 49.962
2024-10-20 | 4:50 | 49.963
2024-10-20 | 4:50 | 49.964
2024-10-20 | 4:51 | 49.963
2024-10-20 | 4:51 | 49.962
2024-10-20 | 4:51 | 49.962
2024-10-20 | 4:51 | 49.963
2024-10-20 | 4:51 | 49.964
2024-10-20 | 4:51 | 49.964
2024-10-20 | 4:51 | 49.963
2024-10-20 | 4:51 | 49.959
2024-10-20 | 4:51 | 49.96
2024-10-20 | 4:51 | 49.961
2024-10-20 | 4:51 | 49.961
2024-10-20 | 4:51 | 49.959
2024-10-20 | 4:51 | 49.959
2024-10-20 | 4:51 | 49.959
2024-10-20 | 4:51 | 49.958
2024-10-20 | 4:51 | 49.96
2024-10-20 | 4:51 | 49.962
2024-10-20 | 4:51 | 49.963
2024-10-20 | 4:51 | 49.964
2024-10-20 | 4:51 | 49.963
2024-10-20 | 4:51 | 49.967
2024-10-20 | 4:51 | 49.966
2024-10-20 | 4:51 | 49.965
2024-10-20 | 4:51 | 49.968
2024-10-20 | 4:51 | 49.967
2024-10-20 | 4:51 | 49.965
2024-10-20 | 4:51 | 49.968
2024-10-20 | 4:51 | 49.965
2024-10-20 | 4:51 | 49.964
2024-10-20 | 4:51 | 49.964
2024-10-20 | 4:51 | 49.959
2024-10-20 | 4:51 | 49.958
2024-10-20 | 4:51 | 49.96
2024-10-20 | 4:51 | 49.96
2024-10-20 | 4:51 | 49.962
2024-10-20 | 4:51 | 49.96
2024-10-20 | 4:51 | 49.962
2024-10-20 | 4:51 | 49.963
2024-10-20 | 4:51 | 49.962
2024-10-20 | 4:51 | 49.963
2024-10-20 | 4:51 | 49.961
2024-10-20 | 4:51 | 49.961
2024-10-20 | 4:51 | 49.962
2024-10-20 | 4:51 | 49.961
2024-10-20 | 4:51 | 49.964
2024-10-20 | 4:51 | 49.964
2024-10-20 | 4:51 | 49.965
2024-10-20 | 4:51 | 49.961
2024-10-20 | 4:51 | 49.96
2024-10-20 | 4:51 | 49.963
2024-10-20 | 4:51 | 49.965
2024-10-20 | 4:51 | 49.969
2024-10-20 | 4:51 | 49.967
2024-10-20 | 4:51 | 49.968
2024-10-20 | 4:51 | 49.965
2024-10-20 | 4:51 | 49.965
2024-10-20 | 4:51 | 49.968
2024-10-20 | 4:51 | 49.964
2024-10-20 | 4:51 | 49.964
2024-10-20 | 4:52 | 49.965
2024-10-20 | 4:52 | 49.963
2024-10-20 | 4:52 | 49.962
2024-10-20 | 4:52 | 49.964
2024-10-20 | 4:52 | 49.964
2024-10-20 | 4:52 | 49.965
2024-10-20 | 4:52 | 49.967
2024-10-20 | 4:52 | 49.968
2024-10-20 | 4:52 | 49.969
2024-10-20 | 4:52 | 49.972
2024-10-20 | 4:52 | 49.974
2024-10-20 | 4:52 | 49.971
2024-10-20 | 4:52 | 49.972
2024-10-20 | 4:52 | 49.973
2024-10-20 | 4:52 | 49.974
2024-10-20 | 4:52 | 49.975
2024-10-20 | 4:52 | 49.971
2024-10-20 | 4:52 | 49.968
2024-10-20 | 4:52 | 49.962
2024-10-20 | 4:52 | 49.962
2024-10-20 | 4:52 | 49.96
2024-10-20 | 4:52 | 49.957
2024-10-20 | 4:52 | 49.957
2024-10-20 | 4:52 | 49.954
2024-10-20 | 4:52 | 49.954
2024-10-20 | 4:52 | 49.952
2024-10-20 | 4:52 | 49.954
2024-10-20 | 4:52 | 49.958
2024-10-20 | 4:52 | 49.96
2024-10-20 | 4:52 | 49.963
2024-10-20 | 4:52 | 49.964
2024-10-20 | 4:52 | 49.962
2024-10-20 | 4:52 | 49.964
2024-10-20 | 4:52 | 49.962
2024-10-20 | 4:52 | 49.964
2024-10-20 | 4:52 | 49.965
2024-10-20 | 4:52 | 49.964
2024-10-20 | 4:52 | 49.965
2024-10-20 | 4:52 | 49.963
2024-10-20 | 4:52 | 49.962
2024-10-20 | 4:52 | 49.962
2024-10-20 | 4:52 | 49.96
2024-10-20 | 4:52 | 49.961
2024-10-20 | 4:52 | 49.963
2024-10-20 | 4:52 | 49.963
2024-10-20 | 4:52 | 49.967
2024-10-20 | 4:52 | 49.964
2024-10-20 | 4:52 | 49.966
2024-10-20 | 4:52 | 49.963
2024-10-20 | 4:52 | 49.967
2024-10-20 | 4:52 | 49.969
2024-10-20 | 4:52 | 49.969
2024-10-20 | 4:52 | 49.97
2024-10-20 | 4:52 | 49.968
2024-10-20 | 4:52 | 49.969
2024-10-20 | 4:52 | 49.973
2024-10-20 | 4:52 | 49.976
2024-10-20 | 4:52 | 49.978
2024-10-20 | 4:52 | 49.975
2024-10-20 | 4:52 | 49.978
2024-10-20 | 4:52 | 49.978
2024-10-20 | 4:53 | 49.979
2024-10-20 | 4:53 | 49.978
2024-10-20 | 4:53 | 49.98
2024-10-20 | 4:53 | 49.979
2024-10-20 | 4:53 | 49.977
2024-10-20 | 4:53 | 49.978
2024-10-20 | 4:53 | 49.978
2024-10-20 | 4:53 | 49.976
2024-10-20 | 4:53 | 49.979
2024-10-20 | 4:53 | 49.978
2024-10-20 | 4:53 | 49.978
2024-10-20 | 4:53 | 49.981
2024-10-20 | 4:53 | 49.982
2024-10-20 | 4:53 | 49.985
2024-10-20 | 4:53 | 49.985
2024-10-20 | 4:53 | 49.986
2024-10-20 | 4:53 | 49.984
2024-10-20 | 4:53 | 49.986
2024-10-20 | 4:53 | 49.988
2024-10-20 | 4:53 | 49.989
2024-10-20 | 4:53 | 49.991
2024-10-20 | 4:53 | 49.989
2024-10-20 | 4:53 | 49.991
2024-10-20 | 4:53 | 49.992
2024-10-20 | 4:53 | 49.993
2024-10-20 | 4:53 | 49.994
2024-10-20 | 4:53 | 49.995
2024-10-20 | 4:53 | 49.993
2024-10-20 | 4:53 | 49.992
2024-10-20 | 4:53 | 49.996
2024-10-20 | 4:53 | 49.998
2024-10-20 | 4:53 | 50.002
2024-10-20 | 4:53 | 50.005
2024-10-20 | 4:53 | 50.005
2024-10-20 | 4:53 | 50.007
2024-10-20 | 4:53 | 50.009
2024-10-20 | 4:53 | 50.009
2024-10-20 | 4:53 | 50.011
2024-10-20 | 4:53 | 50.008
2024-10-20 | 4:53 | 50.01
2024-10-20 | 4:53 | 50.008
2024-10-20 | 4:53 | 50.009
2024-10-20 | 4:53 | 50.009
2024-10-20 | 4:53 | 50.009
2024-10-20 | 4:53 | 50.011
2024-10-20 | 4:53 | 50.009
2024-10-20 | 4:53 | 50.007
2024-10-20 | 4:53 | 50.008
2024-10-20 | 4:53 | 50.006
2024-10-20 | 4:53 | 50
2024-10-20 | 4:53 | 49.996
2024-10-20 | 4:53 | 49.995
2024-10-20 | 4:53 | 49.991
2024-10-20 | 4:53 | 49.989
2024-10-20 | 4:53 | 49.985
2024-10-20 | 4:53 | 49.981
2024-10-20 | 4:53 | 49.98
2024-10-20 | 4:53 | 49.977
2024-10-20 | 4:53 | 49.98
2024-10-20 | 4:53 | 49.98
2024-10-20 | 4:54 | 49.985
2024-10-20 | 4:54 | 49.983
2024-10-20 | 4:54 | 49.984
2024-10-20 | 4:54 | 49.981
2024-10-20 | 4:54 | 49.984
2024-10-20 | 4:54 | 49.979
2024-10-20 | 4:54 | 49.979
2024-10-20 | 4:54 | 49.977
2024-10-20 | 4:54 | 49.975
2024-10-20 | 4:54 | 49.973
2024-10-20 | 4:54 | 49.974
2024-10-20 | 4:54 | 49.973
2024-10-20 | 4:54 | 49.973
2024-10-20 | 4:54 | 49.97
2024-10-20 | 4:54 | 49.969
2024-10-20 | 4:54 | 49.969
2024-10-20 | 4:54 | 49.968
2024-10-20 | 4:54 | 49.97
2024-10-20 | 4:54 | 49.968
2024-10-20 | 4:54 | 49.967
2024-10-20 | 4:54 | 49.969
2024-10-20 | 4:54 | 49.97
2024-10-20 | 4:54 | 49.971
2024-10-20 | 4:54 | 49.974
2024-10-20 | 4:54 | 49.975
2024-10-20 | 4:54 | 49.977
2024-10-20 | 4:54 | 49.979
2024-10-20 | 4:54 | 49.981
2024-10-20 | 4:54 | 49.984
2024-10-20 | 4:54 | 49.987

## 20241021-1
In GMT
Date | Time | Freq
2024-10-21 | 13:14 | 49.984 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-10-21 | 13:14 | 49.979 | 222 | BRITNED | 676.211
2024-10-21 | 13:14 | 49.976 | 268 | WBURB-2 | 428.156
2024-10-21 | 13:14 | 49.974 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-10-21 | 13:14 | 49.973 |  | Viking Link | -648.9
2024-10-21 | 13:14 | 49.969 |  | Viking Link | 1398.96
2024-10-21 | 13:14 | 49.971 | 209 | DRAXX-3 | 626.95
2024-10-21 | 13:14 | 49.967 | 154 | CDCL-1 | 391.57
2024-10-21 | 13:14 | 49.965 | 268 | ROCK-1 | 468.495
2024-10-21 | 13:14 | 49.964 | 148 | IFA Bipole1 | 945.473
2024-10-21 | 13:14 | 49.965 | 132 | IFA Bipole1 | 999.1
2024-10-21 | 13:14 | 49.968 | 141 | IFA Bipole2 | 1000
2024-10-21 | 13:14 | 49.964 | 135 | IFA Bipole1 | 996.75
2024-10-21 | 13:14 | 49.965 |  | Viking Link | -780.3
2024-10-21 | 13:14 | 49.962
2024-10-21 | 13:14 | 49.962
2024-10-21 | 13:14 | 49.961
2024-10-21 | 13:14 | 49.959
2024-10-21 | 13:14 | 49.962
2024-10-21 | 13:14 | 49.961 | 130 | HEYM12 | 271.908
2024-10-21 | 13:14 | 49.96 | 228 | HUMR-1 | 303.75
2024-10-21 | 13:14 | 49.961
2024-10-21 | 13:14 | 49.964
2024-10-21 | 13:14 | 49.966
2024-10-21 | 13:14 | 49.968
2024-10-21 | 13:14 | 49.969
2024-10-21 | 13:14 | 49.973
2024-10-21 | 13:14 | 49.975
2024-10-21 | 13:14 | 49.978
2024-10-21 | 13:14 | 49.984
2024-10-21 | 13:14 | 49.988 | 211 | CDCL-1 | 291.5
2024-10-21 | 13:15 | 49.984 | 199 | STAY-2 | 413.125
2024-10-21 | 13:15 | 49.988 | 173 | CDCL-1 | 397.375
2024-10-21 | 13:15 | 49.988 | 248 | SEAB-2 | 361.25
2024-10-21 | 13:15 | 49.989 | 255 | FRANCE | 995.65
2024-10-21 | 13:15 | 49.993 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-10-21 | 13:15 | 49.998
2024-10-21 | 13:15 | 50.002
2024-10-21 | 13:15 | 50.005
2024-10-21 | 13:15 | 50.011
2024-10-21 | 13:15 | 50.016
2024-10-21 | 13:15 | 50.019
2024-10-21 | 13:15 | 50.021
2024-10-21 | 13:15 | 50.02
2024-10-21 | 13:15 | 50.021
2024-10-21 | 13:15 | 50.023
2024-10-21 | 13:15 | 50.021
2024-10-21 | 13:15 | 50.021
2024-10-21 | 13:15 | 50.019
2024-10-21 | 13:15 | 50.017
2024-10-21 | 13:15 | 50.012
2024-10-21 | 13:15 | 50.01
2024-10-21 | 13:15 | 50.009
2024-10-21 | 13:15 | 50.01
2024-10-21 | 13:15 | 50.012
2024-10-21 | 13:15 | 50.009
2024-10-21 | 13:15 | 50.004
2024-10-21 | 13:15 | 50.004
2024-10-21 | 13:15 | 49.999
2024-10-21 | 13:15 | 49.998
2024-10-21 | 13:15 | 50
2024-10-21 | 13:15 | 49.999
2024-10-21 | 13:15 | 49.998
2024-10-21 | 13:15 | 49.996
2024-10-21 | 13:15 | 49.996
2024-10-21 | 13:15 | 49.995
2024-10-21 | 13:15 | 49.993
2024-10-21 | 13:15 | 49.992
2024-10-21 | 13:15 | 49.992
2024-10-21 | 13:15 | 49.99
2024-10-21 | 13:15 | 49.987
2024-10-21 | 13:15 | 49.983
2024-10-21 | 13:15 | 49.979
2024-10-21 | 13:15 | 49.977
2024-10-21 | 13:15 | 49.978
2024-10-21 | 13:15 | 49.976
2024-10-21 | 13:15 | 49.978
2024-10-21 | 13:15 | 49.977
2024-10-21 | 13:15 | 49.979
2024-10-21 | 13:15 | 49.976
2024-10-21 | 13:15 | 49.978
2024-10-21 | 13:15 | 49.979
2024-10-21 | 13:15 | 49.98
2024-10-21 | 13:15 | 49.98
2024-10-21 | 13:15 | 49.98
2024-10-21 | 13:15 | 49.969
2024-10-21 | 13:15 | 49.945
2024-10-21 | 13:15 | 49.932
2024-10-21 | 13:15 | 49.924
2024-10-21 | 13:15 | 49.92
2024-10-21 | 13:16 | 49.917
2024-10-21 | 13:16 | 49.915
2024-10-21 | 13:16 | 49.911
2024-10-21 | 13:16 | 49.911
2024-10-21 | 13:16 | 49.91
2024-10-21 | 13:16 | 49.907
2024-10-21 | 13:16 | 49.907
2024-10-21 | 13:16 | 49.903
2024-10-21 | 13:16 | 49.9
2024-10-21 | 13:16 | 49.895
2024-10-21 | 13:16 | 49.89
2024-10-21 | 13:16 | 49.889
2024-10-21 | 13:16 | 49.888
2024-10-21 | 13:16 | 49.89
2024-10-21 | 13:16 | 49.891
2024-10-21 | 13:16 | 49.892
2024-10-21 | 13:16 | 49.894
2024-10-21 | 13:16 | 49.892
2024-10-21 | 13:16 | 49.892
2024-10-21 | 13:16 | 49.893
2024-10-21 | 13:16 | 49.896
2024-10-21 | 13:16 | 49.898
2024-10-21 | 13:16 | 49.899
2024-10-21 | 13:16 | 49.898
2024-10-21 | 13:16 | 49.895
2024-10-21 | 13:16 | 49.892
2024-10-21 | 13:16 | 49.893
2024-10-21 | 13:16 | 49.893
2024-10-21 | 13:16 | 49.893
2024-10-21 | 13:16 | 49.894
2024-10-21 | 13:16 | 49.898
2024-10-21 | 13:16 | 49.899
2024-10-21 | 13:16 | 49.899
2024-10-21 | 13:16 | 49.901
2024-10-21 | 13:16 | 49.904
2024-10-21 | 13:16 | 49.902
2024-10-21 | 13:16 | 49.901
2024-10-21 | 13:16 | 49.9
2024-10-21 | 13:16 | 49.9
2024-10-21 | 13:16 | 49.897
2024-10-21 | 13:16 | 49.896
2024-10-21 | 13:16 | 49.893
2024-10-21 | 13:16 | 49.893
2024-10-21 | 13:16 | 49.891
2024-10-21 | 13:16 | 49.891
2024-10-21 | 13:16 | 49.894
2024-10-21 | 13:16 | 49.895
2024-10-21 | 13:16 | 49.895
2024-10-21 | 13:16 | 49.9
2024-10-21 | 13:16 | 49.902
2024-10-21 | 13:16 | 49.903
2024-10-21 | 13:16 | 49.905
2024-10-21 | 13:16 | 49.906
2024-10-21 | 13:16 | 49.909
2024-10-21 | 13:16 | 49.912
2024-10-21 | 13:16 | 49.917
2024-10-21 | 13:16 | 49.919
2024-10-21 | 13:16 | 49.921
2024-10-21 | 13:16 | 49.921
2024-10-21 | 13:16 | 49.921
2024-10-21 | 13:16 | 49.926
2024-10-21 | 13:17 | 49.929
2024-10-21 | 13:17 | 49.931
2024-10-21 | 13:17 | 49.933
2024-10-21 | 13:17 | 49.936
2024-10-21 | 13:17 | 49.932
2024-10-21 | 13:17 | 49.932
2024-10-21 | 13:17 | 49.934
2024-10-21 | 13:17 | 49.936
2024-10-21 | 13:17 | 49.937
2024-10-21 | 13:17 | 49.936
2024-10-21 | 13:17 | 49.94
2024-10-21 | 13:17 | 49.94
2024-10-21 | 13:17 | 49.941
2024-10-21 | 13:17 | 49.938
2024-10-21 | 13:17 | 49.934
2024-10-21 | 13:17 | 49.933
2024-10-21 | 13:17 | 49.933
2024-10-21 | 13:17 | 49.931
2024-10-21 | 13:17 | 49.93
2024-10-21 | 13:17 | 49.932
2024-10-21 | 13:17 | 49.932
2024-10-21 | 13:17 | 49.928
2024-10-21 | 13:17 | 49.928
2024-10-21 | 13:17 | 49.926
2024-10-21 | 13:17 | 49.922
2024-10-21 | 13:17 | 49.924
2024-10-21 | 13:17 | 49.925
2024-10-21 | 13:17 | 49.923
2024-10-21 | 13:17 | 49.926
2024-10-21 | 13:17 | 49.926
2024-10-21 | 13:17 | 49.922
2024-10-21 | 13:17 | 49.922
2024-10-21 | 13:17 | 49.924
2024-10-21 | 13:17 | 49.923
2024-10-21 | 13:17 | 49.924
2024-10-21 | 13:17 | 49.925
2024-10-21 | 13:17 | 49.921
2024-10-21 | 13:17 | 49.921
2024-10-21 | 13:17 | 49.917
2024-10-21 | 13:17 | 49.919
2024-10-21 | 13:17 | 49.916
2024-10-21 | 13:17 | 49.914
2024-10-21 | 13:17 | 49.909
2024-10-21 | 13:17 | 49.908
2024-10-21 | 13:17 | 49.905
2024-10-21 | 13:17 | 49.906
2024-10-21 | 13:17 | 49.906
2024-10-21 | 13:17 | 49.905
2024-10-21 | 13:17 | 49.906
2024-10-21 | 13:17 | 49.906
2024-10-21 | 13:17 | 49.902
2024-10-21 | 13:17 | 49.902
2024-10-21 | 13:17 | 49.903
2024-10-21 | 13:17 | 49.902
2024-10-21 | 13:17 | 49.904
2024-10-21 | 13:17 | 49.906
2024-10-21 | 13:17 | 49.903
2024-10-21 | 13:17 | 49.903
2024-10-21 | 13:17 | 49.904
2024-10-21 | 13:17 | 49.903
2024-10-21 | 13:18 | 49.901
2024-10-21 | 13:18 | 49.902
2024-10-21 | 13:18 | 49.904
2024-10-21 | 13:18 | 49.905
2024-10-21 | 13:18 | 49.904
2024-10-21 | 13:18 | 49.902
2024-10-21 | 13:18 | 49.902
2024-10-21 | 13:18 | 49.902
2024-10-21 | 13:18 | 49.903
2024-10-21 | 13:18 | 49.901
2024-10-21 | 13:18 | 49.898
2024-10-21 | 13:18 | 49.896
2024-10-21 | 13:18 | 49.897
2024-10-21 | 13:18 | 49.897
2024-10-21 | 13:18 | 49.893
2024-10-21 | 13:18 | 49.893
2024-10-21 | 13:18 | 49.893
2024-10-21 | 13:18 | 49.891
2024-10-21 | 13:18 | 49.891
2024-10-21 | 13:18 | 49.891
2024-10-21 | 13:18 | 49.89
2024-10-21 | 13:18 | 49.889
2024-10-21 | 13:18 | 49.892
2024-10-21 | 13:18 | 49.891
2024-10-21 | 13:18 | 49.888
2024-10-21 | 13:18 | 49.889
2024-10-21 | 13:18 | 49.888
2024-10-21 | 13:18 | 49.884
2024-10-21 | 13:18 | 49.885
2024-10-21 | 13:18 | 49.888
2024-10-21 | 13:18 | 49.887
2024-10-21 | 13:18 | 49.885
2024-10-21 | 13:18 | 49.885
2024-10-21 | 13:18 | 49.888
2024-10-21 | 13:18 | 49.893
2024-10-21 | 13:18 | 49.897
2024-10-21 | 13:18 | 49.899
2024-10-21 | 13:18 | 49.904
2024-10-21 | 13:18 | 49.904
2024-10-21 | 13:18 | 49.905
2024-10-21 | 13:18 | 49.904
2024-10-21 | 13:18 | 49.903
2024-10-21 | 13:18 | 49.901
2024-10-21 | 13:18 | 49.901
2024-10-21 | 13:18 | 49.898
2024-10-21 | 13:18 | 49.895
2024-10-21 | 13:18 | 49.891
2024-10-21 | 13:18 | 49.887
2024-10-21 | 13:18 | 49.887
2024-10-21 | 13:18 | 49.886
2024-10-21 | 13:18 | 49.888
2024-10-21 | 13:18 | 49.891
2024-10-21 | 13:18 | 49.894
2024-10-21 | 13:18 | 49.895
2024-10-21 | 13:18 | 49.895
2024-10-21 | 13:18 | 49.894
2024-10-21 | 13:18 | 49.896
2024-10-21 | 13:18 | 49.897
2024-10-21 | 13:18 | 49.896
2024-10-21 | 13:19 | 49.896
2024-10-21 | 13:19 | 49.897
2024-10-21 | 13:19 | 49.896
2024-10-21 | 13:19 | 49.897
2024-10-21 | 13:19 | 49.9
2024-10-21 | 13:19 | 49.901
2024-10-21 | 13:19 | 49.899
2024-10-21 | 13:19 | 49.899
2024-10-21 | 13:19 | 49.901
2024-10-21 | 13:19 | 49.899
2024-10-21 | 13:19 | 49.898
2024-10-21 | 13:19 | 49.896
2024-10-21 | 13:19 | 49.896
2024-10-21 | 13:19 | 49.895
2024-10-21 | 13:19 | 49.894
2024-10-21 | 13:19 | 49.891
2024-10-21 | 13:19 | 49.889
2024-10-21 | 13:19 | 49.888
2024-10-21 | 13:19 | 49.887
2024-10-21 | 13:19 | 49.885
2024-10-21 | 13:19 | 49.884
2024-10-21 | 13:19 | 49.887
2024-10-21 | 13:19 | 49.887
2024-10-21 | 13:19 | 49.886
2024-10-21 | 13:19 | 49.887
2024-10-21 | 13:19 | 49.887
2024-10-21 | 13:19 | 49.887
2024-10-21 | 13:19 | 49.885
2024-10-21 | 13:19 | 49.885
2024-10-21 | 13:19 | 49.886
2024-10-21 | 13:19 | 49.887
2024-10-21 | 13:19 | 49.886
2024-10-21 | 13:19 | 49.888
2024-10-21 | 13:19 | 49.891
2024-10-21 | 13:19 | 49.893
2024-10-21 | 13:19 | 49.894
2024-10-21 | 13:19 | 49.895
2024-10-21 | 13:19 | 49.896
2024-10-21 | 13:19 | 49.896
2024-10-21 | 13:19 | 49.893
2024-10-21 | 13:19 | 49.894
2024-10-21 | 13:19 | 49.892
2024-10-21 | 13:19 | 49.893
2024-10-21 | 13:19 | 49.894
2024-10-21 | 13:19 | 49.897
2024-10-21 | 13:19 | 49.899
2024-10-21 | 13:19 | 49.901
2024-10-21 | 13:19 | 49.902
2024-10-21 | 13:19 | 49.902
2024-10-21 | 13:19 | 49.901
2024-10-21 | 13:19 | 49.902
2024-10-21 | 13:19 | 49.9
2024-10-21 | 13:19 | 49.902
2024-10-21 | 13:19 | 49.901
2024-10-21 | 13:19 | 49.898
2024-10-21 | 13:19 | 49.896
2024-10-21 | 13:19 | 49.893
2024-10-21 | 13:19 | 49.892
2024-10-21 | 13:19 | 49.895
2024-10-21 | 13:19 | 49.898
2024-10-21 | 13:19 | 49.899
2024-10-21 | 13:20 | 49.903
2024-10-21 | 13:20 | 49.905
2024-10-21 | 13:20 | 49.908
2024-10-21 | 13:20 | 49.907
2024-10-21 | 13:20 | 49.908
2024-10-21 | 13:20 | 49.907
2024-10-21 | 13:20 | 49.909
2024-10-21 | 13:20 | 49.91
2024-10-21 | 13:20 | 49.908
2024-10-21 | 13:20 | 49.908
2024-10-21 | 13:20 | 49.909
2024-10-21 | 13:20 | 49.907
2024-10-21 | 13:20 | 49.911
2024-10-21 | 13:20 | 49.911
2024-10-21 | 13:20 | 49.912
2024-10-21 | 13:20 | 49.908
2024-10-21 | 13:20 | 49.907
2024-10-21 | 13:20 | 49.906
2024-10-21 | 13:20 | 49.908
2024-10-21 | 13:20 | 49.906
2024-10-21 | 13:20 | 49.902
2024-10-21 | 13:20 | 49.9
2024-10-21 | 13:20 | 49.901
2024-10-21 | 13:20 | 49.9
2024-10-21 | 13:20 | 49.896
2024-10-21 | 13:20 | 49.895
2024-10-21 | 13:20 | 49.896
2024-10-21 | 13:20 | 49.896
2024-10-21 | 13:20 | 49.898
2024-10-21 | 13:20 | 49.901
2024-10-21 | 13:20 | 49.899
2024-10-21 | 13:20 | 49.899
2024-10-21 | 13:20 | 49.897
2024-10-21 | 13:20 | 49.897
2024-10-21 | 13:20 | 49.899
2024-10-21 | 13:20 | 49.9
2024-10-21 | 13:20 | 49.901
2024-10-21 | 13:20 | 49.899
2024-10-21 | 13:20 | 49.898
2024-10-21 | 13:20 | 49.896
2024-10-21 | 13:20 | 49.896
2024-10-21 | 13:20 | 49.898
2024-10-21 | 13:20 | 49.898
2024-10-21 | 13:20 | 49.897
2024-10-21 | 13:20 | 49.898
2024-10-21 | 13:20 | 49.9
2024-10-21 | 13:20 | 49.903
2024-10-21 | 13:20 | 49.908
2024-10-21 | 13:20 | 49.91
2024-10-21 | 13:20 | 49.912
2024-10-21 | 13:20 | 49.913
2024-10-21 | 13:20 | 49.911
2024-10-21 | 13:20 | 49.912
2024-10-21 | 13:20 | 49.909
2024-10-21 | 13:20 | 49.91
2024-10-21 | 13:20 | 49.91
2024-10-21 | 13:20 | 49.91
2024-10-21 | 13:20 | 49.911
2024-10-21 | 13:20 | 49.908
2024-10-21 | 13:21 | 49.909
2024-10-21 | 13:21 | 49.908
2024-10-21 | 13:21 | 49.908
2024-10-21 | 13:21 | 49.911
2024-10-21 | 13:21 | 49.913
2024-10-21 | 13:21 | 49.915
2024-10-21 | 13:21 | 49.919
2024-10-21 | 13:21 | 49.922
2024-10-21 | 13:21 | 49.922
2024-10-21 | 13:21 | 49.922
2024-10-21 | 13:21 | 49.923
2024-10-21 | 13:21 | 49.921
2024-10-21 | 13:21 | 49.921
2024-10-21 | 13:21 | 49.921
2024-10-21 | 13:21 | 49.92
2024-10-21 | 13:21 | 49.918
2024-10-21 | 13:21 | 49.919
2024-10-21 | 13:21 | 49.917
2024-10-21 | 13:21 | 49.914
2024-10-21 | 13:21 | 49.91
2024-10-21 | 13:21 | 49.908
2024-10-21 | 13:21 | 49.907
2024-10-21 | 13:21 | 49.904
2024-10-21 | 13:21 | 49.903
2024-10-21 | 13:21 | 49.903
2024-10-21 | 13:21 | 49.902
2024-10-21 | 13:21 | 49.9
2024-10-21 | 13:21 | 49.899
2024-10-21 | 13:21 | 49.897
2024-10-21 | 13:21 | 49.898
2024-10-21 | 13:21 | 49.899
2024-10-21 | 13:21 | 49.896
2024-10-21 | 13:21 | 49.894
2024-10-21 | 13:21 | 49.894
2024-10-21 | 13:21 | 49.89
2024-10-21 | 13:21 | 49.889
2024-10-21 | 13:21 | 49.889
2024-10-21 | 13:21 | 49.889
2024-10-21 | 13:21 | 49.891
2024-10-21 | 13:21 | 49.889
2024-10-21 | 13:21 | 49.888
2024-10-21 | 13:21 | 49.888
2024-10-21 | 13:21 | 49.888
2024-10-21 | 13:21 | 49.889
2024-10-21 | 13:21 | 49.889
2024-10-21 | 13:21 | 49.89
2024-10-21 | 13:21 | 49.89
2024-10-21 | 13:21 | 49.889
2024-10-21 | 13:21 | 49.89
2024-10-21 | 13:21 | 49.893
2024-10-21 | 13:21 | 49.894
2024-10-21 | 13:21 | 49.892
2024-10-21 | 13:21 | 49.89
2024-10-21 | 13:21 | 49.891
2024-10-21 | 13:21 | 49.893
2024-10-21 | 13:21 | 49.892
2024-10-21 | 13:21 | 49.891
2024-10-21 | 13:21 | 49.893
2024-10-21 | 13:21 | 49.893
2024-10-21 | 13:21 | 49.89
2024-10-21 | 13:21 | 49.89
2024-10-21 | 13:22 | 49.891
2024-10-21 | 13:22 | 49.89
2024-10-21 | 13:22 | 49.888
2024-10-21 | 13:22 | 49.889
2024-10-21 | 13:22 | 49.891
2024-10-21 | 13:22 | 49.893
2024-10-21 | 13:22 | 49.893
2024-10-21 | 13:22 | 49.894
2024-10-21 | 13:22 | 49.896
2024-10-21 | 13:22 | 49.895
2024-10-21 | 13:22 | 49.897
2024-10-21 | 13:22 | 49.9
2024-10-21 | 13:22 | 49.901
2024-10-21 | 13:22 | 49.901
2024-10-21 | 13:22 | 49.9
2024-10-21 | 13:22 | 49.898
2024-10-21 | 13:22 | 49.895
2024-10-21 | 13:22 | 49.893
2024-10-21 | 13:22 | 49.89
2024-10-21 | 13:22 | 49.89
2024-10-21 | 13:22 | 49.891
2024-10-21 | 13:22 | 49.892
2024-10-21 | 13:22 | 49.893
2024-10-21 | 13:22 | 49.894
2024-10-21 | 13:22 | 49.894
2024-10-21 | 13:22 | 49.893
2024-10-21 | 13:22 | 49.895
2024-10-21 | 13:22 | 49.892
2024-10-21 | 13:22 | 49.888
2024-10-21 | 13:22 | 49.887
2024-10-21 | 13:22 | 49.884
2024-10-21 | 13:22 | 49.883
2024-10-21 | 13:22 | 49.882
2024-10-21 | 13:22 | 49.883
2024-10-21 | 13:22 | 49.881
2024-10-21 | 13:22 | 49.882
2024-10-21 | 13:22 | 49.88
2024-10-21 | 13:22 | 49.883
2024-10-21 | 13:22 | 49.884
2024-10-21 | 13:22 | 49.885
2024-10-21 | 13:22 | 49.885
2024-10-21 | 13:22 | 49.885
2024-10-21 | 13:22 | 49.887
2024-10-21 | 13:22 | 49.888
2024-10-21 | 13:22 | 49.887
2024-10-21 | 13:22 | 49.889
2024-10-21 | 13:22 | 49.89
2024-10-21 | 13:22 | 49.89
2024-10-21 | 13:22 | 49.891
2024-10-21 | 13:22 | 49.892
2024-10-21 | 13:22 | 49.892
2024-10-21 | 13:22 | 49.893
2024-10-21 | 13:22 | 49.893
2024-10-21 | 13:22 | 49.896
2024-10-21 | 13:22 | 49.897
2024-10-21 | 13:22 | 49.897
2024-10-21 | 13:22 | 49.898
2024-10-21 | 13:22 | 49.898
2024-10-21 | 13:22 | 49.9
2024-10-21 | 13:23 | 49.9
2024-10-21 | 13:23 | 49.9
2024-10-21 | 13:23 | 49.899
2024-10-21 | 13:23 | 49.895
2024-10-21 | 13:23 | 49.895
2024-10-21 | 13:23 | 49.894
2024-10-21 | 13:23 | 49.894
2024-10-21 | 13:23 | 49.899
2024-10-21 | 13:23 | 49.898
2024-10-21 | 13:23 | 49.9
2024-10-21 | 13:23 | 49.902
2024-10-21 | 13:23 | 49.903
2024-10-21 | 13:23 | 49.903
2024-10-21 | 13:23 | 49.903
2024-10-21 | 13:23 | 49.902
2024-10-21 | 13:23 | 49.9
2024-10-21 | 13:23 | 49.894
2024-10-21 | 13:23 | 49.895
2024-10-21 | 13:23 | 49.895
2024-10-21 | 13:23 | 49.897
2024-10-21 | 13:23 | 49.898
2024-10-21 | 13:23 | 49.9
2024-10-21 | 13:23 | 49.9
2024-10-21 | 13:23 | 49.901
2024-10-21 | 13:23 | 49.903
2024-10-21 | 13:23 | 49.904
2024-10-21 | 13:23 | 49.903
2024-10-21 | 13:23 | 49.902
2024-10-21 | 13:23 | 49.901
2024-10-21 | 13:23 | 49.899
2024-10-21 | 13:23 | 49.9
2024-10-21 | 13:23 | 49.894
2024-10-21 | 13:23 | 49.892
2024-10-21 | 13:23 | 49.894
2024-10-21 | 13:23 | 49.897
2024-10-21 | 13:23 | 49.896
2024-10-21 | 13:23 | 49.896
2024-10-21 | 13:23 | 49.896
2024-10-21 | 13:23 | 49.896
2024-10-21 | 13:23 | 49.898
2024-10-21 | 13:23 | 49.897
2024-10-21 | 13:23 | 49.899
2024-10-21 | 13:23 | 49.897
2024-10-21 | 13:23 | 49.897
2024-10-21 | 13:23 | 49.9
2024-10-21 | 13:23 | 49.9
2024-10-21 | 13:23 | 49.902
2024-10-21 | 13:23 | 49.902
2024-10-21 | 13:23 | 49.908
2024-10-21 | 13:23 | 49.909
2024-10-21 | 13:23 | 49.914
2024-10-21 | 13:23 | 49.915
2024-10-21 | 13:23 | 49.919
2024-10-21 | 13:23 | 49.92
2024-10-21 | 13:23 | 49.92
2024-10-21 | 13:23 | 49.919
2024-10-21 | 13:23 | 49.915
2024-10-21 | 13:23 | 49.915
2024-10-21 | 13:23 | 49.915
2024-10-21 | 13:23 | 49.913
2024-10-21 | 13:23 | 49.908
2024-10-21 | 13:24 | 49.907
2024-10-21 | 13:24 | 49.906
2024-10-21 | 13:24 | 49.906
2024-10-21 | 13:24 | 49.909
2024-10-21 | 13:24 | 49.908
2024-10-21 | 13:24 | 49.907
2024-10-21 | 13:24 | 49.907
2024-10-21 | 13:24 | 49.91
2024-10-21 | 13:24 | 49.913
2024-10-21 | 13:24 | 49.912
2024-10-21 | 13:24 | 49.912
2024-10-21 | 13:24 | 49.912
2024-10-21 | 13:24 | 49.911
2024-10-21 | 13:24 | 49.909
2024-10-21 | 13:24 | 49.911
2024-10-21 | 13:24 | 49.911
2024-10-21 | 13:24 | 49.909
2024-10-21 | 13:24 | 49.91
2024-10-21 | 13:24 | 49.908
2024-10-21 | 13:24 | 49.91
2024-10-21 | 13:24 | 49.91
2024-10-21 | 13:24 | 49.91
2024-10-21 | 13:24 | 49.912
2024-10-21 | 13:24 | 49.911
2024-10-21 | 13:24 | 49.913
2024-10-21 | 13:24 | 49.912
2024-10-21 | 13:24 | 49.913
2024-10-21 | 13:24 | 49.912
2024-10-21 | 13:24 | 49.913
2024-10-21 | 13:24 | 49.91
2024-10-21 | 13:24 | 49.908
2024-10-21 | 13:24 | 49.904
2024-10-21 | 13:24 | 49.903
2024-10-21 | 13:24 | 49.903
2024-10-21 | 13:24 | 49.904
2024-10-21 | 13:24 | 49.909
2024-10-21 | 13:24 | 49.91
2024-10-21 | 13:24 | 49.911
2024-10-21 | 13:24 | 49.912
2024-10-21 | 13:24 | 49.914
2024-10-21 | 13:24 | 49.914
2024-10-21 | 13:24 | 49.913
2024-10-21 | 13:24 | 49.911
2024-10-21 | 13:24 | 49.909
2024-10-21 | 13:24 | 49.906
2024-10-21 | 13:24 | 49.906
2024-10-21 | 13:24 | 49.906
2024-10-21 | 13:24 | 49.904
2024-10-21 | 13:24 | 49.903
2024-10-21 | 13:24 | 49.902
2024-10-21 | 13:24 | 49.902
2024-10-21 | 13:24 | 49.901
2024-10-21 | 13:24 | 49.9
2024-10-21 | 13:24 | 49.902
2024-10-21 | 13:24 | 49.899
2024-10-21 | 13:24 | 49.9
2024-10-21 | 13:24 | 49.902
2024-10-21 | 13:24 | 49.901
2024-10-21 | 13:24 | 49.902
2024-10-21 | 13:25 | 49.905
2024-10-21 | 13:25 | 49.903
2024-10-21 | 13:25 | 49.906
2024-10-21 | 13:25 | 49.905
2024-10-21 | 13:25 | 49.906
2024-10-21 | 13:25 | 49.904
2024-10-21 | 13:25 | 49.904
2024-10-21 | 13:25 | 49.903
2024-10-21 | 13:25 | 49.901
2024-10-21 | 13:25 | 49.902
2024-10-21 | 13:25 | 49.901
2024-10-21 | 13:25 | 49.901
2024-10-21 | 13:25 | 49.901
2024-10-21 | 13:25 | 49.902
2024-10-21 | 13:25 | 49.901
2024-10-21 | 13:25 | 49.901
2024-10-21 | 13:25 | 49.902
2024-10-21 | 13:25 | 49.9
2024-10-21 | 13:25 | 49.905
2024-10-21 | 13:25 | 49.908
2024-10-21 | 13:25 | 49.913
2024-10-21 | 13:25 | 49.917
2024-10-21 | 13:25 | 49.919
2024-10-21 | 13:25 | 49.918
2024-10-21 | 13:25 | 49.918
2024-10-21 | 13:25 | 49.92
2024-10-21 | 13:25 | 49.923
2024-10-21 | 13:25 | 49.921
2024-10-21 | 13:25 | 49.918
2024-10-21 | 13:25 | 49.917
2024-10-21 | 13:25 | 49.917
2024-10-21 | 13:25 | 49.916
2024-10-21 | 13:25 | 49.912
2024-10-21 | 13:25 | 49.908
2024-10-21 | 13:25 | 49.908
2024-10-21 | 13:25 | 49.906
2024-10-21 | 13:25 | 49.907
2024-10-21 | 13:25 | 49.91
2024-10-21 | 13:25 | 49.916
2024-10-21 | 13:25 | 49.922
2024-10-21 | 13:25 | 49.927
2024-10-21 | 13:25 | 49.927
2024-10-21 | 13:25 | 49.931
2024-10-21 | 13:25 | 49.933
2024-10-21 | 13:25 | 49.938
2024-10-21 | 13:25 | 49.941
2024-10-21 | 13:25 | 49.942
2024-10-21 | 13:25 | 49.942
2024-10-21 | 13:25 | 49.941
2024-10-21 | 13:25 | 49.937
2024-10-21 | 13:25 | 49.937
2024-10-21 | 13:25 | 49.938
2024-10-21 | 13:25 | 49.94
2024-10-21 | 13:25 | 49.942
2024-10-21 | 13:25 | 49.944
2024-10-21 | 13:25 | 49.946
2024-10-21 | 13:25 | 49.947
2024-10-21 | 13:25 | 49.948
2024-10-21 | 13:25 | 49.949
2024-10-21 | 13:25 | 49.947
2024-10-21 | 13:25 | 49.948
2024-10-21 | 13:26 | 49.947
2024-10-21 | 13:26 | 49.948
2024-10-21 | 13:26 | 49.952
2024-10-21 | 13:26 | 49.955
2024-10-21 | 13:26 | 49.956
2024-10-21 | 13:26 | 49.959
2024-10-21 | 13:26 | 49.962
2024-10-21 | 13:26 | 49.958
2024-10-21 | 13:26 | 49.958
2024-10-21 | 13:26 | 49.956
2024-10-21 | 13:26 | 49.954
2024-10-21 | 13:26 | 49.955
2024-10-21 | 13:26 | 49.957
2024-10-21 | 13:26 | 49.959
2024-10-21 | 13:26 | 49.961
2024-10-21 | 13:26 | 49.959
2024-10-21 | 13:26 | 49.962
2024-10-21 | 13:26 | 49.964
2024-10-21 | 13:26 | 49.969
2024-10-21 | 13:26 | 49.971
2024-10-21 | 13:26 | 49.975
2024-10-21 | 13:26 | 49.974
2024-10-21 | 13:26 | 49.975
2024-10-21 | 13:26 | 49.975
2024-10-21 | 13:26 | 49.978
2024-10-21 | 13:26 | 49.981
2024-10-21 | 13:26 | 49.985
2024-10-21 | 13:26 | 49.987
2024-10-21 | 13:26 | 49.991
2024-10-21 | 13:26 | 49.991
2024-10-21 | 13:26 | 49.99
2024-10-21 | 13:26 | 49.988
2024-10-21 | 13:26 | 49.987
2024-10-21 | 13:26 | 49.986
2024-10-21 | 13:26 | 49.987
2024-10-21 | 13:26 | 49.985
2024-10-21 | 13:26 | 49.986
2024-10-21 | 13:26 | 49.984
2024-10-21 | 13:26 | 49.985
2024-10-21 | 13:26 | 49.986
2024-10-21 | 13:26 | 49.984
2024-10-21 | 13:26 | 49.983
2024-10-21 | 13:26 | 49.982
2024-10-21 | 13:26 | 49.982
2024-10-21 | 13:26 | 49.979
2024-10-21 | 13:26 | 49.979
2024-10-21 | 13:26 | 49.977
2024-10-21 | 13:26 | 49.975
2024-10-21 | 13:26 | 49.975
2024-10-21 | 13:26 | 49.971
2024-10-21 | 13:26 | 49.969
2024-10-21 | 13:26 | 49.967
2024-10-21 | 13:26 | 49.967
2024-10-21 | 13:26 | 49.968
2024-10-21 | 13:26 | 49.966
2024-10-21 | 13:26 | 49.969
2024-10-21 | 13:26 | 49.968
2024-10-21 | 13:26 | 49.97
2024-10-21 | 13:26 | 49.971
2024-10-21 | 13:26 | 49.973
2024-10-21 | 13:27 | 49.974
2024-10-21 | 13:27 | 49.977
2024-10-21 | 13:27 | 49.977
2024-10-21 | 13:27 | 49.974
2024-10-21 | 13:27 | 49.973
2024-10-21 | 13:27 | 49.968
2024-10-21 | 13:27 | 49.966
2024-10-21 | 13:27 | 49.967
2024-10-21 | 13:27 | 49.966
2024-10-21 | 13:27 | 49.967
2024-10-21 | 13:27 | 49.968
2024-10-21 | 13:27 | 49.971
2024-10-21 | 13:27 | 49.973
2024-10-21 | 13:27 | 49.975
2024-10-21 | 13:27 | 49.976
2024-10-21 | 13:27 | 49.978
2024-10-21 | 13:27 | 49.978
2024-10-21 | 13:27 | 49.981
2024-10-21 | 13:27 | 49.981
2024-10-21 | 13:27 | 49.978
2024-10-21 | 13:27 | 49.978
2024-10-21 | 13:27 | 49.98
2024-10-21 | 13:27 | 49.978
2024-10-21 | 13:27 | 49.977
2024-10-21 | 13:27 | 49.976
2024-10-21 | 13:27 | 49.978
2024-10-21 | 13:27 | 49.98
2024-10-21 | 13:27 | 49.984
2024-10-21 | 13:27 | 49.987
2024-10-21 | 13:27 | 49.991
2024-10-21 | 13:27 | 49.995
2024-10-21 | 13:27 | 49.995
2024-10-21 | 13:27 | 49.999
2024-10-21 | 13:27 | 50
2024-10-21 | 13:27 | 50
2024-10-21 | 13:27 | 50.004
2024-10-21 | 13:27 | 50.004
2024-10-21 | 13:27 | 50.003
2024-10-21 | 13:27 | 49.998
2024-10-21 | 13:27 | 49.995
2024-10-21 | 13:27 | 49.99
2024-10-21 | 13:27 | 49.987
2024-10-21 | 13:27 | 49.984
2024-10-21 | 13:27 | 49.98
2024-10-21 | 13:27 | 49.98
2024-10-21 | 13:27 | 49.976
2024-10-21 | 13:27 | 49.975
2024-10-21 | 13:27 | 49.973
2024-10-21 | 13:27 | 49.974
2024-10-21 | 13:27 | 49.974
2024-10-21 | 13:27 | 49.976
2024-10-21 | 13:27 | 49.976
2024-10-21 | 13:27 | 49.979
2024-10-21 | 13:27 | 49.98
2024-10-21 | 13:27 | 49.981
2024-10-21 | 13:27 | 49.981
2024-10-21 | 13:27 | 49.979
2024-10-21 | 13:27 | 49.979
2024-10-21 | 13:27 | 49.979
2024-10-21 | 13:28 | 49.981
2024-10-21 | 13:28 | 49.979
2024-10-21 | 13:28 | 49.974
2024-10-21 | 13:28 | 49.972
2024-10-21 | 13:28 | 49.972
2024-10-21 | 13:28 | 49.968
2024-10-21 | 13:28 | 49.966
2024-10-21 | 13:28 | 49.963
2024-10-21 | 13:28 | 49.961
2024-10-21 | 13:28 | 49.962
2024-10-21 | 13:28 | 49.962
2024-10-21 | 13:28 | 49.964
2024-10-21 | 13:28 | 49.959
2024-10-21 | 13:28 | 49.957
2024-10-21 | 13:28 | 49.957
2024-10-21 | 13:28 | 49.957
2024-10-21 | 13:28 | 49.955
2024-10-21 | 13:28 | 49.954
2024-10-21 | 13:28 | 49.95
2024-10-21 | 13:28 | 49.951
2024-10-21 | 13:28 | 49.946
2024-10-21 | 13:28 | 49.944
2024-10-21 | 13:28 | 49.939
2024-10-21 | 13:28 | 49.94
2024-10-21 | 13:28 | 49.941
2024-10-21 | 13:28 | 49.938
2024-10-21 | 13:28 | 49.937
2024-10-21 | 13:28 | 49.933
2024-10-21 | 13:28 | 49.932
2024-10-21 | 13:28 | 49.93
2024-10-21 | 13:28 | 49.926
2024-10-21 | 13:28 | 49.925
2024-10-21 | 13:28 | 49.921

## 20241028-1
In GMT
Date | Time | Freq
2024-10-28 | 5:59 | 50.086 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-10-28 | 5:59 | 50.084 | 222 | BRITNED | 676.211
2024-10-28 | 5:59 | 50.086 | 268 | WBURB-2 | 428.156
2024-10-28 | 5:59 | 50.084 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-10-28 | 5:59 | 50.085 |  | Viking Link | -648.9
2024-10-28 | 6:00 | 50.086 |  | Viking Link | 1398.96
2024-10-28 | 6:00 | 50.083 | 209 | DRAXX-3 | 626.95
2024-10-28 | 6:00 | 50.085 | 154 | CDCL-1 | 391.57
2024-10-28 | 6:00 | 50.082 | 268 | ROCK-1 | 468.495
2024-10-28 | 6:00 | 50.087 | 148 | IFA Bipole1 | 945.473
2024-10-28 | 6:00 | 50.084 | 132 | IFA Bipole1 | 999.1
2024-10-28 | 6:00 | 50.085 | 141 | IFA Bipole2 | 1000
2024-10-28 | 6:00 | 50.085 | 135 | IFA Bipole1 | 996.75
2024-10-28 | 6:00 | 50.085 |  | Viking Link | -780.3
2024-10-28 | 6:00 | 50.086
2024-10-28 | 6:00 | 50.09
2024-10-28 | 6:00 | 50.089
2024-10-28 | 6:00 | 50.092
2024-10-28 | 6:00 | 50.092
2024-10-28 | 6:00 | 50.094 | 130 | HEYM12 | 271.908
2024-10-28 | 6:00 | 50.094 | 228 | HUMR-1 | 303.75
2024-10-28 | 6:00 | 50.096
2024-10-28 | 6:00 | 50.095
2024-10-28 | 6:00 | 50.096
2024-10-28 | 6:00 | 50.097
2024-10-28 | 6:00 | 50.098
2024-10-28 | 6:00 | 50.1
2024-10-28 | 6:00 | 50.098
2024-10-28 | 6:00 | 50.097
2024-10-28 | 6:00 | 50.096
2024-10-28 | 6:00 | 50.097 | 211 | CDCL-1 | 291.5
2024-10-28 | 6:00 | 50.096 | 199 | STAY-2 | 413.125
2024-10-28 | 6:00 | 50.095 | 173 | CDCL-1 | 397.375
2024-10-28 | 6:00 | 50.094 | 248 | SEAB-2 | 361.25
2024-10-28 | 6:00 | 50.092 | 255 | FRANCE | 995.65
2024-10-28 | 6:00 | 50.087 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-10-28 | 6:00 | 50.084
2024-10-28 | 6:00 | 50.079
2024-10-28 | 6:00 | 50.075
2024-10-28 | 6:00 | 50.077
2024-10-28 | 6:00 | 50.075
2024-10-28 | 6:00 | 50.074
2024-10-28 | 6:00 | 50.073
2024-10-28 | 6:00 | 50.074
2024-10-28 | 6:00 | 50.08
2024-10-28 | 6:00 | 50.08
2024-10-28 | 6:00 | 50.082
2024-10-28 | 6:00 | 50.085
2024-10-28 | 6:00 | 50.085
2024-10-28 | 6:00 | 50.087
2024-10-28 | 6:00 | 50.079
2024-10-28 | 6:00 | 50.047
2024-10-28 | 6:00 | 50.018
2024-10-28 | 6:00 | 50.004
2024-10-28 | 6:00 | 49.998
2024-10-28 | 6:00 | 49.99
2024-10-28 | 6:00 | 49.986
2024-10-28 | 6:00 | 49.984
2024-10-28 | 6:00 | 49.981
2024-10-28 | 6:00 | 49.979
2024-10-28 | 6:00 | 49.978
2024-10-28 | 6:00 | 49.975
2024-10-28 | 6:00 | 49.974
2024-10-28 | 6:00 | 49.975
2024-10-28 | 6:00 | 49.974
2024-10-28 | 6:00 | 49.974
2024-10-28 | 6:01 | 49.972
2024-10-28 | 6:01 | 49.969
2024-10-28 | 6:01 | 49.97
2024-10-28 | 6:01 | 49.969
2024-10-28 | 6:01 | 49.974
2024-10-28 | 6:01 | 49.975
2024-10-28 | 6:01 | 49.976
2024-10-28 | 6:01 | 49.974
2024-10-28 | 6:01 | 49.977
2024-10-28 | 6:01 | 49.974
2024-10-28 | 6:01 | 49.971
2024-10-28 | 6:01 | 49.971
2024-10-28 | 6:01 | 49.972
2024-10-28 | 6:01 | 49.97
2024-10-28 | 6:01 | 49.969
2024-10-28 | 6:01 | 49.974
2024-10-28 | 6:01 | 49.975
2024-10-28 | 6:01 | 49.975
2024-10-28 | 6:01 | 49.979
2024-10-28 | 6:01 | 49.981
2024-10-28 | 6:01 | 49.981
2024-10-28 | 6:01 | 49.983
2024-10-28 | 6:01 | 49.983
2024-10-28 | 6:01 | 49.984
2024-10-28 | 6:01 | 49.981
2024-10-28 | 6:01 | 49.982
2024-10-28 | 6:01 | 49.981
2024-10-28 | 6:01 | 49.98
2024-10-28 | 6:01 | 49.978
2024-10-28 | 6:01 | 49.974
2024-10-28 | 6:01 | 49.972
2024-10-28 | 6:01 | 49.973
2024-10-28 | 6:01 | 49.977
2024-10-28 | 6:01 | 49.976
2024-10-28 | 6:01 | 49.978
2024-10-28 | 6:01 | 49.979
2024-10-28 | 6:01 | 49.978
2024-10-28 | 6:01 | 49.977
2024-10-28 | 6:01 | 49.978
2024-10-28 | 6:01 | 49.976
2024-10-28 | 6:01 | 49.977
2024-10-28 | 6:01 | 49.975
2024-10-28 | 6:01 | 49.978
2024-10-28 | 6:01 | 49.98
2024-10-28 | 6:01 | 49.981
2024-10-28 | 6:01 | 49.982
2024-10-28 | 6:01 | 49.981
2024-10-28 | 6:01 | 49.985
2024-10-28 | 6:01 | 49.985
2024-10-28 | 6:01 | 49.988
2024-10-28 | 6:01 | 49.983
2024-10-28 | 6:01 | 49.983
2024-10-28 | 6:01 | 49.982
2024-10-28 | 6:01 | 49.981
2024-10-28 | 6:01 | 49.982
2024-10-28 | 6:01 | 49.981
2024-10-28 | 6:01 | 49.984
2024-10-28 | 6:01 | 49.984
2024-10-28 | 6:01 | 49.986
2024-10-28 | 6:02 | 49.989
2024-10-28 | 6:02 | 49.992
2024-10-28 | 6:02 | 49.999
2024-10-28 | 6:02 | 50.001
2024-10-28 | 6:02 | 50.005
2024-10-28 | 6:02 | 50.009
2024-10-28 | 6:02 | 50.014
2024-10-28 | 6:02 | 50.014
2024-10-28 | 6:02 | 50.017
2024-10-28 | 6:02 | 50.02
2024-10-28 | 6:02 | 50.022
2024-10-28 | 6:02 | 50.022
2024-10-28 | 6:02 | 50.022
2024-10-28 | 6:02 | 50.024
2024-10-28 | 6:02 | 50.024
2024-10-28 | 6:02 | 50.021
2024-10-28 | 6:02 | 50.021
2024-10-28 | 6:02 | 50.022
2024-10-28 | 6:02 | 50.019
2024-10-28 | 6:02 | 50.022
2024-10-28 | 6:02 | 50.022
2024-10-28 | 6:02 | 50.026
2024-10-28 | 6:02 | 50.028
2024-10-28 | 6:02 | 50.033
2024-10-28 | 6:02 | 50.034
2024-10-28 | 6:02 | 50.037
2024-10-28 | 6:02 | 50.037
2024-10-28 | 6:02 | 50.038
2024-10-28 | 6:02 | 50.041
2024-10-28 | 6:02 | 50.043
2024-10-28 | 6:02 | 50.044
2024-10-28 | 6:02 | 50.043
2024-10-28 | 6:02 | 50.042
2024-10-28 | 6:02 | 50.044
2024-10-28 | 6:02 | 50.047
2024-10-28 | 6:02 | 50.043
2024-10-28 | 6:02 | 50.039
2024-10-28 | 6:02 | 50.043
2024-10-28 | 6:02 | 50.041
2024-10-28 | 6:02 | 50.043
2024-10-28 | 6:02 | 50.043
2024-10-28 | 6:02 | 50.042
2024-10-28 | 6:02 | 50.046
2024-10-28 | 6:02 | 50.045
2024-10-28 | 6:02 | 50.045
2024-10-28 | 6:02 | 50.045
2024-10-28 | 6:02 | 50.04
2024-10-28 | 6:02 | 50.038
2024-10-28 | 6:02 | 50.035
2024-10-28 | 6:02 | 50.035
2024-10-28 | 6:02 | 50.037
2024-10-28 | 6:02 | 50.033
2024-10-28 | 6:02 | 50.032
2024-10-28 | 6:02 | 50.035
2024-10-28 | 6:02 | 50.036
2024-10-28 | 6:02 | 50.04
2024-10-28 | 6:02 | 50.041
2024-10-28 | 6:02 | 50.042
2024-10-28 | 6:02 | 50.04
2024-10-28 | 6:02 | 50.039
2024-10-28 | 6:02 | 50.039
2024-10-28 | 6:03 | 50.041
2024-10-28 | 6:03 | 50.041
2024-10-28 | 6:03 | 50.041
2024-10-28 | 6:03 | 50.039
2024-10-28 | 6:03 | 50.038
2024-10-28 | 6:03 | 50.04
2024-10-28 | 6:03 | 50.038
2024-10-28 | 6:03 | 50.035
2024-10-28 | 6:03 | 50.034
2024-10-28 | 6:03 | 50.033
2024-10-28 | 6:03 | 50.032
2024-10-28 | 6:03 | 50.036
2024-10-28 | 6:03 | 50.036
2024-10-28 | 6:03 | 50.036
2024-10-28 | 6:03 | 50.032
2024-10-28 | 6:03 | 50.035
2024-10-28 | 6:03 | 50.035
2024-10-28 | 6:03 | 50.039
2024-10-28 | 6:03 | 50.038
2024-10-28 | 6:03 | 50.039
2024-10-28 | 6:03 | 50.037
2024-10-28 | 6:03 | 50.039
2024-10-28 | 6:03 | 50.04
2024-10-28 | 6:03 | 50.042
2024-10-28 | 6:03 | 50.043
2024-10-28 | 6:03 | 50.04
2024-10-28 | 6:03 | 50.037
2024-10-28 | 6:03 | 50.036
2024-10-28 | 6:03 | 50.032
2024-10-28 | 6:03 | 50.03

## 20241028-2
In GMT
Date | Time | Freq
2024-10-28 | 8:17 | 50.036 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-10-28 | 8:18 | 50.038 | 222 | BRITNED | 676.211
2024-10-28 | 8:18 | 50.04 | 268 | WBURB-2 | 428.156
2024-10-28 | 8:18 | 50.045 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-10-28 | 8:18 | 50.05 |  | Viking Link | -648.9
2024-10-28 | 8:18 | 50.056 |  | Viking Link | 1398.96
2024-10-28 | 8:18 | 50.056 | 209 | DRAXX-3 | 626.95
2024-10-28 | 8:18 | 50.06 | 154 | CDCL-1 | 391.57
2024-10-28 | 8:18 | 50.059 | 268 | ROCK-1 | 468.495
2024-10-28 | 8:18 | 50.058 | 148 | IFA Bipole1 | 945.473
2024-10-28 | 8:18 | 50.055 | 132 | IFA Bipole1 | 999.1
2024-10-28 | 8:18 | 50.052 | 141 | IFA Bipole2 | 1000
2024-10-28 | 8:18 | 50.045 | 135 | IFA Bipole1 | 996.75
2024-10-28 | 8:18 | 50.041 |  | Viking Link | -780.3
2024-10-28 | 8:18 | 50.04
2024-10-28 | 8:18 | 50.04
2024-10-28 | 8:18 | 50.043
2024-10-28 | 8:18 | 50.044
2024-10-28 | 8:18 | 50.044
2024-10-28 | 8:18 | 50.044 | 130 | HEYM12 | 271.908
2024-10-28 | 8:18 | 50.045 | 228 | HUMR-1 | 303.75
2024-10-28 | 8:18 | 50.047
2024-10-28 | 8:18 | 50.046
2024-10-28 | 8:18 | 50.044
2024-10-28 | 8:18 | 50.045
2024-10-28 | 8:18 | 50.047
2024-10-28 | 8:18 | 50.051
2024-10-28 | 8:18 | 50.052
2024-10-28 | 8:18 | 50.053
2024-10-28 | 8:18 | 50.054
2024-10-28 | 8:18 | 50.053 | 211 | CDCL-1 | 291.5
2024-10-28 | 8:18 | 50.051 | 199 | STAY-2 | 413.125
2024-10-28 | 8:18 | 50.052 | 173 | CDCL-1 | 397.375
2024-10-28 | 8:18 | 50.053 | 248 | SEAB-2 | 361.25
2024-10-28 | 8:18 | 50.053 | 255 | FRANCE | 995.65
2024-10-28 | 8:18 | 50.053 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-10-28 | 8:18 | 50.049
2024-10-28 | 8:18 | 50.046
2024-10-28 | 8:18 | 50.042
2024-10-28 | 8:18 | 50.041
2024-10-28 | 8:18 | 50.043
2024-10-28 | 8:18 | 50.042
2024-10-28 | 8:18 | 50.042
2024-10-28 | 8:18 | 50.046
2024-10-28 | 8:18 | 50.045
2024-10-28 | 8:18 | 50.045
2024-10-28 | 8:18 | 50.048
2024-10-28 | 8:18 | 50.046
2024-10-28 | 8:18 | 50.043
2024-10-28 | 8:18 | 50.042
2024-10-28 | 8:18 | 50.039
2024-10-28 | 8:18 | 50.038
2024-10-28 | 8:18 | 50.039
2024-10-28 | 8:18 | 50.037
2024-10-28 | 8:18 | 50.038
2024-10-28 | 8:18 | 50.041
2024-10-28 | 8:18 | 50.041
2024-10-28 | 8:18 | 50.042
2024-10-28 | 8:18 | 50.046
2024-10-28 | 8:18 | 50.049
2024-10-28 | 8:19 | 50.055
2024-10-28 | 8:19 | 50.062
2024-10-28 | 8:19 | 50.064
2024-10-28 | 8:19 | 50.067
2024-10-28 | 8:19 | 50.068
2024-10-28 | 8:19 | 49.991
2024-10-28 | 8:19 | 49.879
2024-10-28 | 8:19 | 49.812
2024-10-28 | 8:19 | 49.779
2024-10-28 | 8:19 | 49.767
2024-10-28 | 8:19 | 49.768
2024-10-28 | 8:19 | 49.767
2024-10-28 | 8:19 | 49.768
2024-10-28 | 8:19 | 49.769
2024-10-28 | 8:19 | 49.768
2024-10-28 | 8:19 | 49.768
2024-10-28 | 8:19 | 49.77
2024-10-28 | 8:19 | 49.77
2024-10-28 | 8:19 | 49.768
2024-10-28 | 8:19 | 49.765
2024-10-28 | 8:19 | 49.76
2024-10-28 | 8:19 | 49.761
2024-10-28 | 8:19 | 49.764
2024-10-28 | 8:19 | 49.765
2024-10-28 | 8:19 | 49.766
2024-10-28 | 8:19 | 49.768
2024-10-28 | 8:19 | 49.771
2024-10-28 | 8:19 | 49.773
2024-10-28 | 8:19 | 49.773
2024-10-28 | 8:19 | 49.769
2024-10-28 | 8:19 | 49.767
2024-10-28 | 8:19 | 49.763
2024-10-28 | 8:19 | 49.762
2024-10-28 | 8:19 | 49.762
2024-10-28 | 8:19 | 49.76
2024-10-28 | 8:19 | 49.76
2024-10-28 | 8:19 | 49.757
2024-10-28 | 8:19 | 49.755
2024-10-28 | 8:19 | 49.751
2024-10-28 | 8:19 | 49.752
2024-10-28 | 8:19 | 49.751
2024-10-28 | 8:19 | 49.749
2024-10-28 | 8:19 | 49.747
2024-10-28 | 8:19 | 49.747
2024-10-28 | 8:19 | 49.75
2024-10-28 | 8:19 | 49.749
2024-10-28 | 8:19 | 49.75
2024-10-28 | 8:19 | 49.752
2024-10-28 | 8:19 | 49.754
2024-10-28 | 8:19 | 49.757
2024-10-28 | 8:19 | 49.762
2024-10-28 | 8:19 | 49.767
2024-10-28 | 8:19 | 49.771
2024-10-28 | 8:19 | 49.773
2024-10-28 | 8:19 | 49.773
2024-10-28 | 8:19 | 49.773
2024-10-28 | 8:19 | 49.776
2024-10-28 | 8:19 | 49.777
2024-10-28 | 8:19 | 49.778
2024-10-28 | 8:19 | 49.782
2024-10-28 | 8:20 | 49.782
2024-10-28 | 8:20 | 49.781
2024-10-28 | 8:20 | 49.788
2024-10-28 | 8:20 | 49.795
2024-10-28 | 8:20 | 49.796
2024-10-28 | 8:20 | 49.794
2024-10-28 | 8:20 | 49.795
2024-10-28 | 8:20 | 49.801
2024-10-28 | 8:20 | 49.803
2024-10-28 | 8:20 | 49.808
2024-10-28 | 8:20 | 49.808
2024-10-28 | 8:20 | 49.811
2024-10-28 | 8:20 | 49.811
2024-10-28 | 8:20 | 49.814
2024-10-28 | 8:20 | 49.812
2024-10-28 | 8:20 | 49.818
2024-10-28 | 8:20 | 49.82
2024-10-28 | 8:20 | 49.817
2024-10-28 | 8:20 | 49.82
2024-10-28 | 8:20 | 49.823
2024-10-28 | 8:20 | 49.824
2024-10-28 | 8:20 | 49.829
2024-10-28 | 8:20 | 49.833
2024-10-28 | 8:20 | 49.834
2024-10-28 | 8:20 | 49.837
2024-10-28 | 8:20 | 49.833
2024-10-28 | 8:20 | 49.835
2024-10-28 | 8:20 | 49.834
2024-10-28 | 8:20 | 49.834
2024-10-28 | 8:20 | 49.836
2024-10-28 | 8:20 | 49.835
2024-10-28 | 8:20 | 49.837
2024-10-28 | 8:20 | 49.835
2024-10-28 | 8:20 | 49.833
2024-10-28 | 8:20 | 49.834
2024-10-28 | 8:20 | 49.832
2024-10-28 | 8:20 | 49.832
2024-10-28 | 8:20 | 49.834
2024-10-28 | 8:20 | 49.833
2024-10-28 | 8:20 | 49.833
2024-10-28 | 8:20 | 49.832
2024-10-28 | 8:20 | 49.829
2024-10-28 | 8:20 | 49.83
2024-10-28 | 8:20 | 49.827
2024-10-28 | 8:20 | 49.828
2024-10-28 | 8:20 | 49.828
2024-10-28 | 8:20 | 49.826
2024-10-28 | 8:20 | 49.826
2024-10-28 | 8:20 | 49.824
2024-10-28 | 8:20 | 49.825
2024-10-28 | 8:20 | 49.827
2024-10-28 | 8:20 | 49.826
2024-10-28 | 8:20 | 49.827
2024-10-28 | 8:20 | 49.829
2024-10-28 | 8:20 | 49.831
2024-10-28 | 8:20 | 49.833
2024-10-28 | 8:20 | 49.835
2024-10-28 | 8:20 | 49.837
2024-10-28 | 8:20 | 49.834
2024-10-28 | 8:20 | 49.833
2024-10-28 | 8:20 | 49.831
2024-10-28 | 8:21 | 49.829
2024-10-28 | 8:21 | 49.83
2024-10-28 | 8:21 | 49.827
2024-10-28 | 8:21 | 49.826
2024-10-28 | 8:21 | 49.826
2024-10-28 | 8:21 | 49.817
2024-10-28 | 8:21 | 49.823
2024-10-28 | 8:21 | 49.82
2024-10-28 | 8:21 | 49.821
2024-10-28 | 8:21 | 49.819
2024-10-28 | 8:21 | 49.823
2024-10-28 | 8:21 | 49.822
2024-10-28 | 8:21 | 49.821
2024-10-28 | 8:21 | 49.822
2024-10-28 | 8:21 | 49.823
2024-10-28 | 8:21 | 49.826
2024-10-28 | 8:21 | 49.828
2024-10-28 | 8:21 | 49.831
2024-10-28 | 8:21 | 49.832
2024-10-28 | 8:21 | 49.831
2024-10-28 | 8:21 | 49.833
2024-10-28 | 8:21 | 49.831
2024-10-28 | 8:21 | 49.834
2024-10-28 | 8:21 | 49.832
2024-10-28 | 8:21 | 49.835
2024-10-28 | 8:21 | 49.834
2024-10-28 | 8:21 | 49.836
2024-10-28 | 8:21 | 49.832
2024-10-28 | 8:21 | 49.832
2024-10-28 | 8:21 | 49.826
2024-10-28 | 8:21 | 49.826
2024-10-28 | 8:21 | 49.825
2024-10-28 | 8:21 | 49.826
2024-10-28 | 8:21 | 49.827
2024-10-28 | 8:21 | 49.827
2024-10-28 | 8:21 | 49.825
2024-10-28 | 8:21 | 49.827
2024-10-28 | 8:21 | 49.825
2024-10-28 | 8:21 | 49.826
2024-10-28 | 8:21 | 49.828
2024-10-28 | 8:21 | 49.825
2024-10-28 | 8:21 | 49.828
2024-10-28 | 8:21 | 49.831
2024-10-28 | 8:21 | 49.829
2024-10-28 | 8:21 | 49.829
2024-10-28 | 8:21 | 49.83
2024-10-28 | 8:21 | 49.829
2024-10-28 | 8:21 | 49.833
2024-10-28 | 8:21 | 49.832
2024-10-28 | 8:21 | 49.826
2024-10-28 | 8:21 | 49.828
2024-10-28 | 8:21 | 49.825
2024-10-28 | 8:21 | 49.826
2024-10-28 | 8:21 | 49.829
2024-10-28 | 8:21 | 49.827
2024-10-28 | 8:21 | 49.831
2024-10-28 | 8:21 | 49.831
2024-10-28 | 8:21 | 49.832
2024-10-28 | 8:21 | 49.837
2024-10-28 | 8:22 | 49.837
2024-10-28 | 8:22 | 49.841
2024-10-28 | 8:22 | 49.842
2024-10-28 | 8:22 | 49.844
2024-10-28 | 8:22 | 49.847
2024-10-28 | 8:22 | 49.847
2024-10-28 | 8:22 | 49.849
2024-10-28 | 8:22 | 49.846
2024-10-28 | 8:22 | 49.848
2024-10-28 | 8:22 | 49.846
2024-10-28 | 8:22 | 49.844
2024-10-28 | 8:22 | 49.842
2024-10-28 | 8:22 | 49.839
2024-10-28 | 8:22 | 49.841
2024-10-28 | 8:22 | 49.836
2024-10-28 | 8:22 | 49.833
2024-10-28 | 8:22 | 49.832
2024-10-28 | 8:22 | 49.832
2024-10-28 | 8:22 | 49.832
2024-10-28 | 8:22 | 49.829
2024-10-28 | 8:22 | 49.831
2024-10-28 | 8:22 | 49.832
2024-10-28 | 8:22 | 49.833
2024-10-28 | 8:22 | 49.838
2024-10-28 | 8:22 | 49.839
2024-10-28 | 8:22 | 49.839
2024-10-28 | 8:22 | 49.844
2024-10-28 | 8:22 | 49.848
2024-10-28 | 8:22 | 49.851
2024-10-28 | 8:22 | 49.853
2024-10-28 | 8:22 | 49.855
2024-10-28 | 8:22 | 49.858
2024-10-28 | 8:22 | 49.859
2024-10-28 | 8:22 | 49.861
2024-10-28 | 8:22 | 49.862
2024-10-28 | 8:22 | 49.863
2024-10-28 | 8:22 | 49.865
2024-10-28 | 8:22 | 49.87
2024-10-28 | 8:22 | 49.876
2024-10-28 | 8:22 | 49.879
2024-10-28 | 8:22 | 49.881
2024-10-28 | 8:22 | 49.88
2024-10-28 | 8:22 | 49.876
2024-10-28 | 8:22 | 49.871
2024-10-28 | 8:22 | 49.873
2024-10-28 | 8:22 | 49.868
2024-10-28 | 8:22 | 49.869
2024-10-28 | 8:22 | 49.867
2024-10-28 | 8:22 | 49.869
2024-10-28 | 8:22 | 49.867
2024-10-28 | 8:22 | 49.869
2024-10-28 | 8:22 | 49.868
2024-10-28 | 8:22 | 49.872
2024-10-28 | 8:22 | 49.873
2024-10-28 | 8:22 | 49.876
2024-10-28 | 8:22 | 49.873
2024-10-28 | 8:22 | 49.877
2024-10-28 | 8:22 | 49.877
2024-10-28 | 8:22 | 49.881
2024-10-28 | 8:22 | 49.883
2024-10-28 | 8:22 | 49.882
2024-10-28 | 8:23 | 49.885
2024-10-28 | 8:23 | 49.883
2024-10-28 | 8:23 | 49.884
2024-10-28 | 8:23 | 49.887
2024-10-28 | 8:23 | 49.89
2024-10-28 | 8:23 | 49.894
2024-10-28 | 8:23 | 49.898
2024-10-28 | 8:23 | 49.897
2024-10-28 | 8:23 | 49.898
2024-10-28 | 8:23 | 49.897
2024-10-28 | 8:23 | 49.899
2024-10-28 | 8:23 | 49.904
2024-10-28 | 8:23 | 49.905
2024-10-28 | 8:23 | 49.907
2024-10-28 | 8:23 | 49.906
2024-10-28 | 8:23 | 49.902
2024-10-28 | 8:23 | 49.901
2024-10-28 | 8:23 | 49.899
2024-10-28 | 8:23 | 49.896
2024-10-28 | 8:23 | 49.895
2024-10-28 | 8:23 | 49.89
2024-10-28 | 8:23 | 49.887
2024-10-28 | 8:23 | 49.89
2024-10-28 | 8:23 | 49.891
2024-10-28 | 8:23 | 49.891
2024-10-28 | 8:23 | 49.893
2024-10-28 | 8:23 | 49.892
2024-10-28 | 8:23 | 49.893
2024-10-28 | 8:23 | 49.891
2024-10-28 | 8:23 | 49.888
2024-10-28 | 8:23 | 49.887
2024-10-28 | 8:23 | 49.889
2024-10-28 | 8:23 | 49.888
2024-10-28 | 8:23 | 49.888
2024-10-28 | 8:23 | 49.889
2024-10-28 | 8:23 | 49.889
2024-10-28 | 8:23 | 49.89
2024-10-28 | 8:23 | 49.895
2024-10-28 | 8:23 | 49.897
2024-10-28 | 8:23 | 49.895
2024-10-28 | 8:23 | 49.896
2024-10-28 | 8:23 | 49.9
2024-10-28 | 8:23 | 49.899
2024-10-28 | 8:23 | 49.903
2024-10-28 | 8:23 | 49.909
2024-10-28 | 8:23 | 49.909
2024-10-28 | 8:23 | 49.909
2024-10-28 | 8:23 | 49.91
2024-10-28 | 8:23 | 49.907
2024-10-28 | 8:23 | 49.905
2024-10-28 | 8:23 | 49.904
2024-10-28 | 8:23 | 49.905
2024-10-28 | 8:23 | 49.904
2024-10-28 | 8:23 | 49.909
2024-10-28 | 8:23 | 49.909
2024-10-28 | 8:23 | 49.913
2024-10-28 | 8:23 | 49.916
2024-10-28 | 8:23 | 49.917
2024-10-28 | 8:23 | 49.918
2024-10-28 | 8:24 | 49.919
2024-10-28 | 8:24 | 49.922
2024-10-28 | 8:24 | 49.923
2024-10-28 | 8:24 | 49.927
2024-10-28 | 8:24 | 49.929
2024-10-28 | 8:24 | 49.932
2024-10-28 | 8:24 | 49.932
2024-10-28 | 8:24 | 49.928
2024-10-28 | 8:24 | 49.927
2024-10-28 | 8:24 | 49.926
2024-10-28 | 8:24 | 49.925
2024-10-28 | 8:24 | 49.925
2024-10-28 | 8:24 | 49.924
2024-10-28 | 8:24 | 49.927
2024-10-28 | 8:24 | 49.928
2024-10-28 | 8:24 | 49.927
2024-10-28 | 8:24 | 49.929
2024-10-28 | 8:24 | 49.928
2024-10-28 | 8:24 | 49.931
2024-10-28 | 8:24 | 49.932
2024-10-28 | 8:24 | 49.935
2024-10-28 | 8:24 | 49.935
2024-10-28 | 8:24 | 49.935
2024-10-28 | 8:24 | 49.936
2024-10-28 | 8:24 | 49.937
2024-10-28 | 8:24 | 49.938
2024-10-28 | 8:24 | 49.938
2024-10-28 | 8:24 | 49.936
2024-10-28 | 8:24 | 49.937
2024-10-28 | 8:24 | 49.94
2024-10-28 | 8:24 | 49.945
2024-10-28 | 8:24 | 49.946
2024-10-28 | 8:24 | 49.946
2024-10-28 | 8:24 | 49.949
2024-10-28 | 8:24 | 49.946
2024-10-28 | 8:24 | 49.946
2024-10-28 | 8:24 | 49.942
2024-10-28 | 8:24 | 49.939
2024-10-28 | 8:24 | 49.933
2024-10-28 | 8:24 | 49.93
2024-10-28 | 8:24 | 49.927
2024-10-28 | 8:24 | 49.926
2024-10-28 | 8:24 | 49.927
2024-10-28 | 8:24 | 49.929
2024-10-28 | 8:24 | 49.933
2024-10-28 | 8:24 | 49.934
2024-10-28 | 8:24 | 49.936
2024-10-28 | 8:24 | 49.935
2024-10-28 | 8:24 | 49.942
2024-10-28 | 8:24 | 49.946
2024-10-28 | 8:24 | 49.946
2024-10-28 | 8:24 | 49.951
2024-10-28 | 8:24 | 49.951
2024-10-28 | 8:24 | 49.952
2024-10-28 | 8:24 | 49.95
2024-10-28 | 8:24 | 49.951
2024-10-28 | 8:24 | 49.948
2024-10-28 | 8:24 | 49.946
2024-10-28 | 8:24 | 49.945
2024-10-28 | 8:24 | 49.945
2024-10-28 | 8:24 | 49.942
2024-10-28 | 8:25 | 49.942
2024-10-28 | 8:25 | 49.939
2024-10-28 | 8:25 | 49.937
2024-10-28 | 8:25 | 49.935
2024-10-28 | 8:25 | 49.935
2024-10-28 | 8:25 | 49.936
2024-10-28 | 8:25 | 49.936
2024-10-28 | 8:25 | 49.937
2024-10-28 | 8:25 | 49.938
2024-10-28 | 8:25 | 49.939
2024-10-28 | 8:25 | 49.942
2024-10-28 | 8:25 | 49.942
2024-10-28 | 8:25 | 49.944
2024-10-28 | 8:25 | 49.944
2024-10-28 | 8:25 | 49.945
2024-10-28 | 8:25 | 49.947
2024-10-28 | 8:25 | 49.945
2024-10-28 | 8:25 | 49.946
2024-10-28 | 8:25 | 49.945
2024-10-28 | 8:25 | 49.944
2024-10-28 | 8:25 | 49.944
2024-10-28 | 8:25 | 49.943
2024-10-28 | 8:25 | 49.941
2024-10-28 | 8:25 | 49.943
2024-10-28 | 8:25 | 49.945
2024-10-28 | 8:25 | 49.949
2024-10-28 | 8:25 | 49.947
2024-10-28 | 8:25 | 49.947
2024-10-28 | 8:25 | 49.946
2024-10-28 | 8:25 | 49.948
2024-10-28 | 8:25 | 49.949
2024-10-28 | 8:25 | 49.948
2024-10-28 | 8:25 | 49.945
2024-10-28 | 8:25 | 49.944
2024-10-28 | 8:25 | 49.943
2024-10-28 | 8:25 | 49.941
2024-10-28 | 8:25 | 49.942
2024-10-28 | 8:25 | 49.934
2024-10-28 | 8:25 | 49.933
2024-10-28 | 8:25 | 49.934
2024-10-28 | 8:25 | 49.938
2024-10-28 | 8:25 | 49.939
2024-10-28 | 8:25 | 49.944
2024-10-28 | 8:25 | 49.95
2024-10-28 | 8:25 | 49.949
2024-10-28 | 8:25 | 49.952
2024-10-28 | 8:25 | 49.951
2024-10-28 | 8:25 | 49.952
2024-10-28 | 8:25 | 49.956
2024-10-28 | 8:25 | 49.956
2024-10-28 | 8:25 | 49.96
2024-10-28 | 8:25 | 49.961
2024-10-28 | 8:25 | 49.964
2024-10-28 | 8:25 | 49.966
2024-10-28 | 8:25 | 49.969
2024-10-28 | 8:25 | 49.972
2024-10-28 | 8:25 | 49.974
2024-10-28 | 8:25 | 49.976
2024-10-28 | 8:25 | 49.978
2024-10-28 | 8:26 | 49.981
2024-10-28 | 8:26 | 49.983
2024-10-28 | 8:26 | 49.985
2024-10-28 | 8:26 | 49.983
2024-10-28 | 8:26 | 49.984
2024-10-28 | 8:26 | 49.985
2024-10-28 | 8:26 | 49.985
2024-10-28 | 8:26 | 49.987
2024-10-28 | 8:26 | 49.989
2024-10-28 | 8:26 | 49.995
2024-10-28 | 8:26 | 49.999
2024-10-28 | 8:26 | 50.003
2024-10-28 | 8:26 | 50.01
2024-10-28 | 8:26 | 50.017
2024-10-28 | 8:26 | 50.024
2024-10-28 | 8:26 | 50.028
2024-10-28 | 8:26 | 50.032
2024-10-28 | 8:26 | 50.032
2024-10-28 | 8:26 | 50.032
2024-10-28 | 8:26 | 50.031
2024-10-28 | 8:26 | 50.028
2024-10-28 | 8:26 | 50.027
2024-10-28 | 8:26 | 50.026
2024-10-28 | 8:26 | 50.031
2024-10-28 | 8:26 | 50.035
2024-10-28 | 8:26 | 50.038
2024-10-28 | 8:26 | 50.041
2024-10-28 | 8:26 | 50.041
2024-10-28 | 8:26 | 50.044
2024-10-28 | 8:26 | 50.047
2024-10-28 | 8:26 | 50.047
2024-10-28 | 8:26 | 50.044
2024-10-28 | 8:26 | 50.046
2024-10-28 | 8:26 | 50.045
2024-10-28 | 8:26 | 50.042
2024-10-28 | 8:26 | 50.041
2024-10-28 | 8:26 | 50.041
2024-10-28 | 8:26 | 50.041
2024-10-28 | 8:26 | 50.043
2024-10-28 | 8:26 | 50.043
2024-10-28 | 8:26 | 50.043
2024-10-28 | 8:26 | 50.044
2024-10-28 | 8:26 | 50.047
2024-10-28 | 8:26 | 50.05
2024-10-28 | 8:26 | 50.052
2024-10-28 | 8:26 | 50.051
2024-10-28 | 8:26 | 50.053
2024-10-28 | 8:26 | 50.055
2024-10-28 | 8:26 | 50.058
2024-10-28 | 8:26 | 50.06
2024-10-28 | 8:26 | 50.061
2024-10-28 | 8:26 | 50.062
2024-10-28 | 8:26 | 50.063
2024-10-28 | 8:26 | 50.064
2024-10-28 | 8:26 | 50.063
2024-10-28 | 8:26 | 50.06
2024-10-28 | 8:26 | 50.059
2024-10-28 | 8:26 | 50.057
2024-10-28 | 8:26 | 50.056
2024-10-28 | 8:26 | 50.055
2024-10-28 | 8:26 | 50.06
2024-10-28 | 8:27 | 50.061
2024-10-28 | 8:27 | 50.061
2024-10-28 | 8:27 | 50.064
2024-10-28 | 8:27 | 50.065
2024-10-28 | 8:27 | 50.066
2024-10-28 | 8:27 | 50.068
2024-10-28 | 8:27 | 50.068
2024-10-28 | 8:27 | 50.066
2024-10-28 | 8:27 | 50.066
2024-10-28 | 8:27 | 50.064
2024-10-28 | 8:27 | 50.064
2024-10-28 | 8:27 | 50.065
2024-10-28 | 8:27 | 50.062
2024-10-28 | 8:27 | 50.059
2024-10-28 | 8:27 | 50.056
2024-10-28 | 8:27 | 50.055
2024-10-28 | 8:27 | 50.051
2024-10-28 | 8:27 | 50.05
2024-10-28 | 8:27 | 50.05
2024-10-28 | 8:27 | 50.053
2024-10-28 | 8:27 | 50.056
2024-10-28 | 8:27 | 50.059
2024-10-28 | 8:27 | 50.062
2024-10-28 | 8:27 | 50.063
2024-10-28 | 8:27 | 50.062
2024-10-28 | 8:27 | 50.065
2024-10-28 | 8:27 | 50.066
2024-10-28 | 8:27 | 50.063
2024-10-28 | 8:27 | 50.063
2024-10-28 | 8:27 | 50.06

## 20241030-1
In GMT
Date | Time | Freq
2024-10-30 | 17:30 | 49.991 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-10-30 | 17:30 | 49.992 | 222 | BRITNED | 676.211
2024-10-30 | 17:30 | 49.992 | 268 | WBURB-2 | 428.156
2024-10-30 | 17:30 | 49.994 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-10-30 | 17:30 | 49.992 |  | Viking Link | -648.9
2024-10-30 | 17:30 | 49.994 |  | Viking Link | 1398.96
2024-10-30 | 17:30 | 49.995 | 209 | DRAXX-3 | 626.95
2024-10-30 | 17:30 | 49.995 | 154 | CDCL-1 | 391.57
2024-10-30 | 17:30 | 49.999 | 268 | ROCK-1 | 468.495
2024-10-30 | 17:30 | 49.999 | 148 | IFA Bipole1 | 945.473
2024-10-30 | 17:31 | 50.001 | 132 | IFA Bipole1 | 999.1
2024-10-30 | 17:31 | 50.005 | 141 | IFA Bipole2 | 1000
2024-10-30 | 17:31 | 50.006 | 135 | IFA Bipole1 | 996.75
2024-10-30 | 17:31 | 50.013 |  | Viking Link | -780.3
2024-10-30 | 17:31 | 50.015
2024-10-30 | 17:31 | 50.021
2024-10-30 | 17:31 | 50.023
2024-10-30 | 17:31 | 50.027
2024-10-30 | 17:31 | 50.026
2024-10-30 | 17:31 | 50.027 | 130 | HEYM12 | 271.908
2024-10-30 | 17:31 | 50.028 | 228 | HUMR-1 | 303.75
2024-10-30 | 17:31 | 50.027
2024-10-30 | 17:31 | 50.027
2024-10-30 | 17:31 | 50.026
2024-10-30 | 17:31 | 50.028
2024-10-30 | 17:31 | 50.029
2024-10-30 | 17:31 | 50.034
2024-10-30 | 17:31 | 50.037
2024-10-30 | 17:31 | 50.041
2024-10-30 | 17:31 | 50.042
2024-10-30 | 17:31 | 50.046 | 211 | CDCL-1 | 291.5
2024-10-30 | 17:31 | 50.045 | 199 | STAY-2 | 413.125
2024-10-30 | 17:31 | 50.045 | 173 | CDCL-1 | 397.375
2024-10-30 | 17:31 | 50.044 | 248 | SEAB-2 | 361.25
2024-10-30 | 17:31 | 50.041 | 255 | FRANCE | 995.65
2024-10-30 | 17:31 | 50.041 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-10-30 | 17:31 | 50.037
2024-10-30 | 17:31 | 50.037
2024-10-30 | 17:31 | 50.038
2024-10-30 | 17:31 | 50.036
2024-10-30 | 17:31 | 50.036
2024-10-30 | 17:31 | 50.033
2024-10-30 | 17:31 | 50.033
2024-10-30 | 17:31 | 50.033
2024-10-30 | 17:31 | 50.03
2024-10-30 | 17:31 | 50.029
2024-10-30 | 17:31 | 50.027
2024-10-30 | 17:31 | 50.023
2024-10-30 | 17:31 | 50.023
2024-10-30 | 17:31 | 50.018
2024-10-30 | 17:31 | 50.016
2024-10-30 | 17:31 | 50.016
2024-10-30 | 17:31 | 50.014
2024-10-30 | 17:31 | 50.015
2024-10-30 | 17:31 | 50.015
2024-10-30 | 17:31 | 50.015
2024-10-30 | 17:31 | 50.017
2024-10-30 | 17:31 | 50.014
2024-10-30 | 17:31 | 50.019
2024-10-30 | 17:31 | 50.018
2024-10-30 | 17:31 | 50.021
2024-10-30 | 17:31 | 50.02
2024-10-30 | 17:31 | 50.023
2024-10-30 | 17:31 | 50.021
2024-10-30 | 17:31 | 50.022
2024-10-30 | 17:31 | 50.022
2024-10-30 | 17:31 | 50.024
2024-10-30 | 17:31 | 50.022
2024-10-30 | 17:31 | 50.024
2024-10-30 | 17:31 | 50.028
2024-10-30 | 17:31 | 50.031
2024-10-30 | 17:32 | 50.036
2024-10-30 | 17:32 | 50.039
2024-10-30 | 17:32 | 50.044
2024-10-30 | 17:32 | 50.048
2024-10-30 | 17:32 | 50.051
2024-10-30 | 17:32 | 50.051
2024-10-30 | 17:32 | 50.056
2024-10-30 | 17:32 | 50.055
2024-10-30 | 17:32 | 50.057
2024-10-30 | 17:32 | 50.056
2024-10-30 | 17:32 | 50.058
2024-10-30 | 17:32 | 50.029
2024-10-30 | 17:32 | 49.988
2024-10-30 | 17:32 | 49.953
2024-10-30 | 17:32 | 49.922
2024-10-30 | 17:32 | 49.881
2024-10-30 | 17:32 | 49.847
2024-10-30 | 17:32 | 49.825
2024-10-30 | 17:32 | 49.806
2024-10-30 | 17:32 | 49.794
2024-10-30 | 17:32 | 49.781
2024-10-30 | 17:32 | 49.776
2024-10-30 | 17:32 | 49.772
2024-10-30 | 17:32 | 49.773
2024-10-30 | 17:32 | 49.77
2024-10-30 | 17:32 | 49.773
2024-10-30 | 17:32 | 49.773
2024-10-30 | 17:32 | 49.775
2024-10-30 | 17:32 | 49.774
2024-10-30 | 17:32 | 49.772
2024-10-30 | 17:32 | 49.773
2024-10-30 | 17:32 | 49.773
2024-10-30 | 17:32 | 49.773
2024-10-30 | 17:32 | 49.772
2024-10-30 | 17:32 | 49.769
2024-10-30 | 17:32 | 49.77
2024-10-30 | 17:32 | 49.766
2024-10-30 | 17:32 | 49.763
2024-10-30 | 17:32 | 49.761
2024-10-30 | 17:32 | 49.76
2024-10-30 | 17:32 | 49.759
2024-10-30 | 17:32 | 49.753
2024-10-30 | 17:32 | 49.754
2024-10-30 | 17:32 | 49.75
2024-10-30 | 17:32 | 49.746
2024-10-30 | 17:32 | 49.746
2024-10-30 | 17:32 | 49.745
2024-10-30 | 17:32 | 49.745
2024-10-30 | 17:32 | 49.744
2024-10-30 | 17:32 | 49.745
2024-10-30 | 17:32 | 49.744
2024-10-30 | 17:32 | 49.746
2024-10-30 | 17:32 | 49.746
2024-10-30 | 17:32 | 49.746
2024-10-30 | 17:32 | 49.747
2024-10-30 | 17:32 | 49.747
2024-10-30 | 17:32 | 49.748
2024-10-30 | 17:32 | 49.746
2024-10-30 | 17:32 | 49.746
2024-10-30 | 17:33 | 49.743
2024-10-30 | 17:33 | 49.745
2024-10-30 | 17:33 | 49.744
2024-10-30 | 17:33 | 49.748
2024-10-30 | 17:33 | 49.747
2024-10-30 | 17:33 | 49.751
2024-10-30 | 17:33 | 49.751
2024-10-30 | 17:33 | 49.753
2024-10-30 | 17:33 | 49.756
2024-10-30 | 17:33 | 49.753
2024-10-30 | 17:33 | 49.755
2024-10-30 | 17:33 | 49.755
2024-10-30 | 17:33 | 49.756
2024-10-30 | 17:33 | 49.758
2024-10-30 | 17:33 | 49.761
2024-10-30 | 17:33 | 49.765
2024-10-30 | 17:33 | 49.767
2024-10-30 | 17:33 | 49.769
2024-10-30 | 17:33 | 49.769
2024-10-30 | 17:33 | 49.774
2024-10-30 | 17:33 | 49.774
2024-10-30 | 17:33 | 49.775
2024-10-30 | 17:33 | 49.775
2024-10-30 | 17:33 | 49.773
2024-10-30 | 17:33 | 49.773
2024-10-30 | 17:33 | 49.774
2024-10-30 | 17:33 | 49.775
2024-10-30 | 17:33 | 49.779
2024-10-30 | 17:33 | 49.778
2024-10-30 | 17:33 | 49.781
2024-10-30 | 17:33 | 49.781
2024-10-30 | 17:33 | 49.783
2024-10-30 | 17:33 | 49.787
2024-10-30 | 17:33 | 49.787
2024-10-30 | 17:33 | 49.794
2024-10-30 | 17:33 | 49.792
2024-10-30 | 17:33 | 49.794
2024-10-30 | 17:33 | 49.798
2024-10-30 | 17:33 | 49.797
2024-10-30 | 17:33 | 49.801
2024-10-30 | 17:33 | 49.803
2024-10-30 | 17:33 | 49.809
2024-10-30 | 17:33 | 49.812
2024-10-30 | 17:33 | 49.816
2024-10-30 | 17:33 | 49.815
2024-10-30 | 17:33 | 49.816
2024-10-30 | 17:33 | 49.819
2024-10-30 | 17:33 | 49.822
2024-10-30 | 17:33 | 49.825
2024-10-30 | 17:33 | 49.83
2024-10-30 | 17:33 | 49.833
2024-10-30 | 17:33 | 49.84
2024-10-30 | 17:33 | 49.845
2024-10-30 | 17:33 | 49.847
2024-10-30 | 17:33 | 49.851
2024-10-30 | 17:33 | 49.855
2024-10-30 | 17:33 | 49.858
2024-10-30 | 17:33 | 49.863
2024-10-30 | 17:33 | 49.867
2024-10-30 | 17:33 | 49.873
2024-10-30 | 17:33 | 49.878
2024-10-30 | 17:34 | 49.883
2024-10-30 | 17:34 | 49.888
2024-10-30 | 17:34 | 49.891
2024-10-30 | 17:34 | 49.892
2024-10-30 | 17:34 | 49.897
2024-10-30 | 17:34 | 49.897
2024-10-30 | 17:34 | 49.902
2024-10-30 | 17:34 | 49.903
2024-10-30 | 17:34 | 49.907
2024-10-30 | 17:34 | 49.909
2024-10-30 | 17:34 | 49.909
2024-10-30 | 17:34 | 49.912
2024-10-30 | 17:34 | 49.912
2024-10-30 | 17:34 | 49.917
2024-10-30 | 17:34 | 49.917
2024-10-30 | 17:34 | 49.918
2024-10-30 | 17:34 | 49.919
2024-10-30 | 17:34 | 49.92
2024-10-30 | 17:34 | 49.921
2024-10-30 | 17:34 | 49.92
2024-10-30 | 17:34 | 49.921
2024-10-30 | 17:34 | 49.922
2024-10-30 | 17:34 | 49.925
2024-10-30 | 17:34 | 49.926
2024-10-30 | 17:34 | 49.931
2024-10-30 | 17:34 | 49.93
2024-10-30 | 17:34 | 49.933
2024-10-30 | 17:34 | 49.934
2024-10-30 | 17:34 | 49.938
2024-10-30 | 17:34 | 49.94
2024-10-30 | 17:34 | 49.939
2024-10-30 | 17:34 | 49.942
2024-10-30 | 17:34 | 49.941
2024-10-30 | 17:34 | 49.945
2024-10-30 | 17:34 | 49.946
2024-10-30 | 17:34 | 49.951
2024-10-30 | 17:34 | 49.949
2024-10-30 | 17:34 | 49.954
2024-10-30 | 17:34 | 49.955
2024-10-30 | 17:34 | 49.958
2024-10-30 | 17:34 | 49.96
2024-10-30 | 17:34 | 49.964
2024-10-30 | 17:34 | 49.964
2024-10-30 | 17:34 | 49.969
2024-10-30 | 17:34 | 49.97
2024-10-30 | 17:34 | 49.97
2024-10-30 | 17:34 | 49.97
2024-10-30 | 17:34 | 49.969
2024-10-30 | 17:34 | 49.971
2024-10-30 | 17:34 | 49.969
2024-10-30 | 17:34 | 49.97
2024-10-30 | 17:34 | 49.967
2024-10-30 | 17:34 | 49.966
2024-10-30 | 17:34 | 49.964
2024-10-30 | 17:34 | 49.963
2024-10-30 | 17:34 | 49.963
2024-10-30 | 17:34 | 49.961
2024-10-30 | 17:34 | 49.962
2024-10-30 | 17:34 | 49.96
2024-10-30 | 17:35 | 49.958
2024-10-30 | 17:35 | 49.956
2024-10-30 | 17:35 | 49.956
2024-10-30 | 17:35 | 49.954
2024-10-30 | 17:35 | 49.954
2024-10-30 | 17:35 | 49.955
2024-10-30 | 17:35 | 49.957
2024-10-30 | 17:35 | 49.955
2024-10-30 | 17:35 | 49.955
2024-10-30 | 17:35 | 49.953
2024-10-30 | 17:35 | 49.952
2024-10-30 | 17:35 | 49.952
2024-10-30 | 17:35 | 49.951
2024-10-30 | 17:35 | 49.951
2024-10-30 | 17:35 | 49.951
2024-10-30 | 17:35 | 49.95
2024-10-30 | 17:35 | 49.951
2024-10-30 | 17:35 | 49.953
2024-10-30 | 17:35 | 49.954
2024-10-30 | 17:35 | 49.955
2024-10-30 | 17:35 | 49.956
2024-10-30 | 17:35 | 49.952
2024-10-30 | 17:35 | 49.955
2024-10-30 | 17:35 | 49.957
2024-10-30 | 17:35 | 49.956
2024-10-30 | 17:35 | 49.958
2024-10-30 | 17:35 | 49.957
2024-10-30 | 17:35 | 49.96
2024-10-30 | 17:35 | 49.958
2024-10-30 | 17:35 | 49.96
2024-10-30 | 17:35 | 49.962
2024-10-30 | 17:35 | 49.964
2024-10-30 | 17:35 | 49.967
2024-10-30 | 17:35 | 49.968
2024-10-30 | 17:35 | 49.967
2024-10-30 | 17:35 | 49.968
2024-10-30 | 17:35 | 49.968
2024-10-30 | 17:35 | 49.971
2024-10-30 | 17:35 | 49.972
2024-10-30 | 17:35 | 49.976
2024-10-30 | 17:35 | 49.977
2024-10-30 | 17:35 | 49.977
2024-10-30 | 17:35 | 49.977
2024-10-30 | 17:35 | 49.974
2024-10-30 | 17:35 | 49.972
2024-10-30 | 17:35 | 49.968
2024-10-30 | 17:35 | 49.965
2024-10-30 | 17:35 | 49.963
2024-10-30 | 17:35 | 49.962
2024-10-30 | 17:35 | 49.963
2024-10-30 | 17:35 | 49.963
2024-10-30 | 17:35 | 49.962
2024-10-30 | 17:35 | 49.963
2024-10-30 | 17:35 | 49.963
2024-10-30 | 17:35 | 49.965
2024-10-30 | 17:35 | 49.966
2024-10-30 | 17:35 | 49.967
2024-10-30 | 17:35 | 49.97
2024-10-30 | 17:35 | 49.971
2024-10-30 | 17:35 | 49.973
2024-10-30 | 17:35 | 49.975
2024-10-30 | 17:36 | 49.973
2024-10-30 | 17:36 | 49.975
2024-10-30 | 17:36 | 49.978
2024-10-30 | 17:36 | 49.979
2024-10-30 | 17:36 | 49.981
2024-10-30 | 17:36 | 49.985
2024-10-30 | 17:36 | 49.987
2024-10-30 | 17:36 | 49.991
2024-10-30 | 17:36 | 49.995
2024-10-30 | 17:36 | 49.999
2024-10-30 | 17:36 | 50.002
2024-10-30 | 17:36 | 50.005
2024-10-30 | 17:36 | 50.007
2024-10-30 | 17:36 | 50.008
2024-10-30 | 17:36 | 50.011
2024-10-30 | 17:36 | 50.015
2024-10-30 | 17:36 | 50.018
2024-10-30 | 17:36 | 50.022
2024-10-30 | 17:36 | 50.028
2024-10-30 | 17:36 | 50.032
2024-10-30 | 17:36 | 50.036
2024-10-30 | 17:36 | 50.04
2024-10-30 | 17:36 | 50.043
2024-10-30 | 17:36 | 50.045
2024-10-30 | 17:36 | 50.048
2024-10-30 | 17:36 | 50.046
2024-10-30 | 17:36 | 50.046
2024-10-30 | 17:36 | 50.044
2024-10-30 | 17:36 | 50.044
2024-10-30 | 17:36 | 50.04
2024-10-30 | 17:36 | 50.036
2024-10-30 | 17:36 | 50.031
2024-10-30 | 17:36 | 50.03
2024-10-30 | 17:36 | 50.024
2024-10-30 | 17:36 | 50.025
2024-10-30 | 17:36 | 50.022
2024-10-30 | 17:36 | 50.022
2024-10-30 | 17:36 | 50.02
2024-10-30 | 17:36 | 50.021
2024-10-30 | 17:36 | 50.02
2024-10-30 | 17:36 | 50.021
2024-10-30 | 17:36 | 50.022
2024-10-30 | 17:36 | 50.023
2024-10-30 | 17:36 | 50.023
2024-10-30 | 17:36 | 50.024
2024-10-30 | 17:36 | 50.023
2024-10-30 | 17:36 | 50.023
2024-10-30 | 17:36 | 50.023
2024-10-30 | 17:36 | 50.024
2024-10-30 | 17:36 | 50.023
2024-10-30 | 17:36 | 50.024
2024-10-30 | 17:36 | 50.025
2024-10-30 | 17:36 | 50.029
2024-10-30 | 17:36 | 50.029
2024-10-30 | 17:36 | 50.034
2024-10-30 | 17:36 | 50.037
2024-10-30 | 17:36 | 50.042
2024-10-30 | 17:36 | 50.044
2024-10-30 | 17:36 | 50.047
2024-10-30 | 17:37 | 50.049
2024-10-30 | 17:37 | 50.047
2024-10-30 | 17:37 | 50.048
2024-10-30 | 17:37 | 50.047
2024-10-30 | 17:37 | 50.045
2024-10-30 | 17:37 | 50.043
2024-10-30 | 17:37 | 50.039
2024-10-30 | 17:37 | 50.037
2024-10-30 | 17:37 | 50.034
2024-10-30 | 17:37 | 50.032
2024-10-30 | 17:37 | 50.029
2024-10-30 | 17:37 | 50.028
2024-10-30 | 17:37 | 50.024
2024-10-30 | 17:37 | 50.025
2024-10-30 | 17:37 | 50.025
2024-10-30 | 17:37 | 50.023
2024-10-30 | 17:37 | 50.022
2024-10-30 | 17:37 | 50.021
2024-10-30 | 17:37 | 50.02
2024-10-30 | 17:37 | 50.019
2024-10-30 | 17:37 | 50.02
2024-10-30 | 17:37 | 50.02
2024-10-30 | 17:37 | 50.02
2024-10-30 | 17:37 | 50.022
2024-10-30 | 17:37 | 50.025
2024-10-30 | 17:37 | 50.027
2024-10-30 | 17:37 | 50.027
2024-10-30 | 17:37 | 50.027
2024-10-30 | 17:37 | 50.028
2024-10-30 | 17:37 | 50.028
2024-10-30 | 17:37 | 50.027