## Slide 1
Annex 6
GC0166 Work Group – Example Scenarios

## Slide 2: Important Definitions For Example Scenarios
These slides are to support the development of the solution by displaying a number of scenarios when calculating MDO/MDB
MDO = Maximum Deliverable Offer
MDB = Maximum Deliverable Bid
In these examples we imagine a single BMU with the following characteristics
  Maximum Import Limit = Maximum Export Limit = 50MW
  The maximum charge on the BMU is 50MWh
  For stable operation we assume the BMU State of Charge must be between 5% and 95%
  Import efficiency = 93%
  Export efficiency = 95%
On the graphs we use the term “Instantaneous MDO” and “Instantaneous MDB”
These are the values that the BMU has as a function of time (on a minute-by-minute basis)
For example – if the BMU has a State of Charge = 50%, this means the BMU has 25MWh of energy stored. To satisfy an Offer taking all of this charge it would discharge from 50% down to 5% (its lower stable limit) with an efficiency of 95% meaning it could provide 21.3MWh if NESO requested this via a Bid-Offer Acceptance (BOA)
A BMU cannot always declare these instantaneous values to NESO because it may have to hold back some charge for later obligations – these are explored in the examples below
NESO requires a declaration of available energy whilst honouring all other commitments, which may not be reflected in the Instantaneous MDO/MDB

## Slide 3: Case 1 - Physical Notification (PN) = 0, No ancillary contracts
The instantaneous values of MDB and MDO are expected to be modelled by the BMU and would be derived from State of Charge at given instance
In this case the MDB and MDO declared to NESO will be the same as the instantaneous values
(Note we are showing MDB as positive but it would be better to be a negative number)
Assuming high ramp rates NESO could issue a BOA at any time in these three settlement periods with the following
  An offer, 50MW, 25 mins flat top, energy = 20.8MWh
  Or an offer, 25MW, 51 mins flat top, energy = 21.2MWh
  Or a bid, -50MW, 29 mins flat top, energy = 24.1MWh
50MW/50MWh
SoC = 50%
Import efficiency = 93%
Export efficiency = 95%
Min SoC = 5%
Max SoC = 95%

## Slide 4: Case 2 - Positive Physical Notification (PN), No ancillary contracts
In this case the MDO declared to NESO must be the lowest value within the BM Window
So, for MDO, the BMU would declare 16.7MWh for all three settlement periods (assuming PN ramps in SP2 at 2MW/min, stops at 20MW for 5 mins, then ramps down at 2MW/min)
If the BMU was to declare MDO = 21.3MWh in SP1 NESO could take a BOA and reduce its charge to 5%
Then it would not have enough charge left to honour the positive PN in SP2
So, it must protect some charge by declaring MDO = 16.7MWh in SP1
50MW/50MWh
SoC = 50%
Import efficiency = 93%
Export efficiency = 95%
Min SoC = 5%
Max SoC = 95%

## Slide 5: Case 3 - Negative Physical Notification (PN), No ancillary contracts
In this case the MDO declared to NESO can increase in value within the BM Window
So, for MDO, the BMU would declare a value that increases from 20.8MWh to 25MWh (assuming PN ramps down in SP2 at 2MW/min, stops at -20MW for 5 mins, then ramps up at 2MW/min)
Time | Declared MDO | Instantaneous MDO
23:00 | 20.8 | 21.3
23:10 | 21.6 | 21.3
23:15 | 24.1 | 21.3
23:30 | 25.0 | 21.3
23:45 | 25.0 | 24.4
24:00 | 25.5 | 25.5
50MW/50MWh
SoC = 50%
Import efficiency = 93%
Export efficiency = 95%
Min SoC = 5%
Max SoC = 95%
In this case the BMU is charging during SP2 and so it can increase its MDO declared to NESO
It would correspondingly reduce its MDB

## Slide 6: Case 4 - Physical Notification (PN) = 0, Dynamic Reserve service starting in SP3
In this case the BMU is expected to provide a Dynamic Reserve (DR) service
DR is given in EFA blocks so this graph explains the case when we are coming up to the start of the DR period
The BMU declares how much capacity it must hold back for, in this case, to satisfy a 10MW Dynamic Containment (DC) low contract
We expect the MEL for the unit to stay as 50MW but the NESO should be aware that the max BOA that can be issued during SP3 is MEL – Contract Quantity (in this case 50MW – 10MW = 40MW)
There may be instances where the LDA uses all capacity to satisfy its DR contract. In this case the BMU will redeclare its PNs and MDO in later SPs (as governed by gate closure)
50MW/50MWh
SoC = 50%
Import efficiency = 93%
Export efficiency = 95%
Min SoC = 5%
Max SoC = 95%

## Slide 7: Case 5 – Mixture of asset types
The BMU now comprises the BMU as described above and a conventional generator which is not of limited duration
Assume the conventional generator is uni-directional and has a stable lower limit of 0MW, with a maximum of 50MW
Assume the BMU and conventional generator are configured to run at the same time so the BMU MEL is 100MW
The generator has no duration limit and so its energy in the BM Window is 50MW X 1.5hours = 75MWh (being slightly lazy and treating the BM Window as 90 mins)
So, in Case 1 the MDO of this BMU will be 75MWh + 21.3MWh (the MDO of the BMU, based on the previous characteristics)
Similar adjustments would be needed for cases 2, 3 and 4
NOTE – if the BMU was made up of just the conventional generator then the BMU could have the single default value of 9999.9MWh and this would be defaulted every day – the fact that it is part of a BMU with a limited duration asset means it must be declared in an appropriate way