## GC0166_Tool
|  |  | Site: | AG-GC0166 BESS | [8 empty] | DC |  |  |  | Input | --> user can configure Battery physical parameters, dispatch profile, simulate BM acceptance, DFR contract commitment
|  |  | MW | MWh | [8 empty] | DM |  |  |  | Calc | --> calculated fields such as expected SoC, DFR SoE envelope, MW headroom/footroom
|  |  | 50 | 50 | [8 empty] | DR |  |  |  | Output | --> MWh MDO/B profile
|  |  | Min SoC | Max SoC | [8 empty] | None
|  |  | 5% | 95% | [13 empty] | Delivery period / Real time (Firm MDO/MDB)
|  |  | Imp_eff | Exp_eff | [13 empty] | Gate Closure (Indicative future operation)
|  |  | 92.5% | 95%
[13 empty] | Yes |  |  |  | No | Use 30min rule for MEL/MIL
|  |  | Daily Cycle Limit | 2 | [8 empty] | No
|  |  | MWh Cycle Limit | 100
|  | SoC Limit: | Ok
| Date | MEL: | Ok | [13 empty] | Dynamic Response Contracts
| 2024-10-21 | [15 empty] | Low Service |  |  |  |  | Check | High Service
| Time | SP | EFA Block | EFA sub-block | Dispatch (MW) | BM/DFR (MW) | SoC (%) |  | MIL (MW) | MEL (MW) | MDB (MWh) | MDO (MWh) | Import (MWh) | Export (MWh) | MWh until cycle limit |  | DFR -LF MW | DFR MinSOC | DFR MWh | MW Headroom | Service | Flag | DFR-HF MW | DFR MaxSoC | DFR MWh | MW Footroom | Service
0:00 | 45585.9583 | 47 | 1 | 1a | 0 | 0 | 20% | 0 | -50 | 50 | -35.1351 | 2.375 | -40.5405 | 7.125 | 100 |  | 20 | 15% | 5 | 30 | DC | 0 | 20 | 85% | 5 | -30 | DC
0:00 | 45585.9792 | 48 |  |  | 0 | 0 | 20% | 0 | -50 | 50 | -35.1351 | 2.375 | -40.5405 | 7.125 | 100 |  |  | 15% | 5 | 30 |  | 0 |  | 85% | 5 | -30
0:00 | 45586 | 1 |  |  | 0 | 0 | 20% | 0 | -50 | 50 | -35.1351 | 2.375 | -40.5405 | 7.125 | 100 |  |  | 15% | 5 | 30 |  | 0 |  | 85% | 5 | -30
0:00 | 45586.0208 | 2 |  |  | 0 | 0 | 20% | 0 | -50 | 50 | -35.1351 | 2.375 | -40.5405 | 7.125 | 100 |  |  | 15% | 5 | 30 |  | 0 |  | 85% | 5 | -30
0:00 | 45586.0417 | 3 |  | 1b | 0 | 0 | 20% | 0 | -50 | 50 | -35.1351 | 2.375 | -40.5405 | 7.125 | 100 |  |  | 15% | 5 | 30 |  | 0 |  | 85% | 5 | -30
0:00 | 45586.0625 | 4 |  |  | 0 | 0 | 20% | 0 | -50 | 50 | -35.1351 | 2.375 | -40.5405 | 7.125 | 100 |  |  | 15% | 5 | 30 |  | 0 |  | 85% | 5 | -30
0:00 | 45586.0833 | 5 |  |  | -3 | 0 | 20% | 0 | -50 | 50 | -35.1351 | 2.375 | -40.5405 | 7.125 | 100 |  |  | 15% | 5 | 30 |  | 0 |  | 85% | 5 | -30
0:00 | 45586.1042 | 6 |  |  | -3 | 0 | 23% | 0 | -50 | 50 | -33.5135 | 3.8 | -38.9189 | 8.55 | 100 |  |  | 15% | 5 | 30 |  | 0 |  | 85% | 5 | -30
0:00 | 45586.125 | 7 | 2 | 2a | 0 | -0.5 | 26% | 0 | -50 | 50 | -4.8649 | 9.975 | -37.2973 | 9.975 | 100 |  | 0 | 5% | 0 | 50 | None | 0 | 30 | 35% | 30 | -20 | DR
0:00 | 45586.1458 | 8 |  |  | 0 | -0.7 | 26% | 0 | -50 | 50 | -4.8649 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 35% | 30 | -20
0:00 | 45586.1667 | 9 |  |  | 0 | -1 | 27% | 0 | -50 | 50 | -4.3243 | 10.45 | -36.7568 | 10.45 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 35% | 30 | -20
0:00 | 45586.1875 | 10 |  |  | 0 | -0.6 | 28% | 0 | -50 | 50 | -3.7838 | 10.925 | -36.2162 | 10.925 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 35% | 30 | -20
0:00 | 45586.2083 | 11 |  | 2b | 0 | -1.6 | 29% | 0 | -50 | 50 | -3.2432 | 11.4 | -35.6757 | 11.4 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 35% | 30 | -20
0:00 | 45586.2292 | 12 |  |  | 0 | -2.1 | 30% | 0 | -50 | 50 | -2.7027 | 11.875 | -35.1351 | 11.875 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 35% | 30 | -20
0:00 | 45586.25 | 13 |  |  | 0 | -0.8 | 32% | 0 | -50 | 50 | -1.6216 | 12.825 | -34.0541 | 12.825 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 35% | 30 | -20
0:00 | 45586.2708 | 14 |  |  | 0 | -1.2 | 33% | 0 | -50 | 50 | -1.0811 | 13.3 | -33.5135 | 13.3 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 35% | 30 | -20
0:00 | 45586.2917 | 15 | 3 | 3a | -20 | 0 | 34% | 0 | -50 | 50 | -24.8649 | 13.775 | -32.973 | 13.775 | 100 |  | 0 | 5% | 0 | 50 | None | 0 | 30 | 80% | 7.5 | -20 | DC
0:00 | 45586.3125 | 16 |  |  | 10 | 30 | 53% | 0 | -50 | 50 | -14.5946 | 22.8 | -22.7027 | 22.8 | 81 |  |  | 5% | 0 | 50 |  | 0 |  | 80% | 7.5 | -20
0:00 | 45586.3333 | 17 |  |  | 0 | 5 | 11% | 0 | -50 | 50 | -37.2973 | 2.85 | -45.4054 | 2.85 | 78.625 |  |  | 5% | 0 | 50 |  | 0 |  | 80% | 7.5 | -20
0:00 | 45586.3542 | 18 |  |  | 0 | 0 | 6% | 0 | -50 | 50 | -40 | 0.475 | -48.1081 | 0.475 | 78.625 |  |  | 5% | 0 | 50 |  | 0 |  | 80% | 7.5 | -20
0:00 | 45586.375 | 19 |  | 3b | 0 | 0 | 6% | 0 | -50 | 50 | -40 | 0.475 | -48.1081 | 0.475 | 78.625 |  |  | 5% | 0 | 50 |  | 0 |  | 80% | 7.5 | -20
0:00 | 45586.3958 | 20 |  |  | 0 | 0 | 6% | 0 | -50 | 50 | -40 | 0.475 | -48.1081 | 0.475 | 78.625 |  |  | 5% | 0 | 50 |  | 0 |  | 80% | 7.5 | -20
0:00 | 45586.4167 | 21 |  |  | 0 | -50 | 6% | 0 | -50 | 50 | -40 | 0.475 | -48.1081 | 0.475 | 78.625 |  |  | 5% | 0 | 50 |  | 0 |  | 80% | 7.5 | -20
0:00 | 45586.4375 | 22 |  |  | 0 | 0 | 52% | 0 | -50 | 50 | -15.1351 | 22.325 | -23.2432 | 22.325 | 78.625 |  |  | 5% | 0 | 50 |  | 0 |  | 80% | 7.5 | -20
0:00 | 45586.4583 | 23 | 4 | 4a | 0 | 0 | 52% | 0 | -50 | 50 | -23.2432 | 22.325 | -23.2432 | 22.325 | 78.625 |  | 0 | 5% | 0 | 50 | None | 0 | 0 | 95% | 0 | -50 | None
0:00 | 45586.4792 | 24 |  |  | 0 | 0 | 52% | 0 | -50 | 50 | -23.2432 | 22.325 | -23.2432 | 22.325 | 78.625 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45586.5 | 25 |  |  | 0 | 0 | 52% | 0 | -50 | 50 | -23.2432 | 22.325 | -23.2432 | 22.325 | 78.625 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45586.5208 | 26 |  |  | 0 | 0 | 52% | 0 | -50 | 50 | -23.2432 | 22.325 | -23.2432 | 22.325 | 78.625 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45586.5417 | 27 |  | 4b | -8 | 0 | 52% | 0 | -50 | 50 | -23.2432 | 22.325 | -23.2432 | 22.325 | 78.625 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45586.5625 | 28 |  |  | -8 | -15 | 59% | 0 | -50 | 50 | -19.4595 | 25.65 | -19.4595 | 25.65 | 78.625 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45586.5833 | 29 |  |  | -8 | 0 | 80% | 0 | -50 | 50 | -8.1081 | 35.625 | -8.1081 | 35.625 | 78.625 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45586.6042 | 30 |  |  | -8 | 0 | 87% | 0 | -50 | 50 | -4.3243 | 38.95 | -4.3243 | 38.95 | 78.625 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45586.625 | 31 | 5 | 5a | 0 | 0 | 94% | 0 | -50 | 50 | -0.54054 | 42.275 | -0.54054 | 42.275 | 78.625 |  | 0 | 5% | 0 | 50 | None | 0 | 0 | 95% | 0 | -50 | None
0:00 | 45586.6458 | 32 |  |  | 0 | 0 | 94% | 0 | -50 | 50 | -0.54054 | 42.275 | -0.54054 | 42.275 | 78.625 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
X | 45586.6667 | 33 |  |  | 0 | 0 | 94% | 0 | -50 | 50 | -0.54054 | 42.275 | -0.54054 | 42.275 | 78.625 | Dispatch timeframe |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45586.6875 | 34 |  |  | 0 | 0 | 94% | 0 | -50 | 50 | -0.54054 | 42.275 | -0.54054 | 42.275 | 78.625 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45586.7083 | 35 |  | 5b | 0 | 0 | 94% | 0 | -50 | 50 | -0.54054 | 42.275 | -0.54054 | 42.275 | 78.625 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
GC | 45586.7292 | 36 |  |  | 0 | 0 | 94% | 0 | -50 | 50 | -0.54054 | 42.275 | -0.54054 | 42.275 | 78.625 | Scheduling timeframe |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45586.75 | 37 |  |  | 50 | 0 | 94% | 0 | -50 | 50 | -0.54054 | 42.275 | -0.54054 | 42.275 | 54.875 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45586.7708 | 38 |  |  | 0 | 34 | 41% | 0 | -50 | 50 | -29.1892 | 17.1 | -29.1892 | 17.1 | 38.725 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45586.7917 | 39 | 6 | 6a | 0 | -1.8 | 5% | 0 | -50 | 0 | -16.2162 | 0 | -48.6486 | 0 | 38.725 |  | 0 | 5% | 0 | 50 | None | 0 | 30 | 35% | 30 | -20 | DR
0:00 | 45586.8125 | 40 |  |  | 0 | -1.1 | 7% | 0 | -50 | 50 | -15.1351 | 0.95 | -47.5676 | 0.95 | 38.725 |  |  | 5% | 0 | 50 |  | 0 |  | 35% | 30 | -20
0:00 | 45586.8333 | 41 |  |  | 0 | -4.4 | 8% | 0 | -50 | 50 | -14.5946 | 1.425 | -47.027 | 1.425 | 38.725 |  |  | 5% | 0 | 50 |  | 0 |  | 35% | 30 | -20
0:00 | 45586.8542 | 42 |  |  | 0 | -2.7 | 12% | 0 | -50 | 50 | -12.4324 | 3.325 | -44.8649 | 3.325 | 38.725 |  |  | 5% | 0 | 50 |  | 0 |  | 35% | 30 | -20
0:00 | 45586.875 | 43 |  | 6b | 0 | -5.6 | 14% | 0 | -50 | 50 | -11.3514 | 4.275 | -43.7838 | 4.275 | 38.725 |  |  | 5% | 0 | 50 |  | 0 |  | 35% | 30 | -20
0:00 | 45586.8958 | 44 |  |  | 0 | -2.1 | 19% | 0 | -50 | 50 | -8.6486 | 6.65 | -41.0811 | 6.65 | 38.725 |  |  | 5% | 0 | 50 |  | 0 |  | 35% | 30 | -20
0:00 | 45586.9167 | 45 |  |  | 0 | -3.3 | 21% | 0 | -50 | 50 | -7.5676 | 7.6 | -40 | 7.6 | 38.725 |  |  | 5% | 0 | 50 |  | 0 |  | 35% | 30 | -20
0:00 | 45586.9375 | 46 |  |  | 0 | -2.5 | 24% | 0 | -50 | 50 | -5.9459 | 9.025 | -38.3784 | 9.025 | 38.725 |  |  | 5% | 0 | 50 |  | 0 |  | 35% | 30 | -20
0:00 | 45586.9583 | 47 | 1 | 1a | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 38.725 |  | 0 | 5% | 0 | 50 | None | 0 | 0 | 95% | 0 | -50 | None
0:00 | 45586.9792 | 48 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 38.725 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587 | 1 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.0208 | 2 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.0417 | 3 |  | 1b | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.0625 | 4 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.0833 | 5 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.1042 | 6 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.125 | 7 | 2 | 2a | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  | 0 | 5% | 0 | 50 | None | 0 | 0 | 95% | 0 | -50 | None
0:00 | 45587.1458 | 8 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.1667 | 9 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.1875 | 10 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.2083 | 11 |  | 2b | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.2292 | 12 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.25 | 13 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.2708 | 14 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.2917 | 15 | 3 | 3a | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  | 0 | 5% | 0 | 50 | None | 0 | 0 | 95% | 0 | -50 | None
0:00 | 45587.3125 | 16 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.3333 | 17 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.3542 | 18 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.375 | 19 |  | 3b | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.3958 | 20 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.4167 | 21 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.4375 | 22 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.4583 | 23 | 4 | 4a | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  | 0 | 5% | 0 | 50 | None | 0 | 0 | 95% | 0 | -50 | None
0:00 | 45587.4792 | 24 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.5 | 25 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.5208 | 26 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.5417 | 27 |  | 4b | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.5625 | 28 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.5833 | 29 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.6042 | 30 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.625 | 31 | 5 | 5a | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  | 0 | 5% | 0 | 50 | None | 0 | 0 | 95% | 0 | -50 | None
0:00 | 45587.6458 | 32 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.6667 | 33 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.6875 | 34 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.7083 | 35 |  | 5b | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.7292 | 36 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.75 | 37 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.7708 | 38 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.7917 | 39 | 6 | 6a | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  | 0 | 5% | 0 | 50 | None | 0 | 0 | 95% | 0 | -50 | None
0:00 | 45587.8125 | 40 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.8333 | 41 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.8542 | 42 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.875 | 43 |  | 6b | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.8958 | 44 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.9167 | 45 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
0:00 | 45587.9375 | 46 |  |  | 0 | 0 | 26% | 0 | -50 | 50 | -37.2973 | 9.975 | -37.2973 | 9.975 | 100 |  |  | 5% | 0 | 50 |  | 0 |  | 95% | 0 | -50
Note on S9: Chris McLeod: If "No" assumes full MW rated response available throughout the useable SoC range
Note on E11: Chris McLeod: Assumes warranted cycles are calculated on export throughput. Resets on a calendar day
Note on F16: Chris McLeod: Operator self dispatch profile / PN profile
Note on G16: Chris McLeod: Can be used to simulate frequency response draw or BM acceptance
Note on T16: Chris McLeod: equal to the reserved energy volume (REV) required under the relevant service terms
Note on U16: Chris McLeod: Following the removal of the '30min rule' from the MEL/MIL NGESO to account for DFR MW commitment in BM Systems at the point of issuing a BOA
Note on H17: Chris McLeod: User defined start of EFA day SoC
Note on B65: Chris McLeod: D+1