BALANCING CODE NO. 2

(BC2)

POST GATE CLOSURE PROCESS

CONTENTS

(This contents page does not form part of the Grid Code)

Paragraph No/Title	Page Number

BC2.1   INTRODUCTION	3

BC2.2   OBJECTIVE	3

BC2.3   SCOPE	3

BC2.4  INFORMATION USED	3

BC2.5   PHYSICAL OPERATION OF BM UNITS	4

BC2.5.1   Accuracy Of Physical Notifications	4

BC2.5.2   Synchronising And De-Synchronising Times	5

BC2.5.3   Revisions To BM Unit Data	6

BC2.5.4   Operation In The Absence Of Instructions From The Company	7

BC2.5.5   Commencement Or Termination Of Participation In The Balancing Mechanism	9

BC2.6   COMMUNICATIONS	10

BC2.6.1   Normal Communications With Control Points	10

BC2.6.2   Communication With Control Points In Emergency Circumstances	10

BC2.6.3   Communication With Network Operators In Emergency Circumstances	11

BC2.6.4   Communication With Externally Interconnected System Operators In Emergency Circumstances	11

BC2.6.5   Communications during Planned Outages Of Electronic Data Communication Facilities	11

BC2.7   BID-OFFER ACCEPTANCES	12

BC2.7.1   Acceptance of Bids and Offers by The Company	12

BC2.7.2   Consistency With Export And Import Limits And Dynamic Parameters	12

BC2.7.3   Confirmation and Rejection of Acceptances	12

BC2.7.4   Action Required From BM Participants	13

BC2.7.5   Additional Action required when responding to Bid-Offer Acceptances	13

BC2.8   ANCILLARY SERVICES	13

BC2.8.1   Call-Off of Ancillary Services by The Company	13

BC2.8.2   Consistency with Export and Import Limits and Dynamic Parameters	14

BC2.8.3   Rejection Of Ancillary Service Instructions	14

BC2.8.4   Action Required From BM Units	14

BC2.8.5   Reactive Despatch Network Restrictions	15

BC2.9   EMERGENCY CIRCUMSTANCES	15

BC2.9.1   Emergency Actions	15

BC2.9.2   Implementation of Emergency Instructions	16

BC2.9.3   Examples of Emergency Instructions	17

BC2.9.4  Maintaining Adequate System And Localised NRAPM (Negative Reserve Active Power Margin)	18

BC2.9.5   Maintaining an adequate level of Frequency Sensitive Generation	19

BC2.9.6   Emergency Assistance to And from External Systems	19

BC2.9.7   Unplanned Outages of Electronic Communication and Computing Facilities	20

BC2.10   OTHER OPERATIONAL INSTRUCTIONS AND NOTIFICATIONS	21

BC2.11   LIAISON WITH GENERATORS FOR RISK OF TRIP AND AVR TESTING	22

BC2.12   LIAISON WITH EXTERNALLY INTERCONNECTED SYSTEM OPERATORS	23

BC2.13   LIAISON WITH INTERCONNECTOR OWNERS	23

APPENDIX 1 - FORM OF BID-OFFER ACCEPTANCES	24

APPENDIX 2 - TYPE AND FORM OF ANCILLARY SERVICE INSTRUCTIONS	26

APPENDIX 3 - SUBMISSION OF REVISED MVAr CAPABILITY	32

APPENDIX 3 ANNEXURE 1	33

APPENDIX 3 ANNEXURE 2	34

APPENDIX 3 ANNEXURE 3	35

APPENDIX 4 - SUBMISSION OF AVAILABILITY OF FREQUENCY SENSITIVE MODE	37

APPENDIX 4 ANNEXURE 1	38

BC2.1	INTRODUCTION

Balancing Code No 2 (BC2) sets out the procedure for:

(a)	the physical operation of BM Units and Generating Units (which could be part of a Power Generating Module) in the absence of any instructions from The Company;

(b)   the submission of Interconnector data by each Interconnector Owner;

(c)	the acceptance by The Company of Balancing Mechanism Bids and Offers,

(d)	the calling off by The Company of Ancillary Services;

(e)	the issuing and implementation of Emergency Instructions; and

(f)	the issuing by The Company of other operational instructions and notifications.

In addition, BC2 deals with any information exchange between The Company and BM Participants or specific Users that takes place after Gate Closure.

In this BC2, “consistent” shall be construed as meaning to the nearest integer MW level.

In this BC2, references to “a BM Unit returning to its Physical Notification” shall take account of any Bid-Offer Acceptances already issued to the BM Unit in accordance with BC2.7 and any Emergency Instructions already issued to the BM Unit or Generating Unit (which could be part of a Power Generating Module) in accordance with BC2.9.

BC2.2	OBJECTIVE

The procedure covering the operation of the Balancing Mechanism and the issuing of instructions to Users is intended to enable The Company as far as possible to maintain the integrity of the National Electricity Transmission System together with the security and quality of supply.

Where reference is made in this BC2 to Power Generating Modules or Generating Units (unless otherwise stated) it only applies:

(a)	to each Generating Unit which forms part of the BM Unit of a Cascade Hydro Scheme; and

(b)	at an Embedded Exemptable Large Power Station where the relevant Bilateral Agreement specifies that compliance with BC2 is required:

(i)	to each Generating Unit which could be part of a Synchronous Power Generating Module, or

(ii)	to each Power Park Module where the Power Station comprises Power Park Modules.

BC2.3	SCOPE

BC2 applies to The Company and to Users, which in this BC2 means:-

(a)	BM Participants;

(b)	Externally Interconnected System Operators, and

(c)	Network Operators.

BC2.4	INFORMATION USED

BC2.4.1	The information which The Company shall use, together with the other information available to it, in assessing:

(a)	which bids and offers to accept;

(b)	which BM Units and/or Generating Units to instruct to provide Ancillary Services;

(c)	the need for and formulation of Emergency Instructions; and

(d)	other operational instructions and notifications which The Company may need to issue

will be:

(a)	the Physical Notification and Bid-Offer Data submitted under BC1;

(b)	Export and Import Limits in respect of that BM Unit and/or Generating Unit supplied under BC1 (and any revisions under BC1 and BC2 to the data); and

(c)	Interconnector data submitted by each Interconnector Owner under BC1; and

(d)	Dynamic Parameters submitted or revised under this BC2.

BC2.4.2	As provided for in BC1.5.4, The Company will monitor the total of the Maximum Export Limit component of the Export and Import Limits against forecast Demand and the Operating Margin and will take account of Dynamic Parameters to see whether the anticipated level of System Margin is insufficient. This will reflect any changes in Export and Import Limits which have been notified to The Company, and will reflect any Demand Control which has also been so notified. The Company may issue new or revised National Electricity Transmission System Warnings – Electricity Margin Notice or High Risk of Demand Reduction in accordance with BC1.5.4.

BC2.5	PHYSICAL OPERATION OF BM UNITS

BC2.5.1	Accuracy Of Physical Notifications

As described in BC1.4.2(a), Physical Notifications must represent the BM Participant’s best estimate of expected input or output of Active Power, except where a BM Unit is affected by a Stage 2 or higher Network Gas Supply Emergency load shedding event. Physical Notifications shall be prepared in accordance with Good Industry Practice.

In the case where a BM Unit is affected by a Network Gas Supply Emergency load shedding event, once Stage 2 or higher has been declared, then their Physical Notifications shall represent the User's best estimate of the contracted power position of the affected BM Unit at the time of the event, taking into account any mitigating actions to reduce the difference between the contracted power position and the volume to be shed.

Each BM Participant must, applying Good Industry Practice, ensure that each of its BM Units follows the Physical Notification in respect of that BM Unit, except where the generation output of a BM Unit for an affected site only is reduced as a result of a Stage 2 or higher Network Gas Supply Emergency load shedding event , (and each of its Generating Units follows the Physical Notification in the case of Physical Notifications supplied under BC1.4.2(a)(2)) that is prevailing at Gate Closure (the data in which will be utilised in producing the Final Physical Notification Data in accordance with the BSC) subject to variations arising from:

(a)	the issue of Bid-Offer Acceptances which have been confirmed by the BM Participant; or

(b)	instructions by The Company in relation to that BM Unit (or a Generating Unit) which require, or compliance with which would result in, a variation in output or input of that BM Unit (or a Generating Unit); or

(c)	compliance with provisions of BC1, BC2 or BC3 which provide to the contrary.

Except where variations from the Physical Notification arise from matters referred to at (a), (b) or (c) above, in respect only of BM Units (or Generating Units) powered by an Intermittent Power Source, where there is a change in the level of the Intermittent Power Source from that forecast and used to derive the Physical Notification, variations from the Physical Notification prevailing at Gate Closure may, subject to remaining within the Registered Capacity, occur providing that the Physical Notification prevailing at Gate Closure was prepared in accordance with Good Industry Practice.

If variations and/or instructions as described in (a),(b) or (c) apply in any instance to BM Units (or Generating Units) powered by an Intermittent Power Source (e.g. a Bid Offer Acceptance is issued in respect of such a BM Unit and confirmed by the BM Participant) then such provisions will take priority over the third paragraph of BC2.5.1 above such that the BM Participant must ensure that the Physical Notification as varied in accordance with (a), (b) or (c) above applies and must be followed, subject to this not being prevented as a result of an unavoidance event as described below.

For the avoidance of doubt, this gives rise to an obligation on each BM Participant (applying Good Industry Practice) to ensure that each of its BM Units (and Generating Units), follows the Physical Notifications prevailing at Gate Closure as amended by such variations and/or instructions unless in relation to any such obligation it is prevented from so doing as a result of an unavoidable event (existing or anticipated) in relation to that BM Unit (or a Generating Unit) which requires a variation in output or input of that BM Unit (or a Generating Unit).

Examples (on a non-exhaustive basis) of such an unavoidable event are:

- plant breakdowns;

- events requiring a variation of input or output on safety grounds (relating to personnel or plant);

- events requiring a variation of input or output to maintain compliance with the relevant Statutory Water Management obligations; and

- uncontrollable variations in output of Active Power.

Any anticipated variations in input or output post Gate Closure from the Physical Notification for a BM Unit (or a Generating Unit) prevailing at Gate Closure (except for those arising from instructions as outlined in (a), (b) or (c) above) must be notified to The Company without delay by the relevant BM Participant (or the relevant person on its behalf).  For the avoidance of doubt, where a change in the level of the Intermittent Power Source from that forecast and used to derive the Physical Notification results in the Shutdown or Shutdown of part of the BM Unit (or Generating Unit), the change must be notified to The Company without delay by the relevant BM Participant (or the relevant person on its behalf).

Implementation of this notification should normally be achieved by the submission of revisions to the Export and Import Limits in accordance with BC2.5.3 below.

BC2.5.2	Synchronising And De-Synchronising Times

BC2.5.2.1	The Final Physical Notification Data provides indicative Synchronising and De-Synchronising times to The Company in respect of any BM Unit which is De-Synchronising or is anticipated to be Synchronising post Gate Closure.

Any delay of greater than five minutes to the Synchronising or any advancement of greater than five minutes to the De-Synchronising of a BM Unit must be notified to The Company without delay by the submission of a revision of the Export and Import Limits.

BC2.5.2.2	Except in the circumstances provided for in BC2.5.2.3, BC2.5.2.4, BC2.5.5.1 or BC2.9, no BM Unit (nor a Generating Unit) is to be Synchronised or De-Synchronised unless:-

(a)	a Physical Notification had been submitted to The Company prior to Gate Closure indicating that a Synchronisation or De-Synchronisation is to occur; or

(b)	The Company has issued a Bid-Offer Acceptance requiring Synchronisation or De-Synchronisation of that BM Unit (or a Generating Unit).

BC2.5.2.3	BM Participants must only Synchronise or De-Synchronise BM Units (or a Generating Unit);

(a)	at the times indicated to The Company, or

(b)	at times consistent with variations in output or input arising from provisions described in BC2.5.1,

(within a tolerance of +/- 5 minutes) or unless that occurs automatically as a result of Operational Intertripping or Low Frequency Relay operations or an Ancillary Service pursuant to an Ancillary Services Agreement

BC2.5.2.4	De-Synchronisation may also take place without prior notification to The Company as a result of plant breakdowns or if it is done purely on safety grounds (relating to personnel or plant). If that happens, The Company must be informed immediately that it has taken place and a revision to Export and Import Limits must be submitted in accordance with BC2.5.3.3. Following any De-Synchronisation occurring as a result of plant failure, no Synchronisation of that BM Unit (or a Generating Unit) is to take place without The Company’s agreement, such agreement not to be unreasonably withheld.

In the case of Synchronisation, following an unplanned De-Synchronisation within the preceding 15 minutes, a minimum of 5 minutes notice of its intention to Synchronise should normally be given to The Company (via a revision to Export and Import Limits). In the case of any other unplanned De-Synchronisation where the User plans to Synchronise before the expiry of the current Balancing Mechanism period, a minimum of 15 minutes notice of Synchronisation should normally be given to The Company (via a revision to Export and Import Limits). In addition, the rate at which the BM Unit is returned to its Physical Notification is not to exceed the limits specified in BC1, Appendix 1 without The Company’s agreement.

The Company will either agree to the Synchronisation or issue a Bid-Offer Acceptance in accordance with BC2.7 to delay the Synchronisation. The Company may agree to an earlier Synchronisation if System conditions allow.

BC2.5.2.5	Notification Of Times To Network Operators

The Company will make changes to the Synchronising and De-Synchronising times available to each Network Operator, but only relating to BM Units Embedded within its User System and those BM Units directly connected to the National Electricity Transmission System which The Company has identified under OC2 and/or BC1 as being those which may, in the reasonable opinion of The Company, affect the integrity of that User System and shall inform the relevant BM Participant that it has done so, identifying the BM Unit concerned.

Each Network Operator must notify The Company of any changes to its User System data as soon as practicable in accordance with BC1.6.1(c).

BC2.5.3	Revisions To BM Unit Data

Following Gate Closure for any Settlement Period, no changes to the Physical Notification or to Bid-Offer Data for that Settlement Period may be submitted to The Company.

BC2.5.3.1	At any time, any BM Participant (or the relevant person on its behalf) may, in respect of any of its BM Units, submit to The Company the data listed in BC1, Appendix 1 under the heading of Dynamic Parameters from the Control Point of its BM Unit to amend the data already held by The Company (including that previously submitted under this BC2.5.3.1) for use in preparing for and operating the Balancing Mechanism. The change will take effect from the time that it is received by The Company. For the avoidance of doubt, the Dynamic Parameters submitted to The Company under BC1.4.2(e) are not used	within the current Operational Day. The Dynamic Parameters submitted under this BC2.5.3.1 shall reasonably reflect the true current operating characteristics of the BM Unit and shall be prepared in accordance with Good Industry Practice.

Following the Operational Intertripping of a System to Generating Unit or a System to CCGT Module and/or a System to Power Generating Module, the BM Participant shall as soon as reasonably practicable re-declare its MEL to reflect more accurately its output capability.

BC2.5.3.2	Revisions to Export and Import Limits or Other Relevant Data supplied (or revised) under BC1 must be notified to The Company without delay as soon as any change becomes apparent to the BM Participant (or the relevant person on its behalf) via the Control Point for the BM Unit (or a Generating Unit) to ensure that an accurate assessment of BM Unit (or a Generating Unit) capability is available to The Company at all times. These revisions should be prepared in accordance with Good Industry Practice and may be submitted by use of electronic data communication facilities or by telephone.

BC2.5.3.3	Revisions to Export and Import Limits must be made by a BM Participant (or the relevant person on its behalf) via the Control Point in the event of any De-Synchronisation of a BM Unit (or a Generating Unit) in the circumstances described in BC2.5.2.4 if the BM Unit (or a Generating Unit) is no longer available for any period of time. Revisions must also be submitted in the event of plant failures causing a reduction in input or output of a BM Unit (or a Generating Unit) even if that does not lead to De-Synchronisation. Following the correction of a plant failure, the BM Participant (or the relevant person on its behalf) must notify The Company via the Control Point of a revision to the Export and Import Limits, if appropriate, of the BM Unit (or a Generating Unit), using reasonable endeavours to give a minimum of 5 minutes notice of its intention to return to its Physical Notification. The rate at which the BM Unit (or a Generating Unit) is returned to its Physical Notification is not to exceed the limits specified in BC1, Appendix 1 without The Company’s agreement.

BC2.5.3.4	Revisions to Maximum Delivery Offer and Maximum Delivery Bid for a BM Unit may only be made following Gate Closure for a Settlement Period in the event of:

(a) The BM Unit no longer being able to achieve the previously stated value as a result of an unavoidable event. Examples of such an event include (but are not limited to) plant breakdowns, or events requiring a variation on safety grounds (relating to personnel or plant); or

(b) The Company issuing a Bid-Offer Acceptance in respect of the BM Unit; or

(c) The BM Unit fully utilising the energy reserved (or storage capacity for energy which was reserved) for delivery of System Ancillary Services or Commercial Ancillary Services; or

(d) Submission of a change to a Physical Notification for the BM Unit under BC1.4.2(a) which covers the Settlement Period after the Balancing Mechanism Window Period.

BC2.5.4	Operation in the Absence of Instructions from The Company

In the absence of any Bid-Offer Acceptances, Ancillary Service instructions issued pursuant to BC2.8 or Emergency Instructions issued pursuant to BC2.9:

(a)	as provided for in BC3, each Synchronised Genset producing Active Power must operate at all times in Limited Frequency Sensitive Mode (unless instructed in accordance with BC3.5.4 to operate in Frequency Sensitive Mode);

(b)	(i)	in the absence of any MVAr Ancillary Service instructions, the MVAr output of each Synchronised Genset located Onshore should be 0 MVAr upon Synchronisation at the circuit-breaker where the Genset is Synchronised. For the avoidance of doubt, in the case of a Genset located Onshore comprising of Non-Synchronous Generating Units, Power Park Modules, HVDC Systems or DC Converters, the steady state tolerance allowed in CC.6.3.2(b) or ECC.6.3.2.4.4 may be applied;

(ii)	In the absence of any MVAr Ancillary Service instructions, the MVAr output of each Synchronised Genset comprising Synchronous Generating Units located Offshore (which could be part of a Synchronous Power Generating Module) should be 0MVAr at the Grid Entry Point upon Synchronisation. For the avoidance of doubt, in the case of a Genset located Offshore comprising of Non-Synchronous Generating Units, Power Park Modules, HVDC Systems or DC Converters, the steady state tolerance allowed in CC.6.3.2(e) or ECC.6.3.2.5.1 or ECC.6.3.2.5.2 or ECC.6.3.2.5.3 or ECC.6.3.2.6.1 or ECC.6.3.2.6.3 or ECC.6.3.2.6.4 (as applicable) may be applied;

(c)	(i)	subject to the provisions of 2.5.4(c) (ii) and 2.5.4 (c) (iii) below, the excitation system or the voltage control system of a Genset located Offshore which has agreed an alternative Reactive Power capability range under CC.6.3.2 (e) (iii) or  ECC.6.3.2.5.2 or ECC.6.3.2.5.3 or ECC.6.3.2.6.1 or ECC.6.3.2.6.3 or ECC.6.3.2.6.4 (as applicable) or a Genset located Onshore, unless otherwise agreed with The Company, must be operated only in its constant terminal voltage mode of operation with VAR limiters in service, with any constant Reactive Power output control mode or constant Power Factor output control mode always disabled, unless agreed otherwise with The Company. In the event of any change in System voltage, a Generator must not take any action to override automatic MVAr response which is produced as a result of constant terminal voltage mode of operation of the automatic excitation control system unless instructed otherwise by The Company or unless immediate action is necessary to comply with Stability Limits or unless constrained by plant operational limits or safety grounds (relating to personnel or plant);

(ii)	In the case of all Gensets comprising Non-Synchronous Generating Units, DC Converters, HVDC Systems and Power Park Modules that are located Offshore and which have agreed an alternative Reactive Power capability range under CC.6.3.2 (e) (iii), or ECC.6.3.2.5.2 or ECC.6.3.2.5.3 or ECC.6.3.2.6.1 or ECC.6.3.2.6.3 or ECC.6.3.2.6.4 (as applicable) or that are located Onshore only when operating below 20 % of the Rated MW output, the voltage control system shall maintain the Reactive Power transfer at the Grid Entry Point (or User System Entry Point if Embedded)  to 0 MVAr.  For the avoidance of doubt, the relevant steady state tolerance allowed for GB Generators in CC.6.3.2(b) or CC.6.3.2 (e) and for EU Generators in ECC.6.3.2.4.4, ECC.6.3.2.5.1, ECC.6.3.2.5.2, or ECC.6.3.2.5.3 or ECC.6.3.2.6.1, ECC.6.3.2.6.2 or ECC.6.3.2.6.3 or ECC.6.3.2.6.4 may be applied.  In the case of any such Gensets owned or operated by GB Code Users  comprising current source DC Converter technology or comprising Power Park Modules connected to the Total System by a current source DC Converter when operating at any power output, the voltage control system shall maintain the Reactive Power transfer at the Grid Entry Point (or User System Entry Point if Embedded)  to 0 MVAr.  For the avoidance of doubt, the relevant steady state tolerance allowed in CC.6.3.2(b) or CC.6.3.2 (c) (i) or CC.6.3.2(e) may be applied.

(iii)	In the case of all Gensets located Offshore which are not subject to the requirements of BC2.5.4 (c) (i) or BC2.5.4 (c) (ii) the control system shall maintain the Reactive Power transfer at the Offshore Grid Entry Point at 0MVAr.  For the avoidance of doubt the steady state tolerance allowed by CC.6.3.2 (e) or ECC.6.3.2.4.4, ECC.6.3.2.5.1, or ECC.6.3.2.5.2 or ECC.6.3.2.5.3, or ECC.6.3.2.6.1 or ECC.6.3.2.6.3 or ECC.6.3.2.6.4 may be applied.

(d)	In the absence of any MVAr Ancillary Service instructions,

(i)	the MVAr output of each Genset located Onshore should be 0 MVAr immediately prior to De-Synchronisation at the circuit-breaker where the Genset is Synchronised, other than in the case of a rapid unplanned De-Synchronisation or in the case of a Genset comprising of Power Generating Modules and/or Non-Synchronous Generating Units and/or Power Park Modules and/or HVDC Converters or DC Converters which is operating at less than 20% of its Rated MW output where the requirements of BC2.5.4 (c) part (ii) apply, or;

(ii)	the MVAr output of each Genset located Offshore should be 0MVAr immediately prior to De-Synchronisation at the Offshore Grid Entry Point, other than in the case of a rapid unplanned De-Synchronisation or in the case of a Genset comprising of Non-Synchronous Generating Units, Power Park Modules, HVDC Converters or DC Converters which is operating at less than 20% of its Rated MW output and which has agreed an alternative Reactive Power capability range (for GB Code  Users) under CC.6.3.2 (e) (iii) or ECC.6.3.2.4.4, ECC.6.3.2.5.1, ECC.6.3.2.5.2, or ECC.6.3.2.5.3, or ECC.6.3.2.6.1 or ECC.6.3.2.6.3 or ECC.6.3.2.6.4 (for EU Code Users ) where the requirements of BC2.5.4 (c) (ii) apply.

(e)	a Generator should at all times operate its CCGT Units in accordance with the applicable CCGT Module Matrix;

(f)	in the case of a Range CCGT Module, a Generator must operate that CCGT Module so that power is provided at the single Grid Entry Point (or User System Entry Point if Embedded) identified in the data given pursuant to PC.A.3.2.1 or at the single Grid Entry Point to which The Company has agreed pursuant to BC1.4.2(f);

(g)	in the event of the System Frequency being above 50.3Hz or below 49.7Hz, BM Participants must not commence any reasonably avoidable action to regulate the input or output of any BM Unit in a manner that could cause the System Frequency to deviate further from 50Hz without first using reasonable endeavours to discuss the proposed actions with The Company.  The Company shall either agree to these changes in input or output or issue a Bid-Offer Acceptance in accordance with BC2.7 to delay the change.

(h)	a Generator should at all times operate its Power Park Units in accordance with the applicable Power Park Module Availability Matrix.

BC2.5.5	Commencement or Termination of Participation in the Balancing Mechanism

BC2.5.5.1	In the event that a BM Participant in respect of a BM Unit with a Demand Capacity with a magnitude of less than 50MW in NGET’s Transmission Area or less than 10MW in SHETL’s Transmission Area or less than 30MW in SPT’s Transmission Area or comprising Generating Units (as defined in the Glossary and Definitions and not limited by BC2.2) and/or Power Generating Modules and/or CCGT Modules and/or Power Park Modules at a Small Power Station, notifies The Company at least 30 days in advance that from a specified Operational Day it will:

(a)	no longer submit Bid-Offer Data under BC1.4.2(d), then with effect from that Operational Day, that BM Participant no longer has to meet the requirements of BC2.5.1 nor the requirements of CC.6.5.8(b) or ECC.6.5.8(b) (as applicable)  in relation to that BM Unit. Also, with effect from that Operational Day, any defaulted Physical Notification and defaulted Bid-Offer Data in relation to that BM Unit arising from the Data Validation, Consistency and Defaulting Rules will be disregarded and the provisions of BC2.5.2 will not apply;

(b)	submit Bid-Offer Data under BC1.4.2(d), then with effect from that Operational Day that BM Participant will need to meet the requirements of BC2.5.1 and the requirements of CC.6.5.8(b) or ECC.6.5.8(b) (as applicable) in relation to that BM Unit.

BC2.5.5.2	In the event that a BM Participant in respect of a BM Unit with a Demand Capacity with a magnitude of 50MW or more in NGET’s Transmission Area or 10MW or more in SHETL’s Transmission Area or 30MW or more in SPT’s Transmission Area or comprising Generating Units (as defined in the Glossary and Definitions and not limited by BC2.2) and/or Power Generating Modules and/or CCGT Modules and/or Power Park Modules at a Medium Power Station or Large Power Station notifies The Company at least 30 days in advance that from a specified Operational Day it will:

(a)	no longer submit Bid-Offer Data under BC1.4.2(d), then with effect from that Operational Day that BM Participant no longer has to meet the requirements of CC.6.5.8(b) or ECC.6.5.8(b) (as applicable) in relation to that BM Unit; also, with effect from that Operational Day, any defaulted Bid-Offer Data in relation to that BM Unit arising from the Data Validation, Consistency and Defaulting Rules will be disregarded;

(b)	submit Bid-Offer Data under BC1.4.2(d), then with effect from that Operational Day that BM Participant will need to meet the requirements of CC.6.5.8(b) or ECC.6.5.8(b) (as applicable) in relation to that BM Unit.

BC2.6	COMMUNICATIONS

Electronic communications are always conducted in GMT. However, the input of data and display of information to Users and The Company and all other communications are conducted in London time.

BC2.6.1	Normal Communication With Control Points

(a)	With the exception of BC2.6.1(c) below, Bid-Offer Acceptances and, unless otherwise agreed with The Company, Ancillary Service instructions shall be given by automatic logging device and will be given to the Control Point for the BM Unit.  For all Planned Maintenance Outages the provisions of BC2.6.5 will apply.  For Generating Units (including DC Connected Power Park Modules (if relevant)) communications under BC2 shall be by telephone unless otherwise agreed by The Company and the User.

(b)	Bid-Offer Acceptances and Ancillary Service instructions must be formally acknowledged immediately by the BM Participant (or the relevant person on its behalf) via the Control Point for the BM Unit or Generating Unit in respect of that BM Unit or that Generating Unit. The acknowledgement and subsequent confirmation or rejection, within two minutes of receipt, is normally given electronically by automatic logging device. If no confirmation or rejection is received by The Company within two minutes of the issue of the Bid-Offer Acceptance, then The Company will contact the Control Point for the BM Unit by telephone to determine the reason for the lack of confirmation or rejection. Any rejection must be given in accordance with BC2.7.3 or BC2.8.3.

(c)	In the event of a failure of the logging device or an outage of The Company’s computer system, Bid-Offer Acceptances and instructions will be given, acknowledged, and confirmed or rejected by telephone. The provisions of BC2.9.7 are also applicable.

(d)	In the event that in carrying out the Bid-Offer Acceptances or providing the Ancillary Services, or when operating at the level of the Final Physical Notification Data as provided in BC2.5.1, an unforeseen problem arises, caused on safety grounds (relating to personnel or plant), The Company must be notified without delay by telephone.

(e)	The provisions of BC2.5.3 are also relevant.

(f)	Submissions of revised MVAr capability may be made by facsimile transmission, using the format given in Appendix 3 to BC2.

(g)	Communication will normally be by telephone for any purpose other than Bid-Offer Acceptances, in relation to Ancillary Services or for revisions of MVAr data.

(h)	Submissions of revised availability of Frequency Sensitive Mode may be made by facsimile transmission, using the format given in Appendix 4 to BC2. This process should only be used for technical restrictions to the availability of Frequency Sensitive Mode.

BC2.6.2	Communication With Control Points In Emergency Circumstances

The Company will issue Emergency Instructions direct to the Control Point for each BM Unit [or Generating Unit] in Great Britain. Emergency Instructions to a Control Point will normally be given by telephone (and will include an exchange of operator names).

BC2.6.3	Communication With Network Operators In Emergency Circumstances

The Company will issue Emergency Instructions direct to the Network Operator at each Control Centre in relation to actions including special actions as set out in BC1.7, actions in the categories set out under BC2.9.3.3, Embedded Generation Control and Demand Control actions.  Emergency Instructions to a Network Operator will normally be given by telephone (and will include an exchange of operator names). OC6 contains further provisions relating to Demand Control instructions; OC6B contains further provisions relating to Embedded Generation Control instructions.

BC2.6.4	Communication with Externally Interconnected System Operators in Emergency Circumstances

The Company will issue Emergency Instructions directly to the Externally Interconnected System Operator at each Control Centre.  Emergency Instructions to an Externally Interconnected System Operator will normally be given by telephone (and will include an exchange of operator names).

BC2.6.5	Communications during Planned Outages of Electronic Data Communication Facilities

Planned Maintenance Outages will normally be arranged to take place during periods of low data transfer activity. Upon any such Planned Maintenance Outage in relation to a post Gate Closure period:-

(a)	BM Participants should operate in relation to any period of time in accordance with the Physical Notification prevailing at Gate Closure current at the time of the start of the Planned Maintenance Outage in relation to each such period of time.  Such operation shall be subject to the provisions of BC2.5.1, which will apply as if set out in this BC2.6.5.  No further submissions of BM Unit Data (other than data specified in BC1.4.2(c) and BC1.4.2(e)) should be attempted or Generating Unit Data. Plant failure or similar problems causing significant deviation from Physical Notification should be notified to The Company by the submission of a revision to Export and Import Limits in relation to the BM Unit or Generating Unit so affected;

(b)	Interconnector Owners should operate in relation to any period of time in accordance with the Interconnector Reference Programme based on the latest Physical Notifications notified by the Interconnector Users at the start of the Planned Maintenance Outage in relation to each such period of time. The Interconnector Owners should communicate such latest Interconnector Reference Programme to The Company prior to the start of the Planned Maintenance Outage and continue to act in accordance with such latest Interconnector Reference Programme. No further submissions of Interconnector Reference Programme should be attempted until the end of the outage is declared.

(c)	during the outage, revisions to the data specified in BC1.4.2(c) and BC1.4.2(e) may be submitted.  Communication between Users Control Points and The Company during the outage will be conducted by telephone;

(d)	The Company will issue Bid-Offer Acceptances by telephone; and

(e)	no data will be transferred from The Company to the BMRA until the communication facilities are re-established.

(f)	The provisions of BC2.9.7 may also be relevant.

BC2.7	BID-OFFER ACCEPTANCES

BC2.7.1	Acceptance of Bids and Offers by The Company

Bid-Offer Acceptances may be issued to the Control Point at any time following Gate Closure.  Any Bid-Offer Acceptance will be consistent with the Dynamic Parameters and Export and Import Limits of the BM Unit in so far as the Balancing Mechanism timescales will allow (see BC2.7.2).

(a)	The Company is entitled to assume that each BM Unit is available in accordance with the BM Unit Data submitted unless and until it is informed of any changes.

(b)	Bid-Offer Acceptances sent to the Control Point will specify the data necessary to define a MW profile to be provided (ramp rate break-points are not normally explicitly sent to the Control Point) and to be achieved consistent with the respective BM Unit's Export and Import Limits provided or modified under BC1 or BC2, and Dynamic Parameters given under BC2.5.3 or, if agreed with the relevant User, such rate within those Dynamic Parameters as is specified by The Company in the Bid-Offer Acceptances.

(c)	All Bid-Offer Acceptances will be deemed to be at the current "Target Frequency", namely where a Genset is in Frequency Sensitive Mode they refer to target output at Target Frequency.

(d)	The form of and terms to be used by The Company in issuing Bid-Offer Acceptances together with their meanings are set out in Appendix 1 in the form of a non-exhaustive list of examples.

BC2.7.2	Consistency With Export And Import Limits And Dynamic Parameters

(a)	Bid-Offer Acceptances will be consistent with the Export and Import Limits provided or modified under BC1 or BC2 and the Dynamic Parameters provided or modified under BC2.  Bid-Offer Acceptances may also recognise Other Relevant Data provided or modified under BC1 or BC2

(b)	In the case of consistency with Dynamic Parameters this will be limited to the time until the end of the Settlement Period for which Gate Closure has most recently occurred.  If  The Company intends to issue a Bid-Offer Acceptance covering a period after the end of the Settlement Period for which Gate Closure has most recently occurred, based upon the then submitted Dynamic Parameters, Export and Import Limits and Bid-Offer Data applicable to that period,  The Company will indicate this to the BM Participant at the Control Point for the BM Unit.  The intention will then be reflected in the issue of a Bid-Offer Acceptance to return the BM Unit to its previously notified Physical Notification after the relevant Gate Closure, provided the submitted data used to formulate this intention has not changed and subject to System conditions which may affect that intention.  Subject to that, assumptions regarding Bid-Offer Acceptances may be made by BM Participants for Settlement Periods for which Gate Closure has not yet occurred when assessing consistency with Dynamic Parameters in Settlement Periods for which Gate Closure has occurred.  If no such subsequent Bid–Offer Acceptance is issued, the original Bid-Offer Acceptance will include an instantaneous return to Physical Notification at the end of the Balancing Mechanism period.

BC2.7.3	Confirmation and Rejection of Acceptances

Bid-Offer Acceptances may only be rejected by a BM Participant :

(a)	on safety grounds (relating to personnel or plant) as soon as reasonably possible and in any event within five minutes; or

(b)	because they are not consistent with the Export and Import Limits or Dynamic Parameters applicable at the time of issue of the Bid-Offer Acceptance.

A reason must always be given for rejection by telephone.

Where a Bid-Offer Acceptance is not confirmed within two minutes or is rejected,  The Company will seek to contact the Control Point for the BM Unit.  The Company must then, within 15 minutes of issuing the Bid-Offer Acceptance, withdraw the Bid-Offer Acceptance or log the Bid-Offer Acceptance as confirmed. The Company will only log a rejected Bid-Offer Acceptance as confirmed following discussion and if the reason given is, in The Company’s reasonable opinion, not acceptable, The Company will inform the BM Participant accordingly.

BC2.7.4	Action Required From BM Participants

(a)	Each BM Participant in respect of its BM Units will comply in accordance with BC2.7.1 with all Bid-Offer Acceptances given by The Company with no more than the delay allowed for by the Dynamic Parameters unless the BM Unit has given notice to The Company under the provisions of BC2.7.3 regarding non-acceptance of a Bid-Offer Acceptance.

(b)	Where a BM Unit’s input or output changes in accordance with a Bid-Offer Acceptance issued under BC2.7.1, such variation does not need to be notified to The Company in accordance with BC2.5.1.

(c)	In the event that while carrying out the Bid-Offer Acceptance an unforeseen problem arises caused by safety reasons (relating to personnel or plant), The Company must be notified immediately by telephone and this may lead to revision of BM Unit Data in accordance with BC2.5.3

BC2.7.5	Additional Action required when responding to Bid-Offer Acceptances

(a)	When complying with Bid-Offer Acceptances for a CCGT Module, a Generator will operate its CCGT Units in accordance with the applicable CCGT Module Matrix.

(b)	When complying with Bid-Offer Acceptances for a CCGT Module which is a Range CCGT Module, a Generator must operate that CCGT Module so that power is provided at the single Grid Entry Point identified in the data given pursuant to PC.A.3.2.1 or at the single Grid Entry Point to which The Company has agreed pursuant to BC1.4.2 (f).

(c)	On receiving a new MW Bid-Offer Acceptance, no tap changing shall be carried out to change the MVAr output unless there is a new MVAr Ancillary Service instruction issued pursuant to BC2.8.

(d)	When complying with Bid-Offer Acceptances for a Power Park Module, a Generator will operate its Power Park Units in accordance with the applicable Power Park Module Availability Matrix.

(e)	When complying with Bid-Offer Acceptances for a Synchronous Power Generating Module, a Generator will operate its Generating Units in accordance with the applicable Synchronous Power Generating Module Availability Matrix.

(f)    When complying with Bid-Offer Acceptances for an Additional BM Unit or Secondary BM Unit they will operate in accordance with the applicable Aggregator Impact Matrix.

BC2.8	ANCILLARY SERVICES

This section primarily covers the call-off of System Ancillary Services. The provisions relating to Commercial Ancillary Services will normally be covered in the relevant Ancillary Services Agreement.

BC2.8.1	Call-Off of Ancillary Services by The Company

(a)	Ancillary Service instructions may be issued at any time.

(b)	The Company is entitled to assume that each BM Unit (or Generating Unit) is available in accordance with the BM Unit Data (or the Generating Unit Data) and data contained in the Ancillary Services Agreement unless and until it is informed of any changes.

(c)	Frequency control instructions may be issued in conjunction with, or separate from, a Bid-Offer Acceptance.

(d)	The form of and terms to be used by The Company in issuing Ancillary Service instructions together with their meanings are set out in Appendix 2 in the form of a non-exhaustive list of examples including Reactive Power and associated instructions.

(e)	In the case of Generating Units that do not form part of a BM Unit any change in Active Power as a result of, or required to enable, the provision of an Ancillary Service will be dealt with as part of that Ancillary Service Agreement and/or provisions under the CUSC.

(f)	A System to Generator Operational Intertripping Scheme will be armed in accordance with BC2.10.2(a).

BC2.8.2	Consistency with Export and Import Limits and Dynamic Parameters

Ancillary Service instructions will be consistent with the Export and Import Limits provided or modified under BC1 or BC2 and the Dynamic Parameters provided or modified under BC2.  Ancillary Service instructions may also recognise Other Relevant Data provided or modified under BC1 or BC2.

BC2.8.3	Rejection of Ancillary Service Instructions

(a)	Ancillary Service instructions may only be rejected, by automatic logging device or by telephone, on safety grounds (relating to personnel or Plant) or because they are not consistent with the applicable Export and Import Limits, Dynamic Parameters, Other Relevant Data or data contained in the Ancillary Services Agreement and a reason must be given immediately for non-acceptance.

(b)	The issue of Ancillary Service instructions for Reactive Power will be made with due regard to any resulting change in Active Power output. The instruction may be rejected if it conflicts with any Bid-Offer Acceptance issued in accordance with BC2.7 or with the Physical Notification.

(c)	Where Ancillary Service instructions relating to Active Power and Reactive Power are given together, and to achieve the Reactive Power output would cause the BM Unit to operate outside Dynamic Parameters as a result of the Active Power instruction being met at the same time, then the timescale of implementation of the Reactive Power instruction may be extended to be no longer than the timescale for implementing the Active Power instruction but in any case to achieve the MVAr Ancillary Service instruction as soon as possible.

BC2.8.4	Action Required From BM Units

(a)	Each BM Unit (or Generating Unit) will comply in accordance with BC2.8.1 with all Ancillary Service instructions relating to Reactive Power properly given by The Company within 2 minutes or such longer period as The Company may instruct, and all other Ancillary Service instructions without delay, unless the BM Unit or Generating Unit has given notice to The Company under the provisions of BC2.8.3 regarding non-acceptance of Ancillary Service instructions.

(b)	Each BM Unit may deviate from the profile of its Final Physical Notification Data, as modified by any Bid-Offer Acceptances issued in accordance with BC2.7.1, only as a result of responding to Frequency deviations when operating in Frequency Sensitive Mode in accordance with the Ancillary Services Agreement.

(c)	Each Generating Unit that does not form part of a BM Unit may deviate from the profile of its Final Physical Notification Data where agreed by The Company and the User, including but not limited to, as a result of providing an Ancillary Service in accordance with the Ancillary Service Agreement.

(d)	In the event that while carrying out the Ancillary Service instructions an unforeseen problem arises caused by safety reasons (relating to personnel or plant), The Company must be notified immediately by telephone and this may lead to revision of BM Unit Data or Generating Unit Data in accordance with BC2.5.3.

BC2.8.5 	Reactive Despatch Network Restrictions

Where The Company has received notification pursuant to the Grid Code that a Reactive Despatch to Zero MVAr Network Restriction is in place with respect to any Embedded Power Generating Module and/or Embedded Generating Unit and/or Embedded Power Park Module or HVDC Converter at an Embedded HVDC Converter Station or DC Converter at an Embedded DC Converter Station, then The Company will not issue any Reactive Despatch Instruction with respect to that Power Generating Module and/or Generating Unit and/or Power Park Module or DC Converter or HVDC Converter until such time as notification is given to The Company pursuant to the Grid Code that such Reactive Despatch to Zero MVAr Network Restriction is no longer affecting that Power Generating Module and/or Generating Unit and/or Power Park Module or DC Converter or HVDC Converter.

BC2.9	EMERGENCY CIRCUMSTANCES

BC2.9.1	Emergency Actions

BC2.9.1.1	In certain circumstances (as determined by The Company in its reasonable opinion) it will be necessary, in order to preserve the integrity of the National Electricity Transmission System and any synchronously connected External System, for The Company to issue Emergency Instructions. In such circumstances, it may be necessary to depart from normal Balancing Mechanism operation in accordance with BC2.7 in issuing Bid-Offer Acceptances. BM Participants must also comply with the requirements of BC3.

BC2.9.1.2	Examples of circumstances that may require the issue of Emergency Instructions include:-

(a)	Events on the National Electricity Transmission System or the System of another User; or

(b)	the need to maintain adequate System and Localised NRAPM in accordance with BC2.9.4 below; or

(c)	the need to maintain adequate Frequency sensitive Gensets in accordance with BC2.9.5 below; or

(d)	the need to implement Demand Control in accordance with OC6; or

(e)	(i)	the need to invoke the System Restoration process or the Re-Synchronisation of Power Island process in accordance with OC9; or

(ii)	the need to request provision of a Maximum Generation Service; or

(iii)	the need to issue an Emergency Deenergisation Instruction in circumstances where the condition or manner of operation of any Transmission Plant and/or Apparatus is such that it may cause damage or injury to any person or to the National Electricity Transmission System; or

(f) the need to implement Embedded Generation Control in accordance with OC6B.

BC2.9.1.3	In the case of BM Units and Generating Units in Great Britain, Emergency Instructions will be issued by The Company direct to the User at the Control Point for the BM Unit or Generating Unit and may require an action or response which is outside its Other Relevant Data or Export and Import Limits submitted under BC1, or revised under BC1 or BC2, or Dynamic Parameters submitted or revised under BC2.

BC2.9.1.4	In the case of a Network Operator or an Externally Interconnected System Operator, Emergency Instructions will be issued to its Control Centre.

BC2.9.2	Implementation of Emergency Instructions

BC2.9.2.1	Users will respond to Emergency Instructions issued by The Company without delay and using all reasonable endeavours to so respond. Emergency Instructions may only be rejected by an User on safety grounds (relating to personnel or plant) and this must be notified to The Company immediately by telephone.

BC2.9.2.2	Emergency Instructions will always be prefixed with the words “This is an Emergency Instruction” except in the case of:

(i) 	Maximum Generation Service instructed by electronic data communication facilities where the instruction will be issued in accordance with the provisions of the Maximum Generation Service Agreement; and

(ii) 	an Emergency Deenergisation Instruction, where the Emergency Deenergisation Instruction will be pre-fixed with the words ‘This is an Emergency Deenergisation Instruction’; and

(iii) 	during System Restoration situation where the Balancing Mechanism has been suspended, any instruction given by The Company will (unless The Company specifies otherwise) be deemed to be an Emergency Instruction and need not be pre-fixed with the words ‘This is an Emergency Instruction’; and

(iv) 	during System Restoration where the Balancing Mechanism has not been suspended, any instruction issued to Restoration Contractors or to Network Operators which are part of an invoked Local Joint Restoration Plan will (unless The Company specifies otherwise) be deemed to be an Emergency Instruction and need not be prefixed with the words ‘This is an Emergency Instruction’.  Equally during a System Restoration where the Balancing Mechanism has not been suspended, any instruction to Network Operators which are part of an activated Distribution Restoration Zone Plan will (unless The Company specifies otherwise) be deemed to be an Emergency Instruction and need not be prefixed by the words “This is an Emergency Instruction”.

In Scotland, any instruction from the Relevant Transmission Licensee to Restoration Contractors which are part of an invoked Local Joint Restoration Plan and are instructed in accordance with the provisions of that Local Joint Restoration Plan, will be deemed to be an Emergency Instruction and need not be prefixed with the words ‘This is an Emergency Instruction’. Equally any instruction from the Relevant Transmission Licensee to Network Operators who are party to an activated Distribution Restoration Zone Plan and are instructed in accordance with the provisions of that Distribution Restoration Zone Plan will be deemed to be an Emergency Instruction and need not be prefixed with the words “This is an Emergency Instruction”.

BC2.9.2.3	In all cases under this BC2.9, except BC2.9.1.2 (e) where The Company issues an Emergency Instruction to a BM Participant which is not rejected under BC2.9.2.1, the Emergency Instruction shall be treated as a Bid-Offer Acceptance.  For the avoidance of doubt, any Emergency Instruction issued to a Network Operator or to an Externally Interconnected System Operator or in respect of a Generating Unit that does not form part of a BM Unit, will not be treated as a Bid-Offer Acceptance.

BC2.9.2.4	In the case of BC2.9.1.2 (e) (ii) where The Company issues an Emergency Instruction pursuant to a Maximum Generation Service Agreement, payment will be dealt with in accordance with the CUSC and the Maximum Generation Service Agreement.

BC2.9.2.5	In the case of BC2.9.1.2 (e) (iii) where The Company issues an Emergency Deenergisation Instruction, payment will be dealt with in accordance with the CUSC, Section 5.

BC2.9.2.6	In the case of BC2.9.1.2 (e) (i), upon receipt of an Emergency Instruction by a Generator during a System Restoration, the provisions of Section G of the BSC relating to compensation shall apply.

BC2.9.3	Examples of Emergency Instructions

BC2.9.3.1	In the case of a BM Unit or a Generating Unit, Emergency Instructions may include an instruction for the BM Unit or the Generating Unit to operate in a way that is not consistent with the Dynamic Parameters and/or Export and Import Limits.

BC2.9.3.2	In the case of a Generator, Emergency Instructions may include:

(a)	an instruction to trip one or more Gensets (excluding Operational Intertripping); or

(b)	an instruction to trip Mills or to Part Load a Generating Unit (as defined in the Glossary and Definitions and not limited by BC2.2); or

(c)	an instruction to Part Load a Power Generating Module and/or CCGT Module or Power Park Module; or

(d)	an instruction for the operation of CCGT Units within a CCGT Module (on the basis of the information contained within the CCGT Module Matrix) when emergency circumstances prevail (as determined by The Company in The Company's reasonable opinion); or

(e)	an instruction to generate outside normal parameters, as allowed for in 4.2 of the CUSC; or

(f)	an instruction for the operation of Generating Units within a Cascade Hydro Scheme (on the basis of the additional information supplied in relation to individual Generating Units) when emergency circumstances prevail (as determined by The Company in The Company’s reasonable opinion); or

(g)	an instruction for the operation of a Power Park Module (on the basis of the information contained within the Power Park Module Availability Matrix) when emergency circumstances prevail (as determined by The Company in The Company's reasonable opinion).

BC2.9.3.3	Instructions to Network Operators relating to the Operational Day may include:

(a) 	a requirement for Demand reduction and disconnection or restoration pursuant to OC6;

(b)	an instruction to effect a load transfer between Grid Supply Points;

(c)	an instruction to switch in a System to Demand Intertrip Scheme;

(d)	an instruction to split a network;

(e)	an instruction to disconnect an item of Plant or Apparatus from the System;

(f)	requirement for Embedded Generation Control or restoration pursuant to OC6B; or

(g)	an instruction to activate a Distribution Restoration Zone Plan as provided for in OC9.4.7.8.1.

BC2.9.4	Maintaining Adequate System and Localised NRAPM (Negative Reserve Active Power Margin)

BC2.9.4.1	Where The Company is unable to satisfy the required System NRAPM or Localised NRAPM by following the process described in BC1.5.5, The Company will issue an Emergency Instruction to exporting BM Units for De-Synchronising on the basis of Bid-Offer Data submitted to The Company in accordance with BC1.4.2(d). If The Company is still unable to satisfy the required System NRAPM or Localised NRAPM then The Company may issue Emergency Instructions to Network Operator(s) as set out under OC6B to carry out Embedded Generation Control.

BC2.9.4.2	In the event that The Company is unable to differentiate between exporting BM Units according to Bid-Offer Data, The Company will instruct a BM Participant to Shutdown a specified exporting BM Unit for such period based upon the following factors:

(a)	effect on power flows (resulting in the minimisation of transmission losses);

(b)	reserve capability;

(c)	Reactive Power worth;

(d)	Dynamic Parameters;

(e)	in the case of Localised NRAPM, effectiveness of output reduction in the management of the System Constraint.

BC2.9.4.3	Where The Company is still unable to differentiate between exporting BM Units, having considered all the foregoing, The Company will decide which exporting BM Unit to Shutdown by the application of a quota for each BM Participant in the ratio of each BM Participant’s Physical Notifications.

BC2.9.4.4	Other than as provided in BC2.9.4.5 and BC2.9.4.6 below, in determining which exporting BM Units to De-Synchronise under this BC2.9.4, The Company shall not consider in such determination (and accordingly shall not instruct to De-Synchronise) any Generating Unit (as defined in the Glossary and Definitions and not limited by BC2.2) within an Existing Gas Cooled Reactor Plant.

BC2.9.4.5	The Company shall be permitted to instruct a Generating Unit (as defined in the Glossary and Definitions and not limited by BC2.2) within an Existing AGR Plant to De-Synchronise if the relevant Generating Unit within the Existing AGR Plant has failed to offer to be flexible for the relevant instance at the request of The Company within the Existing AGR Plant Flexibility Limit.

BC2.9.4.6	Notwithstanding the provisions of BC2.9.4.5 above, if the level of System NRAPM (taken together with System constraints) or Localised NRAPM is such that it is not possible to avoid instructing a Generating Unit (as defined in the Glossary and Definitions and not limited by BC2.2) within an Existing Magnox Reactor Plant and/or an Existing AGR Plant whether or not it has met requests within the Existing AGR Flexibility Limit to De-Synchronise, The Company may, provided the power flow across each External Interconnection is either at zero or results in an export of power from the Total System, so instruct a Generating Unit (as defined in the Glossary and Definitions and not limited by BC2.2) within an Existing Magnox Reactor Plant and/or an Existing AGR Plant to De-Synchronise in the case of System NRAPM, in all cases and in the case of Localised NRAPM, when the power flow would have a relevant effect.

BC2.9.4.7	When instructing exporting BM Units which form part of an On-Site Generator Site to reduce generation or export under this BC2.9.4, The Company will not issue an instruction which would reduce generation or export below the reasonably anticipated Demand of the On-Site Generator Site. For the avoidance of doubt, it should be noted that the term “On-Site Generator Site” only relates to Trading Units which have fulfilled the Class 1 or Class 2 requirements.

BC2.9.5	Maintaining an adequate level of Frequency Sensitive Generation

BC2.9.5.1	If, post Gate Closure, The Company determines, in its reasonable opinion, from the information then available to it (including information relating to a Generating Unit (as defined in the Glossary and Definitions and not limited by BC2.2) breakdown) that the number of, and level of Primary, Secondary and High Frequency Response available from Gensets (other than those units within Existing Gas Cooled Reactor Plant, which are permitted to operate in Limited Frequency Sensitive Mode at all times under BC3.5.3) available to operate in Frequency Sensitive Mode, is such that it is not possible to avoid De-Synchronising Existing Gas Cooled Reactor Plant then provided that:

(a)	there are (or, as the case may be, that The Company anticipates, in its reasonable opinion, that at the time that the instruction is to take effect there will be) no other Gensets generating and exporting on to the Total System which are not operating in Frequency Sensitive Mode (or which are operating with only a nominal amount in terms of level and duration) (unless, in The Company's reasonable opinion, necessary to assist the relief of System constraints or necessary as a result of other System conditions); and

(b)	the power flow across each External Interconnection is (or, as the case may be, is anticipated to be at the time that the instruction is to take effect) either at zero or results in an export of power from the Total System,

then The Company may instruct such of the Existing Gas Cooled Reactor Plant to De-Synchronise as it is, in The Company's reasonable opinion, necessary to De-Synchronise and for the period for which the De-Synchronising is, in The Company's reasonable opinion, necessary.

BC2.9.5.2	If in The Company's reasonable opinion it is necessary for both the procedure in BC2.9.4 and that set out in BC2.9.5.1 to be followed in any given situation, the procedure in BC2.9.4 will be followed first, and then the procedure set out in BC2.9.5.1. For the avoidance of doubt, nothing in this sub-paragraph shall prevent either procedure from being followed separately and independently of the other.

BC2.9.6	Emergency Assistance to and from External Systems

(a)	An Externally Interconnected System Operator (in its role as operator of the External System) may request that The Company takes any available action to increase the Active Energy transferred into its External System, or reduce the Active Energy transferred into the National Electricity Transmission System by way of emergency assistance if the alternative is to instruct a demand reduction on all or part of its External System (or on the system of an Interconnector User using its External System). Such request must be met by The Company providing this does not require a reduction of Demand on the National Electricity Transmission System, or lead to a reduction in security on the National Electricity Transmission System.

(b)	The Company may request that an Externally Interconnected System Operator takes any available action to increase the Active Energy transferred into the National Electricity Transmission System, or reduce the Active Energy transferred into its External System by way of emergency assistance if the alternative is to instruct a Demand reduction on all or part of the National Electricity Transmission System. Such request must be met by the Externally Interconnected System Operator providing this does not require a reduction of Demand on its External System (or on the system of Interconnector Users using its External System), or lead to a reduction in security on such External System or system.

BC2.9.7	Unplanned Outages of Electronic Communication and Computing Facilities

BC2.9.7.1	In the event of an unplanned outage of the electronic data communication facilities or of The Company’s associated computing facilities or in the event of a Planned Maintenance Outage lasting longer than the planned duration, in relation to a post-Gate Closure period The Company will, as soon as it is reasonably able to do so, issue a The Company Computing System Failure notification by telephone or such other means agreed between Users and The Company indicating the likely duration of the outage.

BC2.9.7.2	During the period of any such outage, the following provisions will apply:

(a)	The Company will issue further The Company Computing System Failure notifications by telephone or such other means agreed between Users and The Company to all BM Participants to provide updates on the likely duration of the outage;

(b)	(i)	BM Participants, not subject to the provisions of BC2.9.7.2(b)(iii), should operate in relation to any period of time in accordance with the last Physical Notification prevailing at Gate Closure received prior to the computer system failure in relation to each such period of time. Such operation shall be subject to the provisions of BC2.5.1, which will apply as if set out in this BC2.9.7.2. No further submissions of BM Unit Data or Generating Unit Data (other than data specified in BC1.4.2(c) (Export and Import Limits) and BC1.4.2(e) (Dynamic Parameters) should be attempted. Plant failure or similar problems causing significant deviation from Physical Notification should be notified to The Company by telephone by the submission of a revision to Export and Import Limits in relation to the BM Unit or Generating Unit Data so affected;

(ii)	Interconnector Owners should operate in relation to any period of time in accordance with the last Interconnector Reference Programme based on the last Physical Notifications notified by the Interconnector Users prior to the computer system failure in relation to each such period of time. The Interconnector Owners should continue to act in accordance with last Interconnector Reference Programme. No further submissions of Interconnector Reference Programme should be attempted until the end of the outage is declared.

(iii) BM Participants, who are not required to have Control Telephony or System Telephony staffed at all times as provided for in CC7.9 or ECC7.9, should during periods when their telephones are not staffed operate in relation to any period of time in accordance with the last Physical Notification prevailing at Gate Closure received at the prior of the computer system failure in relation to each such period of time. Such operation shall be subject to the provisions of BC2.5.1, which will apply as if set out in this BC2.9.7.2. If the BM Participants automatic equipment identifies there has been a computer system failure then no further submissions of BM Unit Data or Generating Unit Data (other than data specified in BC1.4.2(c) (Export and Import Limits) and BC1.4.2(e) (Dynamic Parameters) should be attempted. For the avoidance of doubt between 08:00 and 18:00 hours the provisions of BC2.9.7.2(b)(i) shall apply.

(c)	Revisions to Export and Import Limits and to Dynamic Parameters should be notified to The Company by telephone and will be recorded for subsequent use;

(d)	The Company will issue Bid-Offer Acceptances by telephone which will be recorded for subsequent use;

(e)	No data will be transferred from The Company to the BMRA until the communication facilities are re-established.

BC2.9.7.3	The Company will advise BM Participants of the withdrawal of The Company Computing System Failure notification following the re-establishment of the communication facilities.

BC2.9.8  Market Suspension

BC2.9.8.1       Within the GB Synchronous Area, the National Electricity Transmission System shall be determined to be in an emergency state when operational security analysis indicates one or more of the following situations occurring:

- A situation where there is (or could be) a violation of one or more operational criteria as defined under the Security and Quality of Supply Standard (SQSS); or

- A situation when Unacceptable Frequency Conditions as defined under the System Security and Quality of Supply Standard (SQSS) have occurred; or

- At least one measure of the System Defence Plan is activated; or

- There is a failure of the computing facilities used to control and operate the National Electricity Transmission System or unplanned outages of Electronic Communication and Computing Facilities as provided for in BC2.9.7 or the loss of communication, computing and data facilities with other Transmission Licensees as provided for in STCP 06-4.

BC2.9.8.2  While the National Electricity Transmission System is in an emergency state if, after issuing National Electricity Transmission System Warnings and Emergency Instructions in accordance with (but not limited to) the requirements under OC7.4 and BC2.9, the situation deteriorates to such an extent that it results in:-

- a Total Shutdown, The Company will suspend the market in accordance with the provisions of OC9.4.6; or

- a Partial Shutdown, The Company will suspend the market but only where the Market Suspension Threshold has been met in accordance with OC9.4.6.

BC2.10	OTHER OPERATIONAL INSTRUCTIONS AND NOTIFICATIONS

BC2.10.1	The Company may, from time to time, need to issue other instructions or notifications associated with the operation of the National Electricity Transmission System.

BC2.10.2	Such instructions or notifications may include:

Intertrips

(a)	an instruction to arm or disarm an Operational Intertripping scheme;

Tap Positions

(b)	a request for a Genset step-up transformer tap position (for security assessment);

Tests

(c)	an instruction to carry out tests as required under OC5, which may include the issue of an instruction regarding the operation of CCGT Units within a CCGT Module at a Large Power Station;

Future BM Unit Requirements

(d)	a reference to any implications for future BM Unit requirements and the security of the National Electricity Transmission System, including arrangements for a change in output to meet post fault security requirements;

Changes to Target Frequency

(e)	a notification of a change in Target Frequency, which will normally only be 49.95, 50.00, or 50.05Hz but in exceptional circumstances as determined by The Company in its reasonable opinion, may be 49.90 or 50.10Hz.

BC2.10.3	Where an instruction or notification under BC2.10.2 (c) or (d) results in a change to the input or output level of the BM Unit then The Company shall issue a Bid-Offer Acceptance or Emergency Instruction as appropriate.

BC2.11	LIAISON WITH GENERATORS FOR RISK OF TRIP AND AVR TESTING

BC2.11.1	A Generator at the Control Point for any of its Large Power Stations may request The Company's agreement for one of the Gensets at that Power Station to be operated under a risk of trip. The Company's agreement will be dependent on the risk to the National Electricity Transmission System that a trip of the Genset would constitute.

BC2.11.2	(a)	Each Generator at the Control Point for any of its Large Power Stations will operate its Synchronised Gensets (excluding Power Park Modules) with:

(i)	AVRs in constant terminal voltage mode with VAR limiters in service at all times. AVR constant Reactive Power or Power Factor mode should, if installed, be disabled; and

(ii)	its generator step-up transformer tap changer selected to manual mode,

unless released from this obligation in respect of a particular Genset by The Company.

(b)	Each Generator at the Control Point for any of its Large Power Stations will operate its Power Park Modules with a Completion Date before 1st January 2006 at unity Power Factor at the Grid Entry Point (or User System Entry Point if Embedded).

(c)	Each Generator at the Control Point for any of its Large Power Stations will operate its Power Park Modules with a Completion Date on or after 1st January 2006 in voltage control mode at the Grid Entry Point (or User System Entry Point if Embedded). Constant Reactive Power or Power Factor mode should, if installed, be disabled.

(d)	Where a Power System Stabiliser is fitted as part of the excitation system or voltage control system of a Genset, it requires on-load commissioning which must be witnessed by The Company. Only when the performance of the Power System Stabiliser has been approved by The Company, shall it be switched into service by a Generator and then it will be kept in service at all times unless otherwise agreed with The Company. Further reference is made to this in CC.6.3.8 or ECC.6.3.8.

BC2.11.3	A Generator at the Control Point for any of its Power Stations may request The Company's agreement for one of its Gensets at that Power Station to be operated with the AVR in manual mode, or Power System Stabiliser switched out, or VAR limiter switched out. The Company's agreement will be dependent on the risk that would be imposed on the National Electricity Transmission System and any User System. Provided that in any event a Generator may take such action as is reasonably necessary on safety grounds (relating to personnel or plant) .

BC2.11.4 	Each Generator shall operate its dynamically controlled OTSDUW Plant and Apparatus to ensure that the reactive capability and voltage control performance requirements as specified in CC.6.3.2, CC.6.3.8, CC.A.7 or ECC.6.3.2, ECC.6.3.8, ECC.A.7, ECC.A.8 and the Bilateral Agreement can be satisfied in response to the Setpoint Voltage and Slope as instructed by The Company at the Transmission Interface Point.

BC2.12	LIAISON WITH EXTERNALLY INTERCONNECTED SYSTEM OPERATORS

BC2.12.1	Co-Ordination Role Of Externally Interconnected System Operators

(a)	The Externally Interconnected System Operator will act as the Control Point for Bid-Offer Acceptances on behalf of Interconnector Users and will co-ordinate instructions relating to Ancillary Services and Emergency Instructions on behalf of Interconnector Users using its External System in respect of each Interconnector Users BM Units.

(b)	The Company will issue Bid-Offer Acceptances and instructions for Ancillary Services relating to Interconnector Users BM Units to each Externally Interconnected System Operator in respect of each Interconnector User using its External System.

(c)	If, as a result of a reduction in the capability (in MW) of the External Interconnection, the total of the Physical Notifications and Bid-Offer Acceptances issued for the relevant period using that External Interconnection, as stated in the BM Unit Data, exceeds the reduced capability (in MW) of the respective External Interconnection in that period, then The Company shall notify the Externally Interconnected System Operator accordingly. The Externally Interconnected System Operator should seek a revision of Export and Import Limits from one or more of its Interconnector Users for the remainder of the Balancing Mechanism period during which Physical Notifications cannot be revised.

BC2.13		LIAISON WITH INTERCONNECTOR OWNERS

- Calculate the Interconnector Reference Programme

Interconnector Owners shall use best endeavours to deliver updated

- Interconnector Reference Programme to The Company by 10 minutes after each Intraday Cross-Zonal Gate Closure Time.

- The updated Interconnector Reference Programme shall fully reflect the results of the Single Intraday Coupling.

Interconnector Owners must ensure that the updated

- Interconnector Reference Programme is received in its entirety and confirmation that it has been logged into The Company’s computer systems by the time of 10 minutes after each Intraday Cross-zonal Gate Closure Time.

APPENDIX 1 - FORM OF BID-OFFER ACCEPTANCES

BC2.A.1.1	This Appendix describes the forms of Bid-Offer Acceptances. As described in BC2.6.1 Bid-Offer Acceptances are normally given by an automatic logging device, but in the event of failure of the logging device, Bid-Offer Acceptances will be given by telephone.

BC2.A.1.2	For each BM Unit the Bid-Offer Acceptance will consist of a series of MW figures and associated times.

BC2.A.1.3	The Bid-Offer Acceptances relating to CCGT Modules will assume that the CCGT Units within the CCGT Module will operate in accordance with the CCGT Module Matrix, as required by BC1. The Bid-Offer Acceptances relating to Cascade Hydro Schemes will assume that the Generating Unit forming part of the Cascade Hydro Scheme will operate, where submitted, in accordance with the Cascade Hydro Scheme Matrix submitted under BC1. The Bid-Offer Acceptances relating to Synchronous Power Generating Modules will assume that the Synchronous Generating Units within the Synchronous Power Generating Module will operate in accordance with the Synchronous Power Generating Module Matrix, as required by BC1.

BC2.A.1.4	Bid-Offer Acceptances Given By Automatic Logging Device

(a)	The complete form of the Bid-Offer Acceptance is given in the EDL Message Interface Specification which can be made available to Users on request.

(b)	Bid-Offer Acceptances will normally follow the form:

(i)	BM Unit Name

(ii)	Instruction Reference Number

(iii)	Time of instruction

(iv)	Type of instruction

(v)	BM Unit Bid-Offer Acceptance number

(vi)	Number of MW/Time points making up instruction (minimum 2, maximum 5)

(vii)	MW value and Time value for each point identified in (vi)

The times required in the instruction are input and displayed in London time, but communicated electronically in GMT.

BC2.A.1.5	Bid-Offer Acceptances Given By Telephone

(a)	All run-up/run-down rates will be assumed to be constant and consistent with Dynamic Parameters. Each Bid-Offer Acceptance will, wherever possible, be kept simple, drawing as necessary from the following forms and BC2.7

(b)	Bid-Offer Acceptances given by telephone will normally follow the form:

(i)	an exchange of operator names;

(ii)	BM Unit Name;

(iii)	Time of instruction;

(iv)	Type of instruction;

(v)	Number of MW/Time points making up instruction (minimum 2, maximum 5)

(vi)	MW value and Time value for each point identified in (v)

The times required in the instruction are expressed in London time.

For example, for a BM Unit ABCD-1 acceptance logged with a start time at 1400 hours and with a FPN at 300MW:

“BM Unit ABCD-1 Bid-Offer Acceptance timed at 1400 hours.  Acceptance consists of 4 MW/Time points as follows:

300MW at 1400 hours

400MW at 1415 hours

400MW at 1450 hours

300MW at 1500 hours”

BC2.A.1.6	Submission Of Bid-Offer Acceptance Data To The BMRA

The relevant information contained in Bid-Offer Acceptances issued by The Company will be converted into “from” and “to” MW levels and times before they are submitted to the BMRA by The Company.

APPENDIX 2 - TYPE AND FORM OF ANCILLARY SERVICE INSTRUCTIONS

BC2.A.2.1	This part of the Appendix consists of a non-exhaustive list of the forms and types of instruction for a Genset to provide System Ancillary Services. There may be other types of Commercial Ancillary Services and these will be covered in the relevant Ancillary Services Agreement.  In respect of the provision of Ancillary Services by Generating Units the forms and types of instruction will be in the form of this Appendix 2 unless amended in the Ancillary Services Agreement.

As described in CC.8 or ECC.8, System Ancillary Services consist of Part 1 and Part 2 System Ancillary Services.

Part 1 System Ancillary Services Comprise:

(a)	Reactive Power supplied other than by means of synchronous or static compensators. This is required to ensure that a satisfactory System voltage profile is maintained and that sufficient Reactive Power reserves are maintained under normal and fault conditions. Ancillary Service instructions in relation to Reactive Power may include:

(i)	MVAr Output

(ii)	Target Voltage Levels

(iii)	Tap Changes

(iv)	Maximum MVAr Output (‘maximum excitation’)

(v)	Maximum MVAr Absorption (‘minimum excitation’)

(b)	Frequency Control by means of Frequency sensitive generation. Gensets may be required to move to or from Frequency Sensitive Mode in the combinations agreed in the relevant Ancillary Services Agreement. They will be specifically requested to operate so as to provide Primary Response and/or Secondary Response and/or High Frequency Response.

Part 2 System Ancillary Services Comprise:

(c)	Frequency Control by means of Fast Start.

(d)	Anchor Plant Capability or Top Up Restoration Capability

(e)	System to Generator Operational Intertripping

BC2.A.2.2	As Ancillary Service instructions are not part of Bid-Offer Acceptances they do not need to be closed instructions and can cover any period of time, not just limited to the period of the Balancing Mechanism.

BC2.A.2.3	As described in BC2.6.1, unless otherwise agreed with The Company, Ancillary Service instructions are normally given by automatic logging device, but in the absence of, or in the event of failure of the logging device, instructions will be given by telephone.

BC2.A.2.4	Instructions given by Automatic Logging Device

(a)	The complete form of the Ancillary Service instruction is given in the EDL Message Interface Specification which is available to Users on request from The Company.

(b)	Ancillary Service instructions for Frequency Control will normally follow the form:

(i)	BM Unit Name

(ii)	Instruction Reference Number

(iii)	Time of instruction

(iv)	Type of instruction

(v)	Reason Code

(vi)	Start Time

(c)	Ancillary Service instructions for Reactive Power will normally follow the form:

(i)	BM Unit Name

(ii)	Instruction Reference Number

(iii)	Time of instruction

(iv)	Type of instruction (MVAr, VOLT or TAPP)

(v)	Target Value

(vi)	Target Time

The times required in the instruction are input and displayed in London time, but communicated electronically in GMT.

BC2.A.2.5	Instructions given by Telephone

(a)	Ancillary Service instructions for Frequency Control will normally follow the form:

(i)	an exchange of operator names;

(ii)	BM Unit Name;

(iii)	Time of instruction;

(iv)	Type of instruction;

(v)	Start Time.

The times required in the instruction are expressed in London time.

For example, for BM Unit ABCD-1 instructed at 1400 hours to provide Primary and High Frequency response starting at 1415 hours:

“BM Unit ABCD-1 message timed at 1400 hours. Unit to Primary and High Frequency Response at 1415 hours”

(b)	Ancillary Service instructions for Reactive Power will normally follow the form:

(a)	an exchange of operator names;

(b)	BM Unit Name;

(c)	Time of instruction;

(d)	Type of instruction (MVAr, VOLT, SETPOINT, SLOPE or TAPP)

(e)	Target Value

(f)	Target Time.

The times required in the instruction are expressed as London time.

For example, for BM Unit ABCD-1 instructed at 1400 hours to provide 100MVAr by 1415 hours:

“BM Unit ABCD-1 message timed at 1400 hours.  MVAr instruction.  Unit to plus 100 MVAr target time 1415 hours.”

BC2.A.2.6	Reactive Power

As described in BC2.A.2.4 and BC2.A.2.5 instructions for Ancillary Services relating to Reactive Power may consist of any of several specific types of instruction. The following table describes these instructions in more detail:

| Instruction Name | Description | Type of Instruction |
| --- | --- | --- |
| MVAr Output | The individual MVAr output from the Genset onto the National Electricity Transmission System at the Grid Entry Point (or onto the User System at the User System Entry Point in the case of Embedded Power Stations), namely on the higher voltage side of the generator step-up transformer or Grid Entry Point or User System Entry Point in the case of a Power Generating Module. In relation to each Genset, where there is no HV indication, The Company and the Generator will discuss and agree equivalent MVAr levels for the corresponding LV indication. Where a Genset is instructed to a specific MVAr output, the Generator must achieve that output within a tolerance of +/-25 MVAr (for Gensets in England and Wales) or the lesser of +/-5% of rated output or 25MVAr (for Gensets in Scotland) (or such other figure as may be agreed with The Company) by tap changing on the generator step-up transformer, or adjusting the Genset terminal voltage, subject to compliance with CC.6.3.8 (a) (v), or ECC.6.3.8.3.3 (as applicable) to a value that is equal to or higher than 1.0p.u. of the rated terminal voltage, or a combination of both. Once this has been achieved, the Generator will not tap again and will not readjust the Genset terminal voltage without prior consultation with and the agreement of The Company, on the basis that MVAr output will be allowed to vary with System conditions. | MVAr |
| Target Voltage Levels | Target voltage levels to be achieved by the Genset on the National Electricity Transmission System at the Grid Entry Point (or on the User System at the User System Entry Point in the case of Embedded Power Stations, namely on the higher voltage side of the generator step-up transformer or Grid Entry Point or User System Entry Point in the case of a Power Generating Module. Where a Genset is instructed to a specific target voltage, the Generator must achieve that target within a tolerance of ±1 kV (or such other figure as may be agreed with The Company) by tap changing on the generator step-up transformer, or adjusting the Genset terminal voltage, subject to compliance with CC.6.3.8 (a) (v) or ECC.6.3.8.3.3 (as applicable), to a value that is equal to or higher than 1.0p.u. of the rated terminal voltage, or a combination of both. In relation to each Genset, where there is no HV indication, The Company and the Generator will discuss and agree equivalent voltage levels for the corresponding LV indication. Under normal operating conditions, once this target voltage level has been achieved the Generator will not tap again and will not readjust the Genset terminal voltage without prior consultation with, and with the agreement of, The Company. However, under certain circumstances, the Generator may be instructed to maintain a target voltage until otherwise instructed and this will be achieved by tap changing on the generator step-up transformer, or adjusting the Genset terminal voltage, subject to compliance with CC.6.3.8 (a) (v) or ECC.6.3.8.3.3 (as applicable), to a value that is equal to or higher than 1.0p.u. of the rated terminal voltage, or a combination of both without reference to The Company. | VOLT |
| Setpoint Voltage | Where a Non-Synchronous Generating Unit, DC Converter or Power Park Module or HVDC Converter is instructed to a specific Setpoint Voltage, the Generator must achieve that Setpoint Voltage within a tolerance of ±0.25% (or such other figure as may be agreed with The Company). The Generator must maintain the specified Setpoint Voltage target until an alternative target is received from The Company. | SETPOINT |
| Slope | Where a Non-Synchronous Generating Unit, DC Converter or Power Park Module or HVDC Converter is instructed to a specific Slope, the Generator must achieve that Slope within a tolerance of ±0.5% (or such other figure as may be agreed with The Company). The Generator must maintain the specified Slope target until an alternative target is received from The Company. The Generator will not be required to implement a new Slope setting in a time of less than 1 week from the time of the instruction. | SLOPE |
| Tap Changes | Details of the required generator step-up transformer tap changes in relation to a Genset. The instruction for tap changes may be a Simultaneous Tap Change instruction, whereby the tap change must be effected by the Generator in response to an instruction from The Company issued simultaneously to relevant Power Stations. The instruction, which is normally preceded by advance notice, must be effected as soon as possible, and in any event within one minute of receipt from The Company of the instruction. For a Simultaneous Tap Change, change Genset generator step-up transformer tap position by one [two] taps to raise or lower (as relevant) System voltage, to be executed at time of instruction. | TAPP |
| Maximum MVAr Output (“maximum excitation”) | Under certain conditions, such as low System voltage, an instruction to maximum MVAr output at instructed MW output ("maximum excitation") may be given, and a Generator should take appropriate actions to maximise MVAr output unless constrained by plant operational limits or safety grounds (relating to personnel or plant). |  |
| Maximum MVAr Absorption ("minimum excitation") | Under certain conditions, such as high System voltage, an instruction to maximum MVAr absorption at instructed MW output ("minimum excitation") may be given, and a Generator should take appropriate actions to maximise MVAr absorption unless constrained by plant operational limits or safety grounds (relating to personnel or plant). |  |

BC2.A.2.7	In addition, the following provisions will apply to Reactive Power instructions:

(a)	In circumstances where The Company issues new instructions in relation to more than one BM Unit at the same Power Station at the same time, tapping will be carried out by the Generator one tap at a time either alternately between (or in sequential order, if more than two), or at the same time on, each BM Unit.

(b)	Where the instructions require more than two taps per BM Unit and that means that the instructions cannot be achieved within 2 minutes of the instruction time (or such longer period as The Company may have instructed), the instructions must each be achieved with the minimum of delay after the expiry of that period.

(c)	It should be noted that should System conditions require, The Company may need to instruct maximum MVAr output to be achieved as soon as possible, but (subject to the provisions of paragraph (BC2.A.2.7(b) above) in any event no later than 2 minutes after the instruction is issued.

(d)	An Ancillary Service instruction relating to Reactive Power may be given in respect of CCGT Units within a CCGT Module at a Power Station or Generating Units within a Synchronous Power Generating Module at a Power Station where running arrangements and/or System conditions require, in both cases where exceptional circumstances apply and connection arrangements permit.

(e)	In relation to MVAr matters, MVAr generation/output is an export onto the System and is referred to as "lagging MVAr", and MVAr absorption is an import from the System and is referred to as "leading MVAr".

(f)	It should be noted that the excitation control system constant Reactive Power output control mode or constant Power Factor output control mode will always be disabled, unless agreed otherwise with The Company.

APPENDIX 3 - SUBMISSION OF REVISED MVAr CAPABILITY

BC2.A.3.1	For the purpose of submitting revised MVAr data the following terms shall apply:

| Full Output | In the case of a Synchronous Generating Unit (as defined in the Glossary and Definitions ((which could be part of a Synchronous Power Generating Module) and not limited by BC2.2) is the MW output measured at the generator stator terminals representing the LV equivalent of the Registered Capacity at the Grid Entry Point, and in the case of a Non-Synchronous Generating Unit (excluding Power Park Units), HVDC Converter or DC Converter or Power Park Module is the Registered Capacity at the Grid Entry Point. |
| --- | --- |
| Minimum Output | In the case of a Synchronous Generating Unit (as defined in the Glossary and Definitions ((which could be part of a Synchronous Power Generating Module) and not limited by BC2.2 ) is the MW output measured at the generator stator terminals representing the LV equivalent of the Minimum Generation or Minimum Stable Operating Level at the Grid Entry Point, and in the case of a Non-Synchronous Generating Unit (excluding Power Park Units), HVDC Converter or DC Converter or Power Park Module is the Minimum Generation or Minimum Stable Operating Level or Minimum Active Power Transmission Capacity at the Grid Entry Point. |

BC2.A.3.2	The following provisions apply to faxed submission of revised MVAr data:

(a)	The fax must be transmitted to The Company (to the relevant location in accordance with GC6) and must contain all the sections from the relevant part of Annexure 1 and from either Annexure 2 or 3 (as applicable) but with only the data changes set out. The "notification time" must be completed to refer to the time of transmission, where the time is expressed as London time.

(b)	Upon receipt of the fax, The Company will acknowledge receipt by sending a fax back to the User. The acknowledgement will either state that the fax has been received and is legible or will state that it (or part of it) is not legible and will request re-transmission of the whole (or part) of the fax.

(c)	Upon receipt of the acknowledging fax the User will, if requested, re-transmit the whole or the relevant part of the fax.

(d)	The provisions of paragraphs (b) and (c) then apply to that re-transmitted fax.

APPENDIX 3 - ANNEXURE 1

Optional Logo

Company name REVISED REACTIVE POWER

CAPABILITY DATA

| TO: | National Electricity Transmission System Control Centre |  |  | Fax telephone No. |
| --- | --- | --- | --- | --- |

Number of pages inc. header:.............................

Sent By : ........................................................................................................

Return Acknowledgement Fax to ....................................................................

For Retransmission or Clarification ring..........................................................

Acknowledged by The Company: (Signature)

................................................................................

Acknowledgement time and date

....................................................................................

Legibility of FAX :

| Acceptable |  |  |
| --- | --- | --- |
| Unacceptable (List pages if appropriate) |  | ( Resend FAX ) |

APPENDIX 3 - ANNEXURE 2

To:	 National Electricity Transmission System Control Centre

From :	[Company Name & Location]

REVISED REACTIVE POWER CAPABILITY DATA – GENERATING UNITS EXCLUDING POWER PARK MODULES AND DC CONVERTERS

| Notification Time (HH:MM): | Notification Date (DD/MM/YY): |
| --- | --- |
| Start Time (HH:MM): | Start Date (DD/MM/YY): |
| Generating Unit* |  |

* For a Synchronous Power Generating Module and/or CCGT Module and/or a Cascade Hydro Scheme, the redeclaration is for a Generating Unit within a Synchronous Power Generating Module and/or CCGT Module and/or Cascade Hydro Scheme. For BM Units, quote The Company BM Unit id, for other units quote the Generating Unit id used for OC2.4.1.2 Outage Planning submissions. Generating Unit has the meaning given in the Glossary and Definitions and is not limited by BC2.2.

REVISION TO THE REACTIVE POWER CAPABILITY AT THE GENERATING UNIT STATOR TERMINALS (at rated terminal volts) AS STATED IN THE RELEVANT ANCILLARY SERVICES AGREEMENT:

|  | MW | MINIMUM (MVAr +ve for lag, -ve for lead) | MAXIUM (MVAr +ve for lag, -ve for lead) |
| --- | --- | --- | --- |
| AT RATED MW |  |  |  |
| AT FULL OUTPUT (MW) |  |  |  |
| AT MINIMUM OUTPUT (MW) |  |  |  |

COMMENTS e.g. generator transformer tap restrictions, predicted end time if known

_________________________________________________________________________

_________________________________________________________________________

Redeclaration made by (Signature)

_________________________________________________

APPENDIX 3 - ANNEXURE 3

To:	 National Electricity Transmission System Control Centre

From :	[Company Name & Location]

REVISED REACTIVE POWER CAPABILITY DATA – POWER PARK MODULES, HVDC CONVERTERS AND DC  CONVERTERS

| Notification Time (HH:MM): | Notification Date (DD/MM/YY): |
| --- | --- |
| Start Time (HH:MM): | Start Date (DD/MM/YY): |
| Power Park Module / DC Converter* |  |

* For BM Units quote The Company BM Unit id, for other units quote the id used for OC2.4.1.2 Outage Planning submissions

Start Time/Date (if not effective immediately)

REVISION TO THE REACTIVE POWER CAPABILITY AT THE COMMERCIAL BOUNDARY AS STATED IN THE RELEVANT ANCILLARY SERVICES AGREEMENT:

|  | MINIMUM (MVAr +ve for lag, -ve for lead) | MAXIMUM (MVAr +ve for lag, -ve for lead) |
| --- | --- | --- |
| AT RATED MW |  |  |
| AT 50% OF RATED MW |  |  |
| AT 20% OF RATED MW |  |  |
| BELOW 20% OF RATED MW |  |  |
| AT 0% OF RATED MW |  |  |

COMMENTS e.g. generator transformer tap restrictions, predicted end time if known

_________________________________________________________________________

_________________________________________________________________________

Redeclaration made by (Signature)

_________________________________________________
APPENDIX 4 - SUBMISSION OF AVAILABILITY OF FREQUENCY SENSITIVE MODE

BC2.A.4.1	For the purpose of submitting availability of Frequency Sensitive Mode, this process only relates to the provision of response under the Frequency Sensitive Mode and does not cover the provision of response under the Limited Frequency Sensitive Mode.

BC2.A.4.2	The following provisions apply to the faxed submission of the Frequency Sensitive Mode availability;

(a)	The fax must be transmitted to The Company (to the relevant location in accordance with GC6) and must contain all the sections relevant to Appendix 4 - Annexure1 but with only the data changes set out. The “notification time” must be completed to refer to the time and date of transmission, where the time is expressed in London time.

(b)	Upon receipt of the fax, The Company will acknowledge receipt by sending a fax back to the User.  This acknowledging fax should be in the format of Appendix 4 – Annexure 1. The acknowledgement will either state that the fax has been received and is legible or will state that it (or part of it) is not legible and will request re-transmission of the whole (or part) of the fax.

(c)	Upon receipt of the acknowledging fax the User will, if requested re-transmit the whole or the relevant part of the fax.

(d)	The provisions of paragraph (b) and (c) then apply to the re-transmitted fax.

BC2.A.4.3	The User shall ensure the availability of operating in Frequency Sensitive Mode is restored as soon as reasonably practicable and will notify The Company using the format of Appendix 4 – Annexure 1. In the event of a sustained unavailability of Frequency Sensitive Mode, The Company may seek to confirm compliance with the relevant requirements in the CC or ECC through the process in OC5 or ECP.

APPENDIX 4 - ANNEXURE 1

To:	 National Electricity Transmission System Control Centre

From :	[Company Name & Location]

Submission of availability of Frequency Sensitive Mode

| Notification Time (HH:MM): | Notification Date (DD/MM/YY): |
| --- | --- |
| Start Time (HH:MM): | Start Date (DD/MM/YY): |
| Genset or DC Converter |  |

The availability of the above unit to operate in Frequency Sensitive Mode is as follows:

All contract modes: Available / Unavailable [delete as applicable]; or

Change to the availability of individual contract modes:

| Contract Mode e.g. A | Availability for operation in Frequency Sensitive Mode [Y/N] |
| --- | --- |

COMMENTS e.g. reason for submission, predicted end time if known

_________________________________________________________________________

_________________________________________________________________________

Redeclaration made by (Signature)______________________________________________

Receipt Acknowledgement from The Company

| Legible (tick box) |  | Illegible (tick box) |  |
| --- | --- | --- | --- |
| Explanation: |  |  |  |
| Time: Date: Signature: |  |  |  |

< END OF BALANCING CODE 2 >