## Menu
Electricity Ten Year Statement (ETYS) 2014
Appendix B - Supplementary Technical Data
Table | Title
B.1.1a | SHE Transmission Index of Substation Codes
B.1.1b | SPT Index of Substation Codes
B.1.1c | NGET Index of Substation Codes
B.1.1d | OFTO Index of Substation Codes
B.2.1a | SHE Transmission Circuits 2014/15
B.2.1b | SPT Circuits 2014/15
B.2.1c | NGET Circuits 2014/15
B.2.1d | OFTO Circuits 2014/15
B.2.2a | SHE Transmission Circuit Changes 2015/16 to 2023/24
B.2.2b | SPT Transmission Circuit Changes 2015/16 to 2023/24
B.2.2c | NGET Transmission Circuit Changes 2015/16 to 2023/24
B.2.2d | OFTO Circuit Changes 2015/16 to 2023/24
B.3.1a | SHE Transmission Transformers Winter 2014/15
B.3.1b | SPT Transformers Winter 2014/15
B.3.1c | NGET Transformers Winter 2014/15
B.3.1d | OFTO Transformers 2014/15
B.3.2a | SHE Transmission Transformer Changes 2015/16 to 2023/24
B.3.2b | SPT Transformer Changes 2015/16 to 2023/24
B.3.2c | NGET Transformer Changes 2015/16 to 2023/24
B.3.2d | OFTO Transformer Changes 2015/16 to 2023/24
B.4.1a | SHE Transmission Reactive Compensation Equipment Winter 2014/15
B.4.1b | SPT Reactive Compensation Equipment Winter 2014/15
B.4.1c | NGET Reactive Compensation Equipment Winter 2014/15
B.4.1d | OFTO Reactive Compensation Equipment Winter 2014/15
B.4.2a | SHE Transmission Reactive Compensation Equipment Changes 2015/16 to 2023/24
B.4.2b | SPT Reactive Compensation Equipment Changes 2015/16 to 2023/24
B.4.2c | NGET Reactive Compensation Equipment Changes 2015/16 to 2023/24
B.4.2d | OFTO Reactive Compensation Equipment Changes 2015/16 to 2023/24

## B-1-1a
Table B.1.1a - SHE Transmission Index of Substation Codes |  |  | Back To Menu
Site Code | Site Name | Voltage (kV)
ABBA | Aberdeen Bay | 132
ABBA | Aberdeen Bay | 33
ABNE | Abernethy | 132
ABNE | Abernethy | 33
ACHR | A-Cruach | 132
ACHR | A-Cruach | 33
AIGA | Aigas | 132
ALLT | Allt Duine | 132
ALLT | Allt Duine | 33
ALNE | Alness | 132
ALNE | Alness | 33
ALYT | Alyth | 400
ALYT | Alyth | 275
ALYT | Alyth | 33
AMUL | Amulree | 132
ANSU | An Suidhe | 132
ANSU | An Suidhe | 33
ARBR | Arbroath | 132
ARBR | Arbroath | 33
ARDK | Ardkinglas | 132
ARDK | Ardkinglas | 33
ARDR | Ardross | 275
ARMO | Ardmore | 132
ARMO | Ardmore | 33
AULW | Aultmore | 132
AULW | Aultmore | 33
BADA | Bad A Cheo | 33
BASK | Bay of Skaill | 220
BASK | Bay of Skaill | 132
BASK | Bay of Skaill | 33
BEAT | Beatrice Wind | 400
BEAU | Beauly | 400
BEAU | Beauly | 275
BEAU | Beauly | 132
BEAU | Beauly | 33
BEIN | Beinneun | 132
BEIN | Beinneun | 33
BENA | Ben Aketil | 33
BERB | Berryburn | 275
BERB | Berryburn | 33
BETH | Beinn Tharsuinn | 33
BGLA | Beinn Ghlas | 33
BHLA | Bhlaraidh | 132
BHLA | Bhlaraidh | 33
BIHI | Birkhill | 132
BLHI | Blackhillock | 400
BLHI | Blackhillock | 275
BLHI | Blackhillock | 132
BLHI | Blackhillock | 33
BOAG | Boat of Garten | 132
BOAG | Boat of Garten | 33
BONB | Bonnybridge Boundary | 400
BONB | Bonnybridge Boundary | 275
BOYN | Boyndie | 33
BRAC | Braco | 275
BRAC | Braco | 33
BRDU | Braes of Doune Wind | 33
BREC | Brechin | 132
BRID | Bridge of Dun | 132
BRID | Bridge of Dun | 33
BROA | Broadford | 132
BROA | Broadford | 33
BROR | Brora | 132
BROR | Brora | 33
BTUI | Beinn an Tuirc | 33
BUMU | Burghmuir | 132
BUMU | Burghmuir | 33
BUWH | Burn of Whilk | 33
CAAD | Carradale | 132
CAAD | Carradale | 33
CAIR | Cairn Uish Rothes | 33
CAMW | Camster Wind | 33
CASH | Cashlie | 33
CASS | Cashley | 132
CASS | Cashley | 33
CAUS | Causeymire | 33
CEAN | Ceannacroc | 132
CEAN | Ceannacroc | 33
CHAR | Charleston | 132
CHAR | Charleston | 33
CLAC | Clachan | 132
CLAC | Clachan | 33
CLAS | Clashindarroch | 275
CLAS | Clashindarroch | 33
CLAY | Clayhills | 132
CLAY | Clayhills | 33
CLUN | Clunie | 132
COGA | Corriegarth | 132
COGA | Corriegarth | 33
COGL | Coire Glas | 400
COIN | Coire Na Cloiche | 33
CONN | Connagill | 275
CONN | Connagill | 132
CONN | Connagill | 33
CORI | Corriemoillie | 132
CORI | Corriemoillie | 33
COUA | Coupar Angus | 132
COUA | Coupar Angus | 33
COUW | Cour Wind | 33
CRAI | Craigiebuckler | 132
CRAI | Craigiebuckler | 33
CROB | Crossburns | 275
CROB | Crossburns | 33
CRSS | Crossaig | 220
CRSS | Crossaig | 132
CRSS | Crossaig | 33
CULL | Culligran | 132
DAAS | Dallas | 275
DAAS | Dallas | 33
DALC | Dalchonzie | 33
DALN | Dalnessie | 132
DALN | Dalnessie | 33
DEAN | Deanie | 132
DENS | Denside | 132
DEUC | Deucherin Hill | 33
DORE | Dorenell | 132
DORE | Dorenell | 33
DOUN | Dounreay | 275
DOUN | Dounreay | 220
DOUN | Dounreay | 132
DOUN | Dounreay | 33
DRUB | Druim Ba | 132
DRUB | Druim Ba | 33
DRUL | Druim Lethann | 132
DUCC | Dunmore Cable Compound | 132
DUBE | Dunbeath | 132
DUBE | Dunbeath | 33
DUDH | Dudhope | 132
DUDH | Dudhope | 33
DUGR | Dunvegan | 132
DUGR | Dunvegan | 33
DUNM | Dunmaglass | 132
DUNM | Dunmaglass | 33
DYCE | Dyce | 132
DYCE | Dyce | 33
EDIN | Edinbane | 132
EDIN | Edinbane | 33
EDNT | Edintore | 33
EISE | Eishken | 132
ELGI | Elgin | 132
ELGI | Elgin | 33
ERRO | Errochty | 132
FAAR | Farr Windfarm | 132
FAAR | Farr Windfarm | 33
FARI | Farigaig | 275
FARI | Farigaig | 132
FARI | Farigaig | 33
FASN | Fasnakyle | 275
FASN | Fasnakyle | 33
FAUG | Fort Augustus | 400
FAUG | Fort Augustus | 275
FAUG | Fort Augustus | 132
FAUG | Fort Augustus | 33
FAWI | Fairburn Wind | 33
FAWX | Fairburn Extension | 132
FAWX | Fairburn Extension | 33
FERO | Fernoch | 132
FERO | Fernoch | 33
FETT | Fetteresso | 400
FETT | Fetteresso | 132
FETT | Fetteresso | 33
FIDD | Fiddes | 132
FIDD | Fiddes | 33
FINL | Finlarig | 132
FOFF | Firth of Forth | 275
FOGG | Foggieton | 132
FOYE | Foyers | 275
FRAS | Fraserburgh | 132
FRAS | Fraserburgh | 33
FWIL | Fort William | 132
FWIL | Fort William | 33
FYRI | Fyrish | 275
FYRI | Fyrish | 132
FYRI | Fyrish | 33
GARB | Gareloch Boundary | 132
GILB | Gills Bay | 132
GILB | Gills Bay | 33
GLAG | Glen Agnes | 132
GLAG | Glen Agnes | 33
GLCA | Glencassley | 33
GLDO | Glendoe Substation | 132
GLEM | Glenmorie | 132
GLEM | Glenmorie | 33
GLEN | Glenmoriston | 132
GLFA | Glenfarclas | 132
GLFA | Glenfarclas | 33
GLOF | Glens of Foundland | 33
GLRB | Glenrothes Boundary | 275
GOHI | Gordonstown Hill | 33
GORW | Gordonbush Wind | 275
GORW | Gordonbush Wind | 33
GRAR | Gravir | 132
GRIF | Griffin Wind | 132
GRIF | Griffin Wind | 33
GRUB | Grudie Bridge | 132
GRUB | Grudie Bridge | 33
GRUB | Grudie Bridge | 33
HALY | Halsary | 33
HILF | Hilll of Fishrie | 33
HITO | Hill of Towie | 33
HUER | Hunterston (Note this is SP) | 220
INAW | Inverawe | 33
INGA | Invergarry | 132
INNE | Inverness | 132
INNE | Inverness | 33
INRU | Inverugie | 132
INVB | Inverarnan Boundary | 275
INVE | Inveraray | 132
INVR | Inverarnan | 132
INVR | Inverarnan | 33
KEIT | Keith | 275
KEIT | Keith | 132
KEIT | Keith | 33
KEIT | Keith | 33
KIIN | Killin | 132
KIIN | Killin | 33
KILC | Kilchrenan | 132
KILO | Kinlochleven | 132
KILO | Kinlochleven | 33
KINB | Kincardine Boundary | 400
KINT | Kintore | 400
KINT | Kintore | 275
KINT | Kintore | 132
KINT | Kintore | 33
KIOR | Kilmorack | 132
KNOC | Knocknagael | 275
KNOC | Knocknagael | 132
KNOC | Knocknagael | 33
GLKY | Kyllachy | 132
GLKY | Kyllachy | 33
LAGG | Laggan | 132
LAGR | Lag Na Greine | 132
LAIR | Lairg | 132
LAIR | Lairg | 33
LIME | Limekilns Wind | 132
LIME | Limekilns Wind | 33
LOCB | Loch Buidhe | 275
LOCB | Loch Buidhe | 132
LOCB | Loch Buidhe | 33
LOCH | Lochay | 132
LOCH | Lochay | 33
LOCL | Loch Lundie | 132
LOCL | Loch Lundie | 33
LUBR | Lubreoch | 33
LUIC | Luichart | 132
LUMB | Lumbs | 132
LUNA | Lunanhead | 132
LUNA | Lunanhead | 33
LYND | Lyndhurst | 132
LYND | Lyndhurst | 33
MACD | Macduff | 132
MACD | Macduff | 33
MEYG | Meygen Tidal | 132
MEYG | Meygen Tidal | 33
MIHW | Midhill Wind | 33
MILC | Milton of Craigie | 132
MILC | Milton of Craigie | 33
MILS | Millenium South | 132
MILS | Millenium South | 33
MILW | Millenium Wind | 132
MILW | Millenium Wind | 33
MORF | Moray Firth Wind | 400
MOSS | Mossford | 132
MOYW | Moy Wind | 33
MUAI | Muaithebheal | 132
MYBS | Mybster | 132
MYBS | Mybster | 33
NAIR | Nairn | 132
NAIR | Nairn | 33
NANT | Nant | 132
NEDE | New Deer | 400
NOVA | Novar | 33
NOVW | Novar Wind | 33
ORKN | Orkney | 220
ORKN | Orkney | 132
ORKN | Orkney | 33
ORRI | Orrin | 132
ORRI | Orrin | 33
PAUH | Paul's Hill Aberlour | 33
PEHE | Peterhead | 400
PEHE | Peterhead | 275
PEHE | Peterhead | 275
PEHE | Peterhead | 275
PEHE | Peterhead | 132
PEHE | Peterhead | 33
PEHG | Peterhead Grange | 132
PEHG | Peterhead Grange | 33
PERS | Persley | 275
PERS | Persley | 132
PERS | Persley | 33
PERW | Pentland Road Wind | 132
PORA | Port Ann | 132
PORA | Port Ann | 33
QUOI | Quoich | 132
RANN | Rannoch | 132
RANN | Rannoch | 33
REDM | Redmoss | 132
REDM | Redmoss | 33
ROSH | Rosehall | 33
ROTI | Rothienorman | 400
SALA | Sallachy | 132
SALA | Sallachy | 33
SFEG | St Fergus Gas Terminal | 132
SFEM | St Fergus Mobil | 132
SFER | St Fergus | 132
SFIL | St Fillians | 132
SFIL | St Fillians | 33
SHET | Shetland | 132
SHIN | Shin | 275
SHIN | Shin | 132
SHIN | Shin | 33
SLOY | Sloy | 132
SOUI | Sound of Islay | 33
SPIH | Spittal Hill | 33
SPIT | Spittal | 275
SPIT | Spittal | 132
SPIT | Spittal | 33
STOM | Stoneywood Mills | 33
STWD | Stornoway Wind | 132
STRB | Strathbrora Substation | 275
STRB | Strathbrora Substation | 33
STRI | Strichen | 132
STRI | Strichen | 33
STRL | Stronelairg Wind | 400
STRL | Stronelairg Wind | 132
STRL | Stronelairg Wind | 33
STRS | Stroupster Wind | 33
STRW | Strathy | 275
STRW | Strathy | 132
STRW | Strathy | 33
TANG | Tangy | 33
TARL | Tarland | 132
TARL | Tarland | 33
TAYN | Taynuilt | 132
TAYN | Taynuilt | 33
TEAL | Tealing | 275
TEAL | Tealing | 132
TEAL | Tealing | 33
THSO | Thurso | 275
THSO | Thurso | 132
THSO | Thurso | 33
TOLS | Tolsta | 132
TOLS | Tolsta | 33
TOMN | Tom Na Clach | 132
TOMN | Tom Na Clach | 33
TOMT | Tomatin | 275
TOMT | Tomatin | 132
TOMT | Tomatin | 33
TOMW | Tomatin Wind | 33
TORA | Torr Achilty | 33
TULL | Tullich | 33
TULW | Tullo 2 | 33
TUMB | Tummel Bridge | 132
TUMB | Tummel Bridge | 33
TUMM | Tummel | 400
TUMM | Tummel | 275
TUMM | Tummel | 132
TUMM | Tummel | 33
WATH | Wathegar 2 | 33
WFIB | Westfield Boundary | 275
WHIB | Whitebridge | 132
WIOW | Willowdale | 132
WIOW | Willowdale | 33
WOHI | Woodhill | 132
WOHI | Woodhill | 33

## B-1-1b
Table B.1.1b - SPT Index of Substation Codes |  |  | Back To Menu
Site Code | Site Name | Voltage (kV)
AREC | Arecleoch | 132
AREC | Arecleoch | 33
AUCH | Auchencrosh | 275
AUCW | Auchenwynd | 132
AYR- | Ayr | 275
AYR- | Ayr | 33
BAGA | Bathgate | 132
BAGA | Bathgate | 33
BAIN | Bainsford | 132
BAIN | Bainsford | 33
BERW | Berwick | 132
BERW | Berwick | 33
BLKL | Black Law | 132
BLKL | Black Law | 33
BONB | Bonnybridge Boundary | 132
BONN | Bonnybridge | 132
BONN | Bonnybridge | 275
BONN | Bonnybridge | 33
BPGR | BP Grangemouth | 33
BRAE | Braehead | 132
BRAP | Braehead Park | 132
BRAP | Braehead Park | 33
BROX | Broxburn | 132
BROX | Broxburn | 33
BUSB | Busby | 275
CAFA | Carsfad | 132
CALD | Calder | 33
CATY | Carntyne | 132
CATY | Carntyne | 33
CHAP | Chapelcross | 132
CHAP | Chapelcross | 33
CHAS | Charlotte Street | 275
CHAS | Charlotte Street | 33
CLYM | Clyde's Mill | 275
CLYM | Clyde's Mill | 33
CLYN | Clyde North | 275
CLYN | Clyde North | 33
CLYS | Clyde South | 275
CLYS | Clyde South | 33
COAL | Coalburn | 132
COAL | Coalburn | 33
COAL | Coalburn | 400
COAT | Coatbridge | 275
COAT | Coatbridge | 33
COCK | Cockenzie | 275
COCK | Cockenzie | 33
COCK | Cockenzie | 400
COYL | Coylton | 132
COYL | Coylton | 275
COYL | Coylton | 33
COYT | Coylton Tee | 132
COYW | Coylton West | 275
CRMH | Cruach Mhor | 33
CROO | Crookston | 132
CROO | Crookston | 33
CRUA | Cruachan | 275
CRYR | Crystal Rigg | 132
CRYR | Crystal Rigg | 33
CRYR | Crystal Rigg | 400
CUMB | Cumbernauld | 132
CUMB | Cumbernauld | 33
CUPA | Cupar | 132
CUPA | Cupar | 33
CURR | Currie | 132
CURR | Currie | 275
CURR | Currie | 33
DALL | Dalmally | 275
DALM | Dalmarnock | 132
DALM | Dalmarnock | 275
DALM | Dalmarnock | 33
DENN | Denny North | 275
DEVM | Devol Moor | 132
DEVM | Devol Moor | 33
DEVM | Devol Moor | 400
DEVO | Devonside | 132
DEVO | Devonside | 33
DEWP | Dewar Place | 275
DEWP | Dewar Place | 33
DRCR | Drumcross | 132
DRCR | Drumcross | 33
DRUM | Drumchapel | 275
DRUM | Drumchapel | 33
DUMF | Dumfries | 132
DUMF | Dumfries | 33
DUNB | Dunbar | 132
DUNB | Dunbar | 33
DUNE | Dunlaw Extension | 132
DUNE | Dunlaw Extension | 33
DUNF | Dunfermline | 132
DUNF | Dunfermline | 33
DUNO | Dunoon | 132
DUNO | Dunoon | 33
EAST | Earlstoun | 132
ECCF | Ecclefechan | 132
ECCL | Eccles | 132
ECCL | Eccles | 33
ECCL | Eccles | 400
EERH | Easterhouse | 275
EERH | Easterhouse | 33
EKIL | East Kilbride | 275
EKIL | East Kilbride | 33
EKIS | East Kilbride South | 275
EKIS | East Kilbride South | 33
ELDE | Elderslie | 132
ELDE | Elderslie | 33
ELVA | Elvanfoot | 275
ELVA | Elvanfoot | 33
ELVA | Elvanfoot | 400
ERSK | Erskine | 132
ERSK | Erskine | 33
ESST | Essenside | 132
EXON | Exxon mobil | 33
FALL | Fallago | 33
FALL | Fallago | 400
FIFE | Fife Energy | 132
FINN | Finnieston | 132
FINN | Finnieston | 33
GALA | Galashields | 132
GALA | Galashields | 33
GARB | Gareloch Boundary | 132
GARE | Gareloch | 132
GIFF | Giffnock | 275
GIFF | Giffnock | 33
GLLE | Glenlee | 132
GLLU | Glenluce | 132
GLLU | Glenluce | 33
GLNI | Glenniston | 132
GLNI | Glenniston | 33
GLRB | Glenrothes Boundary | 275
GLRO | Glenrothes | 275
GLRO | Glenrothes | 33
GORG | Gorgie | 132
GORG | Gorgie | 33
GOVA | Govan | 132
GOVA | Govan | 33
GRMO | Grangemouth | 275
GRMO | Grangemouth | 33
GRNA | Gretna | 132
GRNA | Gretna | 33
GRNA | Gretna | 400
HADH | Hadyard Hill | 132
HADH | Hadyard Hill | 33
HAGR | Haggs Road | 132
HAGR | Haggs Road | 33
HAKB | Harker Border Node | 132
HAKB | Harker Border Node | 400
HARE | Harestanes | 132
HARE | Harestanes | 33
HAWI | Hawick | 132
HAWI | Hawick | 33
HELE | Helensburgh | 132
HELE | Helensburgh | 33
HUER | Hunterston | 132
HUER | Hunterston | 33
HUER | Hunterston | 400
HUNF | Hunterston Farm | 132
HUNF | Hunterston Farm | 33
INKE | Inverkeithing | 132
INKE | Inverkeithing | 33
INVB | Inverarnan Boundary | 275
INVR | Inverarnan | 275
INWI | Innerwick | 132
JOHN | Johnstone | 132
JOHN | Johnstone | 33
JUNA | Junction A | 132
JUNV | Junction V | 132
KAIM | Kaimes | 275
KAIM | Kaimes | 33
KEOO | Kendoon | 132
KIER | Killermont | 132
KIER | Killermont | 33
KILB | Kilbowie | 132
KILB | Kilbowie | 33
KILS | Kilmarnock South | 132
KILS | Kilmarnock South | 275
KILS | Kilmarnock South | 33
KILS | Kilmarnock South | 400
KILT | Kilmarnock Town | 275
KILT | Kilmarnock Town | 33
KILW | Kilwinning | 132
KILW | Kilwinning | 33
KINB | Kincardine Boundary | 275
KINC | Kincardine | 275
LAMB | Lambhill | 275
LEVE | Leven | 132
LEVE | Leven | 33
LEVT | Leven Tee | 132
LING | Livingstone | 132
LING | Livingstone | 33
LINM | Linmill | 132
LINM | Linmill | 33
LOAN | Longannet | 275
LOPA | Longpark | 33
MAHI | Mark's Hill | 132
MAHI | Mark's Hill | 275
MAHI | Mark's Hill | 33
MAYB | Maybole | 132
MAYB | Maybole | 33
MAYT | Maybole Tee | 132
MEAD | Meadowhead | 132
MOFF | Moffat | 132
MOFF | Moffat | 33
MOFF | Moffat | 400
MOSH | Mossmorran Shell | 132
MOSM | Mossmorran | 132
MOSM | Mossmorran | 275
MOSM | Mossmorran | 33
NEAR | Newarthill | 275
NEAR | Newarthill | 33
NEIL | Neilston | 132
NEIL | Neilston | 275
NEIL | Neilston | 33
NEIL | Neilston | 400
NETS | Newton Stewart | 132
NETS | Newton Stewart | 33
PAIS | Paisley | 132
PAIS | Paisley | 33
PART | Partick | 132
PART | Partick | 33
POLK | Polkemmet | 33
POOB | Portobello | 275
POOB | Portobello | 33
PORD | Port Dundas | 275
PORD | Port Dundas | 33
RAVE | Ravenscraig | 33
REDH | Redhouse | 132
REDH | Redhouse | 33
ROBP | Rothes BioPower | 33
SACO | Saltcoats | 132
SACO | Saltcoats | 33
SANX | St Andrews Cross | 132
SANX | St Andrews Cross | 33
SHRU | Shrubhill | 275
SHRU | Shrubhill | 33
SIGH | Sighthill | 275
SIGH | Sighthill | 33
SMEA | Smeaton | 132
SMEA | Smeaton | 275
SMEA | Smeaton | 33
SMEA | Smeaton | 400
SPAV | Spango Valley | 132
SPAV | Spango Valley | 33
STCR | Steven's Croft | 33
STHA | Strathaven | 275
STHA | Strathaven | 33
STHA | Strathaven | 400
STIR | Stirling | 132
STIR | Stirling | 33
STLE | Strathleven | 132
STLE | Strathleven | 33
STWB | Stella West Border Node | 400
TELR | Telford Road | 132
TELR | Telford Road | 33
TODD | Toddleburn | 33
TONG | Tongland | 132
TORN | Torness | 132
TORN | Torness | 33
TORN | Torness | 400
WFIB | Westfield Boundary | 275
WFIE | Westfield | 132
WFIE | Westfield | 275
WFIE | Westfield | 33
WGEO | West George Street | 275
WGEO | West George Street | 33
WHHO | Whitehouse | 275
WHHO | Whitehouse | 33
WHTB | Whistlefield Boundary | 132
WHTL | Whistlefield | 132
WHTL | Whistlefield | 33
WISH | Wishaw (Gowkthrapple) | 132
WISH | Wishaw (Gowkthrapple) | 275
WISH | Wishaw (Gowkthrapple) | 33
WIYH | Windyhill | 132
WIYH | Windyhill | 275
WIYH | Windyhill | 33
WIYH | Windyhill | 400
WLEE | Whitelee | 275
WLEE | Whitelee | 33
WLEX | Whitelee Extension | 275
WLEX | Whitelee Extension | 33

## B-1-1c
Table B.1.1c - NGET Index of Substation Codes |  |  | Back To Menu
Site Code | Site Name | Voltage (kV)
ABHA | Abham | 132
ABHA | Abham | 400
ABTH | Aberthaw | 132
ABTH | Aberthaw | 275
AESB | AES Barry | 132
ALDW | Aldwarke | 33
ALDW | Aldwarke | 275
ALVE | Alverdiscott | 400
AMEM | Amersham | 132
AUST | Aust | 400
AXMI | Axminster | 132
AXMI | Axminster | 400
BAGB | Baglan Bay | 275
BARK | Barking | 33
BARK | Barking | 132
BARK | Barking | 275
BARK | Barking | 400
BARY | Barry | 132
BEDD | Beddington | 132
BEDD | Beddington | 275
BEDD | Beddington | 400
BESW | Berkswell | 132
BESW | Berkswell | 275
BICF | Bicker Fen | 132
BICF | Bicker Fen | 400
BIRK | Birkenhead | 275
BISW | Bishops Wood | 275
BLYT | Blyth | 275
BLYT | Blyth | 400
BOLN | Bolney | 132
BOLN | Bolney | 400
BOTW | Botley Wood | 400
BRAW | Bradford West | 275
BRAW | Bradford West | 400
BRED | Bredbury | 275
BRFO | Bramford | 400
BRIM | Brimsdown | 132
BRIM | Brimsdown | 275
BRIM | Brimsdown | 400
BRIN | Brinsworth | 275
BRIN | Brinsworth | 400
BRLE | Bramley | 400
BRWA | Bridgwater | 275
BRWA | Bridgewater | 400
BRWE | Bradwell | 132
BURW | Burwell | 400
BUSH | Bushbury | 275
BUST | Bustleholm | 275
BUST | Bustleholm | 400
CADS | Cardiff South | 132
CAML | Camblesforth | 66
CANT | Canterbury | 400
CANT | Canterbury | 132
CAPE | Capenhurst | 132
CAPE | Capenhurst | 275
CAPE | Capenhurst | 400
CARE | Cardiff East | 275
CARN | Carnedd Wen | 400
CARR | Carrington | 132
CARR | Carrington | 275
CARR | Carrington | 400
CELL | Cellarhead | 132
CELL | Cellarhead | 400
CHIC | Chickerell | 400
CHIC | Chickerell | 132
CHSI | Chessington | 132
CHSI | Chessington | 275
CHTE | Chesterfield | 275
CILF | Cilfynydd | 275
CILF | Cilfynydd | 400
CITR | City Road | 400
CLEV | Cleve Hill | 132
CLEH | Cleve Hill | 400
CONQ | Connah's Quay | 132
COSO | Coryton South | 400
COTT | Cottam | 400
COVE | Coventry | 275
COWL | Cowley | 400
COWT | Cowbridge Tee | 275
CREB | Creyke Beck | 275
CREB | Creyke Beck | 400
CULJ | Culham Jet | 400
DAIN | Daines | 400
DAMC | Damhead Creek | 400
DEES | Deeside | 400
DIDC | Didcot | 400
DINO | Dinorwig | 400
DISS | Diss | 400
DRAK | Drakelow | 132
DRAK | Drakelow | 275
DRAK | Drakelow | 400
DRAX | Drax | 132
DRAX | Drax | 400
DUNG | Dungeness | 275
DUNG | Dungeness | 400
EALI | Ealing | 275
EASO | Eaton Socon | 400
ECLA | East Claydon | 132
ECLA | East Claydon | 400
EGGB | Eggborough | 400
ELLA | Elland | 132
ELLA | Elland | 275
ELST | Elstree | 132
ELST | Elstree | 275
ELST | Elstree | 400
ENDE | Enderby | 400
EXET | Exeter | 400
EXET | Exeter | 132
FAWL | Fawley | 132
FAWL | Fawley | 400
FECK | Feckenham | 66
FECK | Feckenham | 275
FECK | Feckenham | 400
FERR | Ferrybridge | 132
FERR | Ferrybridge | 275
FERR | Ferrybridge | 400
FFES | Ffestiniog | 275
FIDF | Fiddler's Ferry | 275
FINP | Finsbury Park | 400
FLEE | Fleet | 400
FOUR | Fourstones | 275
FROD | Frodsham | 275
FROD | Frodsham | 400
GRAI | Grain | 400
GREN | Grendon | 132
GREN | Grendon | 400
GRIW | Grimsby West | 132
GRIW | Grimsby West | 400
GRSA | Greystones 'B' | 275
GRSB | Greystones 'B' | 275
GRST | Greystones | 275
GRTO | Grangetown | 275
HACK | Hackney | 275
HACK | Hackney | 400
HAKB | Harker Border (Node) | 400
HAMH | Hams Hall | 132
HAMH | Hams Hall | 275
HAMH | Hams Hall | 400
HARK | Harker | 132
HARK | Harker | 275
HARK | Harker | 400
HARM | Hart Moor | 275
HATL | Hartlepool | 275
HAWP | Hawthorn Pit | 275
HAWP | Hawthorn Pit | 400
HEDD | Heddon Tee | 400
HEDO | Hedon | 275
HEND | Hendon | 132
HEYS | Heysham | 132
HEYS | Heysham | 400
HIGM | High Marnham | 275
HIGM | High Marnham | 400
HINP | Hinkley Point | 275
HINP | Hinkley Point | 400
HIRN | Hirst North | 400
HUMR | Humber Refinery | 400
HURS | Hurst | 275
HUTT | Hutton | 400
IMPP | Imperial Park | 400
INCE | Ince | 132
INDQ | Indian Queens | 400
IROA | Iron Acton | 132
IROA | Iron Acton | 275
IRON | Ironbridge | 132
IRON | Ironbridge | 400
IVER | Iver | 275
IVER | Iver | 400
JORD | Jordanthorpe | 275
KEAD | Keadby | 132
KEAD | Keadby | 400
KEAR | Kearsley | 132
KEAR | Kearsley | 275
KEAR | Kearsley | 400
KEMS | Kemsley | 400
KEMS | Kemsley | 132
KENG | Kensal Green | 400
KIBY | Kirkby | 275
KILL | Killinghome | 400
KILY | Kings Lynn | 400
KINO | Kingsnorth | 132
KINO | Kingsnorth | 400
KIRK | Kirkstall | 132
KIRK | Kirkstall | 275
KITW | Kitwell | 275
KLYN | Kings Lynn | 132
KNAR | Knaresborough | 132
KNAR | Knaresborough | 275
LACK | Lackenby | 275
LACK | Lackenby | 400
LAKE | Lakeside | 400
LALE | Laleham | 275
LAND | Landulph | 400
LAGA | Langage | 400
LEGA | Legacy | 400
LEIB | Leighton Buzzard | 400
LISD | Lister Drive | 275
LITB | Little Barford | 400
LITD | Little Dunham | 275
LITT | Littlebrook | 132
LITT | Littlebrook | 275
LITT | Littlebrook | 400
LOFI | Longfield | 400
LOVE | Lovedean | 400
LOWE | Lowestoft | 400
MACC | Macclesfield | 275
MACC | Macclesfield | 400
MAGA | Margam | 275
MANN | Mannington | 400
MAWO | Marchwood | 400
MEDW | Medway | 400
MEDW | Medway | 400
MELK | Melksham | 132
MELK | Melksham | 275
MELK | Melksham | 400
MILH | Mill Hill | 132
MILH | Mill Hill | 275
MITY | Minety | 400
MIWW | Mid Wales West | 400
MOEL | St Asaph | 400
MONF | Monk Fryston | 275
MONF | Monk Fryston | 400
MUCF | Mucking Flats | 400
MUMB | Mumby | 400
NECH | Nechells | 275
NEEP | Neepsend | 275
NEEP | Neepsend | 400
NEWX | New Cross | 275
NFLE | Northfleet East | 132
NFLE | Northfleet East | 400
NHYD | North Hyde | 66
NHYD | North Hyde | 275
NINF | Ninfield | 400
NINF | Ninfield | 132
NORL | Norton Lees | 275
NORT | Norton | 275
NORT | Norton | 400
NORW | Norwich Main | 400
NORW | Norwich | 132
NURS | Nursling | 400
OCKH | Ocker Hill | 132
OCKH | Ocker Hill | 275
OFFE | Offerton | 275
OLDB | Oldbury | 132
OLDB | Oldbury | 275
OLDB | Oldbury | 400
OLDS | Oldbury-on-Severn | 400
OSBA | Osbaldwick | 132
OSBA | Osbaldwick | 400
OSWE | Oswestry | 400
PADI | Padiham | 132
PADI | Padiham | 400
PAFB | Patford Bridge | 400
PELH | Pelham | 400
PEMB | Pembroke | 132
PEMB | Pembroke | 400
PENN | Penn | 275
PENN | Penn | 400
PENN | Penn | 132
PENT | Pentir | 400
PENT | Pentir | 132
PEWO | Penwortham | 275
PEWO | Penwortham | 400
PITS | Pitsmoor | 275
POPP | Poppleton | 275
PURI | Puritan | 400
PYLE | Pyle | 132
PYLE | Pyle | 275
RAIN | Rainhill | 275
RASS | Rassau | 400
RATS | Ratcliffe-on-Soar | 132
RATS | Ratcliffe-on-Soar | 275
RATS | Ratcliffe-on-Soar | 400
RAYL | Rayleigh | 400
REBR | Redbridge | 275
RHIG | Rhigos | 400
RICH | Richborough | 400
ROCH | Rochdale | 275
ROCH | Rochdale | 400
ROCK | Rocksavage | 400
RUGE | Rugeley | 132
RUGE | Rugeley | 400
RYEH | Rye House | 400
SAEN | Saltend North | 275
SAES | Saltend South | 275
SAFO | Sandford | 400
SALH | Saltholme | 275
SBAR | Stoke Bardolph | 132
SBAR | Stoke Bardolph | 400
SEAB | Seabank | 132
SEAB | Seabank | 400
SELL | Sellindge | 400
SELW | Sellindge West | 400
SHBA | South Humber Bank | 400
SHEC | Sheffield City | 275
SHRE | Shrewsbury | 132
SHRE | Shrewsbury | 400
SING | Singlewell | 400
SIZE | Sizewell | 132
SIZE | Sizewell | 400
SJOW | St Johns Wood | 275
SJOW | St Johns Wood | 400
SKLG | Skelton Grange | 132
SKLG | Skelton Grange | 275
SMAN | South Manchester | 275
SPEN | Spennymoor | 400
SPEN | Spennymoor | 132
SPEN | Spennymoor | 275
SPLN | Spalding North | 400
SSHI | South Shields | 275
STAH | Stanah | 400
STAL | Stalybridge | 275
STAL | Stalybridge | 400
STAY | Staythorpe | 400
STAY | Staythorpe | 400
STEN | Stella North | 132
STES | Stella South | 132
STEW | Stella West | 275
STEW | Stella West | 400
STSB | Stocksbridge | 400
STYC | Staythorpe | 132
SUND | Sundon | 400
SUTB | Sutton Bridge | 400
SWAN | Swansea North | 275
SWAN | Swansea North | 400
TAUN | Taunton | 400
TEMP | Templeborough | 275
THOM | Thorpe Marsh | 66
THOM | Thorpe Marsh | 275
THOM | Thorpe Marsh | 400
THOR | Brine Field | 400
THTO | Thornton | 400
THUR | Thurcroft | 275
TILB | Tilbury | 132
TILB | Tilbury | 275
TILB | Tilbury | 400
TINP | Tinsley Park | 275
TOCK | Tockington | 400
TODP | Tod Point | 275
TODP | Tod Point | 400
TOTE | Tottenham East | 275
TOTT | Tottenham | 132
TOTT | Tottenham | 275
TOTT | Tottenham | 400
TOTW | Tottenham West | 275
TRAW | Trawsfynydd | 275
TRAW | Trawsfynydd | 400
TREM | Tremorfa | 275
TREU | Treuddyn Tee | 400
TYNE | Tynemouth | 11
TYNE | Tynemouth | 132
TYNE | Tynemouth | 275
UPPB | Upper Boat | 275
USKM | Uskmouth | 132
USKM | Uskmouth | 275
WALH | Walham | 400
WALP | Walpole | 132
WALP | Walpole | 400
WALX | Waltham Cross | 275
WALX | Waltham Cross | 400
WARL | Warley | 275
WASF | Washway Farm | 275
WATS | Watford South | 132
WATS | Watford South | 275
WBOL | West Boldon | 275
WBUR | West Burton | 132
WBUR | West Burton | 400
WHAM | West Ham | 132
WHAM | West Ham | 400
WHGA | Whitegate | 275
WHSO | Whitson | 275
WHSO | Whitson | 400
WIBA | Wincobank | 275
WIEN | Willenhall | 275
WILE | Willington East | 400
WILL | Willington | 132
WILL | Willington | 275
WIMB | Wimbledon | 132
WIMB | Wimbledon | 275
WISD | Willesden | 66
WISD | Willesden | 132
WISD | Willesden | 275
WMEL | West Melton | 275
WTHU | West Thurrock | 400
WTHU | West Thurrock | 33
WWEY | West Weybridge | 275
WWEY | West Weybridge | 400
WMAR | Weston Marsh | 400
WYLF | Wylfa | 132
WYLF | Wylfa | 400
WYMO | Wymondley | 400

## B-1-1d
Table B1.1d - Offshore Transmission Sites |  | Back To Menu
Code | Site
BAOW | Barrow Offshore Wind Farm
BURB | Burbo Bank
DOCS | Docking Shoal
DOGG | Dogger Bank
DUDG | Dudgeon
GGON | Greater Gabbard Onshore
GUNS | Gunfleet Sands
GWYN | Gwynt Y Mor
HORN | Hornsea
HUMG | Humber Gateway
IGOF | Greater Gabbard Offshore
LITD | Little Dunham
LOAW | London Array Wind Farm
LONO | London Array
ORMO | Ormonde
RACB | Race Bank
RORE | Robin Rigg East
RORW | Robin Rigg West
RREW | Robin Rigg East Wind Farm
RRWW | Robin Rigg West Wind Farm
SHSW | Sheringham Shoal Wind Farm
WAAW | Walney 1 Wind Farm
WABW | Walney 2 Wind Farm
WERW | Westermost Rough Wind Farm
WODS | West of Duddon Sands

## B-2-1a
Table B.2.1a - SHE Transmission Circuits ETYS Yr1 - 2014/15 | [11 empty] | Back To Menu
Node1 | Node2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter (MVA) | Spring (MVA) | Summer (MVA) | Autumn (MVA)
ABNE1Q | ABNE1R | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
ABNE1Q | CHAR1- | 24.5 | 0 | OHL | 2.49 | 5.66 | 1.22 | 131.9999 | 122.0999 | 105.402 | 122.0999
ABNE1R | AMUL1G | 27.4 | 0 | OHL | 2.799 | 6.4179 | 1.361 | 131.9999 | 122.0999 | 105.402 | 122.0999
AIGA1Q | KIOR1Q | 2.4 | 0.52 | Composite | 0.264 | 0.594 | 0.66 | 111 | 102.675 | 88.6335 | 102.675
ALNE1Q | MOTA1Q | 1.3 | 0 | OHL | 0.06 | 0.28 | 0.07 | 229.0011 | 211.826 | 182.8574 | 211.826
ALNE1R | MOTA1R | 1.3 | 0 | OHL | 0.06 | 0.28 | 0.07 | 229.0011 | 211.826 | 182.8574 | 211.826
AMUL1E | AMUL1F | 0 | 9 | Cable | 0.295 | 0.852 | 10.345 | 140 | 129.5 | 111.79 | 129.5
AMUL1F | GRIF1S | 6.8 | 0 | OHL | 0.6947 | 1.5928 | 0.338 | 131.9999 | 122.0999 | 105.402 | 122.0999
AMUL1G | AMUL1H | 0 | 9 | Cable | 0.295 | 0.852 | 10.345 | 140 | 129.5 | 111.79 | 129.5
AMUL1H | GRIF1T | 6.8 | 0 | OHL | 0.6947 | 1.5928 | 0.338 | 131.9999 | 122.0999 | 105.402 | 122.0999
ARBR1Q | DENS1Q | 14.5 | 0 | OHL | 1.47 | 3.37 | 0.71 | 182.9999 | 169.2749 | 146.1254 | 169.2749
ARBR1R | TEAL1- | 23.2 | 0 | OHL | 1.85 | 5.27 | 1.17 | 182.9999 | 169.2749 | 146.1254 | 169.2749
ARDK1- | INVE1J | 9 | 0 | OHL | 0.92 | 2.1 | 0.44 | 131.9999 | 122.0999 | 105.402 | 122.0999
ARDK1- | SLOY1T | 10 | 0 | OHL | 1.02 | 2.33 | 0.49 | 131.9999 | 122.0999 | 105.402 | 122.0999
ARDR2Q | BEAU2J | 33.5 | 0 | OHL | 0.2664 | 1.8257 | 7.073 | 535.0006 | 494.8756 | 427.198 | 494.8756
ARDR2Q | STRB2- | 51.3 | 0 | OHL | 0.408 | 2.7957 | 10.832 | 535.0006 | 494.8756 | 427.198 | 494.8756
ARMO1J | DUGR1Q | 14 | 0 | OHL | 2.38 | 3.94 | 0.93 | 83 | 76.775 | 66.2755 | 76.775
BEAU1J | BEAU1K | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
BEAU1J | BEAU1R | 0 | 2.4 | Cable | 0.0787 | 0.2272 | 2.758 | 140 | 129.5 | 111.79 | 129.5
BEAU1J | CULL1Q | 14 | 0 | OHL | 1.43 | 3.28 | 0.69 | 111 | 102.675 | 88.6335 | 102.675
BEAU1J | FAAR1Q | 30.1 | 0 | OHL | 3.065 | 7.025 | 1.49 | 131.9999 | 122.0999 | 105.402 | 122.0999
BEAU1J | ORRI1S | 13.5 | 0 | OHL | 1.36 | 3.2 | 0.64 | 126 | 116.55 | 100.611 | 116.55
BEAU1K | BEAU1S | 0 | 2.4 | Cable | 0.0787 | 0.2272 | 2.758 | 140 | 129.5 | 111.79 | 129.5
BEAU1K | FAAR1R | 30.1 | 0 | OHL | 3.065 | 7.025 | 1.49 | 131.9999 | 122.0999 | 105.402 | 122.0999
BEAU1K | KIOR1Q | 1.1 | 0.2 | Composite | 0.13 | 0.29 | 0.06 | 111 | 102.675 | 88.6335 | 102.675
BEAU1K | ORRI1T | 13.5 | 0 | OHL | 1.36 | 3.2 | 0.64 | 126 | 116.55 | 100.611 | 116.55
BEAU1L | MOTA1R | 29.2 | 0 | OHL | 2.967 | 6.794 | 1.446 | 126 | 116.55 | 100.611 | 116.55
BEAU1M | MOTA1Q | 29.2 | 0 | OHL | 2.967 | 6.794 | 1.446 | 126 | 116.55 | 100.611 | 116.55
BEAU1P | BEAU1L | 0 | 2.1 | Cable | 0.0689 | 0.1988 | 2.414 | 140 | 129.5 | 111.79 | 129.5
BEAU1Q | BEAU1M | 0 | 2.1 | Cable | 0.0689 | 0.1988 | 2.414 | 140 | 129.5 | 111.79 | 129.5
BEAU1R | INNE1Q | 13.4 | 0 | OHL | 1.365 | 3.122 | 0.661 | 126 | 116.55 | 100.611 | 116.55
BEAU1S | INNE1R | 13.4 | 0 | OHL | 1.365 | 3.122 | 0.661 | 126 | 116.55 | 100.611 | 116.55
BEAU2J | BEAU2K | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
BEAU2J | FASN2- | 25.3 | 0 | OHL | 0.069 | 1.025 | 7.23 | 1910 | 1766.75 | 1525.135 | 1766.75
BEAU2J | KNOC2L | 16.8 | 0 | OHL | 0.099 | 0.687 | 4.672 | 934.9996 | 864.8746 | 746.5972 | 864.8746
BEAU2K | DOUN2- | 153.2 | 0 | OHL | 0.9584 | 8.0602 | 32.238 | 702.001 | 649.351 | 560.5478 | 649.351
BEAU2K | KNOC2M | 16.8 | 0 | OHL | 0.099 | 0.687 | 4.672 | 934.9996 | 864.8746 | 746.5972 | 864.8746
BEAU4- | FAUG4- | 48.6 | 0 | OHL | 0.063 | 0.931 | 29.386 | 2779.9968 | 2571.4971 | 2219.8275 | 2571.4971
BLHI2J | BERB2Q | 45.81 | 0 | OHL | 0.5335 | 1.9644 | 12.113 | 524.998 | 485.6232 | 419.2109 | 485.6232
BLHI2J | BLHI2K | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
BLHI2J | KINT2K | 51.5 | 0 | OHL | 0.6 | 2.21 | 13.66 | 524.998 | 485.6232 | 419.2109 | 485.6232
BLHI2J | PEHERSV1 | 82.72 | 0 | OHL | 0.42 | 3.576 | 21.598 | 1090.0017 | 1008.2515 | 870.3663 | 1008.2515
BLHI2K | DAAS2- | 32.2 | 0 | OHL | 0.38 | 1.381 | 8.51 | 524.998 | 485.6232 | 419.2109 | 485.6232
BLHI2K | KEIT2Q | 2.4 | 0 | OHL | 0.01 | 0.1 | 0.58 | 1090.0017 | 1008.2515 | 870.3663 | 1008.2515
BLHI2K | KINT2J | 51.5 | 0 | OHL | 0.6 | 2.21 | 13.66 | 524.998 | 485.6232 | 419.2109 | 485.6232
BOAG1Q | FAAR1Q | 30.1 | 0 | OHL | 3.065 | 7.025 | 1.49 | 131.9999 | 122.0999 | 105.402 | 122.0999
BOAG1Q | GLFA1- | 21.3 | 0 | OHL | 3.3496 | 7.6799 | 1.633 | 126 | 116.55 | 100.611 | 116.55
BOAG1R | FAAR1R | 30.1 | 0 | OHL | 3.065 | 7.025 | 1.49 | 131.9999 | 122.0999 | 105.402 | 122.0999
BRAC1Q | BONB1J | 9.7 | 0 | OHL | 0.98 | 2.23 | 0.48 | 126 | 116.55 | 100.611 | 116.55
BRAC1Q | ERRO1J | 57.5 | 0 | OHL | 5.87 | 13.41 | 2.86 | 131.9999 | 122.0999 | 105.402 | 122.0999
BRAC1R | BONB1K | 9.7 | 0 | OHL | 0.98 | 2.23 | 0.48 | 126 | 116.55 | 100.611 | 116.55
BRAC1R | ERRO1K | 57.5 | 0 | OHL | 5.87 | 13.41 | 2.86 | 131.9999 | 122.0999 | 105.402 | 122.0999
BREC1Q | BREC1R | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
BREC1Q | BRID1Q | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 103.6 | 89.432 | 103.6
BREC1Q | FIDD1B | 30.1 | 0 | OHL | 3.54 | 7.26 | 1.48 | 112 | 103.6 | 89.432 | 103.6
BREC1R | BRID1R | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 103.6 | 89.432 | 103.6
BREC1R | DENS1Q | 26.1 | 0 | OHL | 3.08 | 6.33 | 1.29 | 112 | 103.6 | 89.432 | 103.6
BROA1Q | EDIN1- | 44.9 | 0 | OHL | 6.014 | 9.963 | 2.332 | 83 | 76.775 | 66.2755 | 76.775
BROA1Q | QUOI1Q | 63.4 | 0 | OHL | 8.99 | 14.87 | 3.11 | 83 | 76.775 | 66.2755 | 76.775
BROR1- | BROR1Q | 1.1 | 0 | OHL | 0.12 | 0.27 | 0.06 | 111 | 102.675 | 88.6335 | 102.675
BROR1Q | DUBE1Q | 38.8 | 0 | OHL | 3.94 | 9.01 | 1.91 | 126 | 116.55 | 100.611 | 116.55
BROR1Q | SHIN1- | 34.3 | 0 | OHL | 3.49 | 7.99 | 1.7 | 126 | 116.55 | 100.611 | 116.55
BUMU1Q | BUMU1R | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
BUMU1Q | CHAR1- | 42.2 | 0 | OHL | 4.29 | 9.76 | 2.1 | 131.9999 | 122.0999 | 105.402 | 122.0999
BUMU1R | AMUL1E | 17.1 | 0 | OHL | 1.7468 | 4.0054 | 0.849 | 131.9999 | 122.0999 | 105.402 | 122.0999
CAAD1Q | PORA1Q | 61.8 | 0 | OHL | 8.75 | 14.53 | 3.01 | 99.0001 | 91.5751 | 79.0516 | 91.5751
CAAD1R | PORA1R | 61.8 | 0 | OHL | 8.75 | 14.53 | 3.01 | 99.0001 | 91.5751 | 79.0516 | 91.5751
CASS1Q | LAIR1Q | 28 | 0 | OHL | 2.84 | 6.75 | 1.33 | 111 | 102.675 | 88.6335 | 102.675
CEAN1Q | MILW1S | 3.7 | 0 | OHL | 0.38 | 0.86 | 0.18 | 111 | 102.675 | 88.6335 | 102.675
CHAR1- | BIHI1R | 3.9 | 0 | OHL | 0.17 | 0.851 | 0.206 | 229.0011 | 211.826 | 182.8574 | 211.826
CHAR1- | CHAR1R | 1 | 0 | OHL | 0 | 0.01 | 0 | 229.0011 | 211.826 | 182.8574 | 211.826
CHAR1- | CHAR1S | 1 | 0 | OHL | 0 | 0.01 | 0 | 126 | 116.55 | 100.611 | 116.55
CHAR1- | CHAR1T | 1 | 0 | OHL | 0 | 0.01 | 0 | 126 | 116.55 | 100.611 | 116.55
CHAR1R | BIHI1Q | 3.9 | 0 | OHL | 0.17 | 0.851 | 0.206 | 229.0011 | 211.826 | 182.8574 | 211.826
CHAR1S | GLAG1Q | 1.5 | 2.2 | Composite | 0.2 | 0.46 | 4.13 | 126 | 116.55 | 100.611 | 116.55
CHAR1S | LYND1Q | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 116.55 | 100.611 | 116.55
CHAR1T | GLAG1R | 1.5 | 2.2 | Composite | 0.2 | 0.46 | 4.13 | 126 | 116.55 | 100.611 | 116.55
CHAR1T | LYND1R | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 116.55 | 100.611 | 116.55
CLAC1Q | INVE1J | 8.4 | 0 | OHL | 0.85 | 1.95 | 0.41 | 126 | 116.55 | 100.611 | 116.55
CLAC1Q | SLOY1K | 14.2 | 0 | OHL | 1.44 | 3.3 | 0.7 | 131.9999 | 122.0999 | 105.402 | 122.0999
CLAY1Q | CLAY1S | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
CLAY1Q | WIOW1Q | 2.1 | 0 | OHL | 0.08 | 0.12 | 4.19 | 120 | 111 | 95.82 | 111
CLAY1R | CLAY1T | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
CLAY1S | REDM1Q | 0 | 4.8 | Cable | 0.19 | 0.28 | 9.82 | 120 | 111 | 95.82 | 111
CLAY1T | REDM1R | 0 | 4.8 | Cable | 0.19 | 0.28 | 9.82 | 120 | 111 | 95.82 | 111
CLUN1Q | CLUN1S | 1 | 0 | OHL | 0 | 0.01 | 0 | 126 | 116.55 | 100.611 | 116.55
CLUN1R | CLUN1T | 1 | 0 | OHL | 0 | 0.01 | 0 | 126 | 116.55 | 100.611 | 116.55
CLUN1S | COUA1Q | 38.1 | 0 | OHL | 3.88 | 8.88 | 1.88 | 126 | 116.55 | 100.611 | 116.55
CLUN1S | ERRO1K | 15.4 | 0 | OHL | 1.57 | 3.6 | 0.76 | 126 | 116.55 | 100.611 | 116.55
CLUN1T | COUA1R | 38.1 | 0 | OHL | 3.88 | 8.88 | 1.88 | 126 | 116.55 | 100.611 | 116.55
CLUN1T | ERRO1J | 15.4 | 0 | OHL | 1.57 | 3.6 | 0.76 | 126 | 116.55 | 100.611 | 116.55
CORI1J | CORI1K | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
CORI1J | LUIC1Q | 7.238 | 0 | OHL | 0.748 | 1.756 | 0.353 | 126 | 116.55 | 100.611 | 116.55
CORI1J | MOSS1S | 3.87 | 0.64 | Composite | 0.419 | 0.998 | 0.947 | 126 | 116.55 | 100.611 | 116.55
CORI1K | LUIC1R | 7.238 | 0 | OHL | 0.748 | 1.756 | 0.353 | 126 | 116.55 | 100.611 | 116.55
CORI1K | MOSS1T | 3.87 | 0.64 | Composite | 0.419 | 0.998 | 0.947 | 126 | 116.55 | 100.611 | 116.55
COUA1Q | BIHI1Q | 14.6 | 0 | OHL | 1.49 | 3.41 | 0.72 | 126 | 116.55 | 100.611 | 116.55
COUA1R | BIHI1R | 14.6 | 0 | OHL | 1.49 | 3.41 | 0.72 | 126 | 116.55 | 100.611 | 116.55
CRAI1- | CRAI1Q | 1 | 0 | OHL | 0 | 0.01 | 0 | 145.0001 | 134.1251 | 115.7826 | 134.1251
CRAI1- | FOGG1Q | 4.7 | 0 | OHL | 0.485 | 1.057 | 0.221 | 131.9999 | 122.0999 | 105.402 | 122.0999
CRAI1- | FOGG1R | 4.7 | 0 | OHL | 0.485 | 1.057 | 0.221 | 131.9999 | 122.0999 | 105.402 | 122.0999
CRAI1- | KINT1- | 17.5 | 0 | OHL | 1.24 | 3.97 | 0.89 | 145.0001 | 134.1251 | 115.7826 | 134.1251
CRAI1- | KINT1- | 17.5 | 0 | OHL | 1.24 | 3.97 | 0.89 | 145.0001 | 134.1251 | 115.7826 | 134.1251
CRAI1- | REDM1R | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 145.225 | 125.3645 | 145.225
CRAI1- | WOHI1Q | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130.0001 | 120.2501 | 103.8051 | 120.2501
CRAI1- | WOHI1R | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130.0001 | 120.2501 | 103.8051 | 120.2501
CRAI1Q | REDM1Q | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 145.225 | 125.3645 | 145.225
CULL1Q | DEAN1Q | 9 | 0 | OHL | 0.93 | 2.12 | 0.45 | 111 | 102.675 | 88.6335 | 102.675
DENS1Q | TEAL1- | 8.7 | 0 | OHL | 0.38 | 1.9 | 0.46 | 182.9999 | 169.2749 | 146.1254 | 169.2749
DOUN1- | THSO1Q | 15.4 | 0 | OHL | 1.57 | 3.6 | 0.76 | 131.9999 | 122.0999 | 105.402 | 122.0999
DOUN1- | THSO1R | 15.4 | 0 | OHL | 1.57 | 3.6 | 0.76 | 131.9999 | 122.0999 | 105.402 | 122.0999
DOUN2- | GORW2- | 58.1 | 0 | OHL | 0.4621 | 3.1663 | 12.268 | 535.0006 | 494.8756 | 427.198 | 494.8756
DUBE1Q | MYBS1R | 20.8 | 0 | OHL | 2.12 | 4.86 | 1.03 | 126 | 116.55 | 100.611 | 116.55
DUDH1Q | GLAG1Q | 0 | 1.6 | Cable | 0.06 | 0.09 | 3.28 | 120 | 111 | 95.82 | 111
DUDH1Q | MILC1R | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 130.9999 | 121.1749 | 104.6034 | 121.1749
DUDH1R | GLAG1R | 0 | 1.6 | Cable | 0.06 | 0.09 | 3.28 | 120 | 111 | 95.82 | 111
DUDH1R | MILC1V | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 130.9999 | 121.1749 | 104.6034 | 121.1749
DUGR1Q | EDIN1- | 9 | 0 | OHL | 1.206 | 1.997 | 0.468 | 83 | 76.775 | 66.2755 | 76.775
DYCE1Q | KINT1- | 11.119 | 0.58099 | Composite | 0.83 | 2.65 | 1.82 | 145.0001 | 134.1251 | 115.7826 | 134.1251
DYCE1R | KINT1- | 11.119 | 0.58099 | Composite | 0.83 | 2.65 | 1.82 | 145.0001 | 134.1251 | 115.7826 | 134.1251
ELGI1Q | KEIT1- | 27.7 | 0 | OHL | 2.81 | 6.43 | 1.37 | 126 | 116.55 | 100.611 | 116.55
ELGI1Q | NAIR1Q | 35.4 | 0 | OHL | 3.6 | 8.22 | 1.75 | 126 | 116.55 | 100.611 | 116.55
ELGI1R | KEIT1- | 27.7 | 0 | OHL | 2.81 | 6.43 | 1.37 | 126 | 116.55 | 100.611 | 116.55
ELGI1R | NAIR1R | 35.4 | 0 | OHL | 3.6 | 8.22 | 1.75 | 126 | 116.55 | 100.611 | 116.55
ERRO1A | TUMM1J | 1.33 | 0 | OHL | 0.014 | 0.098 | 2.572 | 182.0001 | 168.3501 | 145.3271 | 168.3501
ERRO1B | TUMM1K | 1.3 | 0 | OHL | 0.013 | 0.095 | 2.51 | 182.0001 | 168.3501 | 145.3271 | 168.3501
ERRO1J | ERRO1A | 1 | 0 | OHL | 0 | 0.01 | 0 | 240.0005 | 222.0005 | 191.6404 | 222.0005
ERRO1J | ERRO1K | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
ERRO1J | ERRO1T | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
ERRO1J | TUMB1R | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 116.55 | 100.611 | 116.55
ERRO1K | ERRO1B | 1 | 0 | OHL | 0 | 0.01 | 0 | 240.0005 | 222.0005 | 191.6404 | 222.0005
ERRO1K | TUMB1Q | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 116.55 | 100.611 | 116.55
ERRO1T | KIIN1- | 36.9 | 0 | OHL | 3.75 | 8.58 | 1.82 | 131.9999 | 122.0999 | 105.402 | 122.0999
FASN2- | FAUG2- | 25.4 | 0 | OHL | 0.069 | 1.029 | 7.259 | 1910 | 1766.75 | 1525.135 | 1766.75
FAUG1- | FAUG1Q | 1 | 0 | OHL | 0.005 | 0.012 | 0.002 | 126 | 116.55 | 100.611 | 116.55
FAUG1- | GLDO1G | 0 | 6 | Cable | 0.21 | 0.47 | 5.91 | 127 | 117.475 | 101.4095 | 117.475
FAUG1- | LAGG1Q | 6.4 | 0 | OHL | 0.06 | 0.23 | 0.05 | 203.0001 | 187.7751 | 162.0955 | 187.7751
FAUG1- | LOCL1Q | 8.5 | 0 | OHL | 0.87 | 1.98 | 0.42 | 126 | 116.55 | 100.611 | 116.55
FAUG1- | LOCL1R | 8.5 | 0 | OHL | 0.87 | 1.98 | 0.42 | 126 | 116.55 | 100.611 | 116.55
FAUG1- | LOCL1S | 8.5 | 0 | OHL | 0.8616 | 1.9747 | 0.419 | 111 | 102.675 | 88.6335 | 102.675
FAUG1- | TUMM1T | 77.2 | 0 | OHL | 0.917 | 13.576 | 5.083 | 916.9989 | 848.224 | 732.2236 | 848.224
FAUG2- | TUMM2J | 77.2 | 0 | OHL | 0.211 | 3.128 | 22.063 | 1910 | 1766.75 | 1525.135 | 1766.75
FERO1- | FERO1S | 16.5 | 0 | OHL | 1.68 | 3.84 | 0.81 | 131.9999 | 122.0999 | 105.402 | 122.0999
FETT2P | FETT2R | 1 | 0 | OHL | 0 | 0.01 | 0 | 999.0019 | 924.0767 | 797.703 | 924.0767
FETT2Q | FETT2R | 1 | 0 | OHL | 0 | 0.01 | 0 | 999.0019 | 924.0767 | 797.703 | 924.0767
FETT2Q | KINB2J | 137.33 | 0 | OHL | 0.6853 | 5.8914 | 35.895 | 955 | 883.375 | 762.5675 | 883.375
FIDD1Q | FIDD1R | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
FIDD1Q | FOGG1R | 25.4 | 0 | OHL | 3.004 | 6.157 | 1.238 | 112 | 103.6 | 89.432 | 103.6
FIDD1R | FIDD1B | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
FINL1Q | KIIN1- | 2.1 | 0 | OHL | 0.21 | 0.5 | 0.1 | 131.9999 | 122.0999 | 105.402 | 122.0999
FOYE2- | FOYE2J | 1 | 0 | OHL | 0.004 | 0.024 | 6.22 | 399.9999 | 369.9999 | 319.3999 | 369.9999
FOYE2- | KNOC2J | 24 | 0 | OHL | 0.28 | 1.029 | 6.35 | 524.998 | 485.6232 | 419.2109 | 485.6232
FOYE2- | KNOC2K | 24 | 0 | OHL | 0.28 | 1.029 | 6.35 | 524.998 | 485.6232 | 419.2109 | 485.6232
FRAS1Q | LUMB1Q | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.502 | 133 | 123.025 | 106.2005 | 123.025
FRAS1R | LUMB1R | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.502 | 126 | 116.55 | 100.611 | 116.55
FWIL1Q | LOCL1Q | 34.9 | 0 | OHL | 3.55 | 8.11 | 1.73 | 126 | 116.55 | 100.611 | 116.55
FWIL1R | KILO1- | 22.6 | 0 | OHL | 1.75 | 5 | 1.19 | 131.9999 | 122.0999 | 105.402 | 122.0999
FWIL1R | LOCL1R | 34.9 | 0 | OHL | 3.55 | 8.11 | 1.73 | 126 | 116.55 | 100.611 | 116.55
GLDO8- | GLDO8J | 1.2 | 0 | OHL | 0.39 | 1.02 | 0.01 | 131.0001 | 121.1751 | 104.6036 | 121.1751
GLEN1Q | LAGG1Q | 5 | 0 | OHL | 0.51 | 1.2 | 0.24 | 111 | 102.675 | 88.6335 | 102.675
GORW2- | STRB2- | 10.3 | 0 | OHL | 0.0819 | 0.5613 | 2.175 | 535.0006 | 494.8756 | 427.198 | 494.8756
GRUB1Q | MOSS1S | 2.7 | 0 | OHL | 0.28 | 0.64 | 0.14 | 126 | 116.55 | 100.611 | 116.55
GRUB1R | MOSS1T | 2.7 | 0 | OHL | 0.28 | 0.64 | 0.14 | 126 | 116.55 | 100.611 | 116.55
INGA1Q | LOCL1R | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 126 | 116.55 | 100.611 | 116.55
INNE1J | INNE1K | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
INNE1J | KNOC1J | 4.57 | 0 | OHL | 0.1051 | 0.3818 | 6.326 | 171 | 158.175 | 136.5435 | 158.175
INNE1K | INNE1L | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
INNE1L | KNOC1J | 4.48 | 0 | OHL | 0.1042 | 0.3784 | 6.27 | 171 | 158.175 | 136.5435 | 158.175
INNE1Q | NAIR1Q | 27.8 | 1.5 | Composite | 2.863 | 6.6 | 3.1 | 126 | 116.55 | 100.611 | 116.55
INNE1R | INNE1T | 1 | 0 | OHL | 0 | 0.001 | 0 | 126 | 116.55 | 100.611 | 116.55
INNE1T | NAIR1R | 27.8 | 1.5 | Composite | 2.863 | 6.599 | 3.1 | 126 | 116.55 | 100.611 | 116.55
INRU1Q | PEHE1- | 6.8 | 0 | OHL | 0.69 | 1.57 | 0.33 | 150 | 138.75 | 119.775 | 138.75
INRU1Q | PEHG1Q | 1.8 | 0 | OHL | 0.18 | 0.41 | 0.09 | 126 | 116.55 | 100.611 | 116.55
INRU1Q | SFER1L | 6.1 | 0 | OHL | 0.62 | 1.42 | 0.3 | 126 | 116.55 | 100.611 | 116.55
INRU1R | PEHE1- | 6.8 | 0 | OHL | 0.69 | 1.57 | 0.33 | 126 | 116.55 | 100.611 | 116.55
INRU1R | PEHG1R | 1.8 | 0 | OHL | 0.18 | 0.41 | 0.09 | 126 | 116.55 | 100.611 | 116.55
INRU1R | SFER1M | 6.1 | 0 | OHL | 0.62 | 1.42 | 0.3 | 126 | 116.55 | 100.611 | 116.55
INRU1S | PEHE1- | 3 | 0 | OHL | 0.0687 | 0.2536 | 4.105 | 186 | 172.05 | 148.521 | 172.05
INRU1S | SFER1J | 11.3 | 0 | OHL | 0.6 | 2.379 | 0.617 | 195 | 180.375 | 155.7075 | 180.375
INVE1J | FERO1S | 15.21 | 0 | OHL | 2.157 | 3.571 | 0.744 | 99.0001 | 91.5751 | 79.0516 | 91.5751
INVE1J | INVE1K | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
INVE1J | PORA1R | 35.4 | 0 | OHL | 5.02 | 8.32 | 1.73 | 99.0001 | 91.5751 | 79.0516 | 91.5751
INVE1K | ANSU1- | 11.13 | 0 | OHL | 1.578 | 2.615 | 0.544 | 99.0001 | 91.5751 | 79.0516 | 91.5751
INVE1K | KILC1Q | 15.1 | 0 | OHL | 2.15 | 3.55 | 0.74 | 99.0001 | 91.5751 | 79.0516 | 91.5751
INVE1K | SLOY1J | 22.6 | 0 | OHL | 2.29 | 5.25 | 1.11 | 126 | 116.55 | 100.611 | 116.55
INVR1- | SLOY1T | 5.82 | 0 | OHL | 0.59 | 1.356 | 0.285 | 131.9999 | 122.0999 | 105.402 | 122.0999
KEIT1- | GLFA1- | 41.3 | 0 | OHL | 3.0087 | 6.8969 | 1.466 | 126 | 116.55 | 100.611 | 116.55
KEIT1- | MACD1Q | 37.8 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 102.675 | 88.6335 | 102.675
KEIT1- | MACD1R | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 102.675 | 88.6335 | 102.675
KEIT2Q | KEIT2R | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
KEIT2R | KINT2J | 56.2 | 0 | OHL | 0.29 | 2.44 | 14.72 | 1090.0017 | 1008.2515 | 870.3663 | 1008.2515
KEITH3A | HITO3- | 9 | 0 | OHL | 0.73 | 0.97 | 0.11 | 38.3 | 35.4275 | 30.5825 | 35.4275
KEITH3A | HITO3- | 9 | 0 | OHL | 0.73 | 0.97 | 0.11 | 38.3 | 35.4275 | 30.5825 | 35.4275
KIIN1- | INVR1- | 33.68 | 0 | OHL | 3.43 | 7.84 | 1.66 | 131.9999 | 122.0999 | 105.402 | 122.0999
KIIN1- | INVR1- | 33.68 | 0 | OHL | 3.43 | 7.84 | 1.66 | 131.9999 | 122.0999 | 105.402 | 122.0999
KIIN1- | LOCH1- | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 111 | 102.675 | 88.6335 | 102.675
KIIN1- | SFIL1Q | 21.6 | 0 | OHL | 2.19 | 5.2 | 1.03 | 131.9999 | 122.0999 | 105.402 | 122.0999
KILC1Q | NANT1Q | 4.2 | 0 | OHL | 0.59 | 1.03 | 0.19 | 99.0001 | 91.5751 | 79.0516 | 91.5751
KILC1Q | TAYN1Q | 7.6 | 0 | OHL | 1.07 | 1.78 | 0.37 | 99.0001 | 91.5751 | 79.0516 | 91.5751
KINT1- | FOGG1Q | 15.6 | 0 | OHL | 1.826 | 3.742 | 0.752 | 112 | 103.6 | 89.432 | 103.6
KINT2J | KINT2K | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
KINT2J | PERS2R | 28.2 | 0 | OHL | 0.14 | 1.23 | 7.42 | 1090.0017 | 1008.2515 | 870.3663 | 1008.2515
KINT2J | TEAL2J | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 694.9992 | 642.8743 | 554.9569 | 642.8743
KINT2K | FETT2P | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 955 | 883.375 | 762.5675 | 883.375
KINT2K | FETT2Q | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 955 | 883.375 | 762.5675 | 883.375
KINT2K | PEHE2Q | 70.5 | 0 | OHL | 0.36 | 3.07 | 18.48 | 1090.0017 | 1008.2515 | 870.3663 | 1008.2515
KINT2K | PEHE2R | 50.4 | 0 | OHL | 0.26 | 2.19 | 13.22 | 1090.0017 | 1008.2515 | 870.3663 | 1008.2515
KINT2K | TEAL2K | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 694.9992 | 642.8743 | 554.9569 | 642.8743
KNOC2J | BERB2Q | 41.79 | 0 | OHL | 0.4865 | 1.7916 | 11.047 | 524.998 | 485.6232 | 419.2109 | 485.6232
KNOC2J | KNOC2K | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
KNOC2J | KNOC2L | 1.47 | 0 | OHL | 0.0024 | 0.042 | 8.36 | 929.9983 | 860.2484 | 742.6036 | 860.2484
KNOC2K | DAAS2- | 55.4 | 0 | OHL | 0.65 | 2.375 | 14.65 | 524.998 | 485.6232 | 419.2109 | 485.6232
KNOC2M | KNOC2K | 1.29 | 0 | OHL | 0.0021 | 0.037 | 7.336 | 929.9983 | 860.2484 | 742.6036 | 860.2484
LAGG1Q | MILW1S | 5.7 | 0 | OHL | 0.58 | 1.33 | 0.28 | 111 | 102.675 | 88.6335 | 102.675
LAIR1Q | SHIN1- | 10.5 | 0 | OHL | 1.06 | 2.52 | 0.5 | 111 | 102.675 | 88.6335 | 102.675
LOCL1S | QUOI1Q | 18.3 | 0 | OHL | 1.91 | 4.54 | 0.9 | 111 | 102.675 | 88.6335 | 102.675
LUIC1Q | ORRI1S | 5.1 | 0 | OHL | 0.53 | 1.23 | 0.25 | 126 | 116.55 | 100.611 | 116.55
LUIC1R | ORRI1T | 5.1 | 0 | OHL | 0.53 | 1.23 | 0.25 | 126 | 116.55 | 100.611 | 116.55
LUMB1Q | SFER1K | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 116.55 | 100.611 | 116.55
LUMB1Q | STRI1Q | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.395 | 133 | 123.025 | 106.2005 | 123.025
LUMB1R | SFER1J | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 116.55 | 100.611 | 116.55
LUMB1R | STRI1R | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.395 | 133 | 123.025 | 106.2005 | 123.025
LUNA1Q | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 182.9999 | 169.2749 | 146.1254 | 169.2749
LUNA1R | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 182.9999 | 169.2749 | 146.1254 | 169.2749
MILC1R | MILC1S | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
MILC1R | MILC1T | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
MILC1S | MILC1V | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
MILC1S | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 182.9999 | 169.2749 | 146.1254 | 169.2749
MILC1T | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 182.9999 | 169.2749 | 146.1254 | 169.2749
MILW1S | MILW1Q | 1.3 | 0 | OHL | 0.17 | 0.29 | 0.07 | 83 | 76.775 | 66.2755 | 76.775
MOSS1Q | MOSS1S | 1 | 0 | OHL | 0 | 0.01 | 0 | 126 | 116.55 | 100.611 | 116.55
MOSS1R | MOSS1T | 1 | 0 | OHL | 0 | 0.01 | 0 | 126 | 116.55 | 100.611 | 116.55
MOTA1Q | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 131.9999 | 122.0999 | 105.402 | 122.0999
MOTA1R | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 126 | 116.55 | 100.611 | 116.55
MYBS1Q | MYBS1S | 1 | 0 | OHL | 0 | 0.01 | 0 | 998.9996 | 924.0746 | 797.7012 | 924.0746
MYBS1Q | SHIN1- | 93.8 | 0 | OHL | 9.54 | 21.84 | 4.63 | 126 | 116.55 | 100.611 | 116.55
MYBS1R | MYBS1T | 1 | 0 | OHL | 0 | 0.01 | 0 | 998.9996 | 924.0746 | 797.7012 | 924.0746
MYBS1S | THSO1Q | 16.1 | 0 | OHL | 1.64 | 3.75 | 0.79 | 126 | 116.55 | 100.611 | 116.55
MYBS1T | THSO1R | 16.1 | 0 | OHL | 1.64 | 3.75 | 0.79 | 126 | 116.55 | 100.611 | 116.55
ORRI1Q | ORRI1S | 1 | 0 | OHL | 0 | 0.01 | 0 | 126 | 116.55 | 100.611 | 116.55
ORRI1R | ORRI1T | 1 | 0 | OHL | 0 | 0.01 | 0 | 126 | 116.55 | 100.611 | 116.55
PEHE1- | PEHE1L | 1 | 0 | OHL | 0.012 | 0.056 | 0 | 219.9999 | 203.4999 | 175.6699 | 203.4999
PEHE1- | PEHE1M | 1 | 0 | OHL | 0.012 | 0.056 | 0 | 219.9999 | 203.4999 | 175.6699 | 203.4999
PEHE1- | PEHE1Q | 1 | 0 | OHL | 0.086 | 0.059 | 1.51 | 69.0001 | 63.8251 | 55.0965 | 63.8251
PEHE1- | PEHE1R | 1 | 0 | OHL | 0.08 | 0.056 | 1.41 | 69.0001 | 63.8251 | 55.0965 | 63.8251
PEHE2- | PEHE2Q | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
PEHE2- | PEHE2S | 1 | 0 | OHL | 0.002 | 0.033 | 14.21 | 776.0012 | 717.8011 | 619.637 | 717.8011
PEHE2- | PEHEMEC6 | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
PEHE2- | PERS2Q | 47.6 | 0 | OHL | 0.24 | 2.08 | 12.52 | 1090.0017 | 1008.2515 | 870.3663 | 1008.2515
PEHE2R | PEHERSV2 | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
PEHE2T | PEHERSV1 | 1 | 0 | OHL | 0.002 | 0.032 | 13.51 | 776.0012 | 717.8011 | 619.637 | 717.8011
PEHE2U | PEHEMEC5 | 1 | 0 | OHL | 0.006 | 0.021 | 5.25 | 313.0002 | 289.5252 | 249.9307 | 289.5252
PEHE2V | PEHEMEC3 | 1 | 0 | OHL | 0.006 | 0.021 | 5.25 | 313.0002 | 289.5252 | 249.9307 | 289.5252
PEHE2W | PEHEMEC1 | 1 | 0 | OHL | 0.006 | 0.021 | 5.25 | 313.0002 | 289.5252 | 249.9307 | 289.5252
PEHEMEC1 | PEHEMEC2 | 1 | 0 | OHL | 0 | 0.1 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
PEHEMEC1 | PEHEMEC6 | 1 | 0 | OHL | 0 | 0.1 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
PEHEMEC2 | PEHEMEC3 | 1 | 0 | OHL | 0 | 0.1 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
PEHEMEC3 | PEHEMEC4 | 1 | 0 | OHL | 0 | 0.1 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
PEHEMEC4 | PEHEMEC5 | 1 | 0 | OHL | 0 | 0.1 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
PEHEMEC5 | PEHEMEC6 | 1 | 0 | OHL | 0 | 0.1 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
PEHERSV1 | PEHEMEC4 | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
PEHERSV2 | PEHEMEC2 | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
PERS1Q | PERS1R | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
PERS1Q | WIOW1R | 0 | 3.7 | Cable | 0.84 | 2.21 | 51.04 | 155 | 129 | 129 | 129
PERS1R | WIOW1Q | 0 | 3.7 | Cable | 0.84 | 2.21 | 51.04 | 155 | 129 | 129 | 129
PERS2Q | PERS2R | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
PORA1Q | ANSU1- | 24.27 | 0 | OHL | 3.442 | 5.705 | 1.186 | 99.0001 | 91.5751 | 79.0516 | 91.5751
QUOI1- | QUOI1Q | 1.6 | 0 | OHL | 0.12 | 0.28 | 0.05 | 111 | 102.675 | 88.6335 | 102.675
RANN1Q | TUMB1Q | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 116.55 | 100.611 | 116.55
RANN1R | TUMB1R | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 116.55 | 100.611 | 116.55
SFEG1Q | SFEG1S | 0.4 | 0 | OHL | 0.009 | 0.034 | 0.46 | 159.9999 | 147.9999 | 127.7599 | 147.9999
SFEG1R | SFEG1T | 0.4 | 0 | OHL | 0.009 | 0.034 | 0.46 | 159.9999 | 147.9999 | 127.7599 | 147.9999
SFEG1S | SFEG1T | 1 | 0 | OHL | 0.01 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
SFER1J | SFER1M | 1 | 0 | OHL | 0 | 0.001 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
SFER1K | SFER1J | 1 | 0 | OHL | 0 | 0.001 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
SFER1K | SFER1L | 1 | 0 | OHL | 0 | 0.001 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
SFER1L | SFEG1Q | 2.1 | 0 | OHL | 0.25 | 0.49 | 0.1 | 126 | 116.55 | 100.611 | 116.55
SFER1L | SFEM1Q | 1.92 | 1.18 | Composite | 0.382 | 0.557 | 1.871 | 131.9999 | 122.0999 | 105.402 | 122.0999
SFER1L | SFER1M | 1 | 0 | OHL | 0.01 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
SFER1M | SFEG1R | 2.1 | 0 | OHL | 0.25 | 0.49 | 0.1 | 126 | 116.55 | 100.611 | 116.55
SFER1M | SFEM1R | 1.92 | 1.18 | Composite | 0.382 | 0.557 | 1.871 | 131.9999 | 122.0999 | 105.402 | 122.0999
SLOY1J | GARB1R | 14.9 | 0 | OHL | 1.44 | 3.3 | 0.7 | 131.9999 | 122.0999 | 105.402 | 122.0999
SLOY1J | GARB1S | 14.9 | 0 | OHL | 1.45 | 3.31 | 0.7 | 131.9999 | 122.0999 | 105.402 | 122.0999
SLOY1J | SLOY1K | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
SLOY1J | SLOY1N | 1.4 | 0 | OHL | 0.15 | 0.34 | 0.07 | 126 | 116.55 | 100.611 | 116.55
SLOY1J | SLOY1P | 1.4 | 0 | OHL | 0.15 | 0.34 | 0.07 | 126 | 116.55 | 100.611 | 116.55
SLOY1J | SLOY1T | 5.4 | 0 | OHL | 0.547 | 1.254 | 0.266 | 131.9999 | 122.0999 | 105.402 | 122.0999
SLOY1K | GARB1Q | 14.9 | 0 | OHL | 1.45 | 3.31 | 0.7 | 131.9999 | 122.0999 | 105.402 | 122.0999
SLOY1K | GARB1T | 14.9 | 0 | OHL | 1.44 | 3.3 | 0.7 | 131.9999 | 122.0999 | 105.402 | 122.0999
SLOY1K | INVR1- | 11.22 | 0 | OHL | 1.14 | 2.614 | 0.55 | 131.9999 | 122.0999 | 105.402 | 122.0999
SLOY1K | SLOY1L | 1.3 | 0 | OHL | 0.13 | 0.3 | 0.06 | 126 | 116.55 | 100.611 | 116.55
SLOY1K | SLOY1M | 1.3 | 0 | OHL | 0.13 | 0.3 | 0.06 | 126 | 116.55 | 100.611 | 116.55
TARL1Q | FOGG1Q | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 131.9999 | 122.0999 | 105.402 | 122.0999
TARL1R | FOGG1R | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 131.9999 | 122.0999 | 105.402 | 122.0999
TAYN1R | FERO1S | 7.49 | 0 | OHL | 1.063 | 1.759 | 0.366 | 99.0001 | 91.5751 | 79.0516 | 91.5751
TEAL1- | BIHI1Q | 5.6 | 0 | OHL | 0.239 | 1.199 | 0.29 | 229.0011 | 211.826 | 182.8574 | 211.826
TEAL1- | BIHI1R | 5.6 | 0 | OHL | 0.239 | 1.199 | 0.29 | 229.0011 | 211.826 | 182.8574 | 211.826
TEAL2J | KINB2K | 86.18 | 0 | OHL | 0.4329 | 3.735 | 23 | 955 | 883.375 | 762.5675 | 883.375
TEAL2J | TEAL2K | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
TEAL2J | WFIB2- | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 955 | 883.375 | 762.5675 | 883.375
TEAL2K | FETT2P | 83.55 | 0 | OHL | 0.4226 | 3.6513 | 21.994 | 955 | 883.375 | 762.5675 | 883.375
TEAL2K | GLRB2- | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 955 | 883.375 | 762.5675 | 883.375
TUMM1J | TUMM1T | 0.2 | 0 | OHL | 0.002 | 0.015 | 0.39 | 150 | 138.75 | 119.775 | 138.75
TUMM2J | TUMM2K | 1 | 0 | OHL | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
WHIB1A | ERRO1J | 4.87 | 0 | OHL | 0.4973 | 1.14 | 0.242 | 131.9999 | 122.0999 | 105.402 | 122.0999
WHIB1A | WHIB1C | 0 | 2.93 | Cable | 0.0962 | 0.2778 | 3.373 | 140 | 129.5 | 111.79 | 129.5
WHIB1B | ERRO1K | 4.87 | 0 | OHL | 0.4973 | 1.14 | 0.242 | 131.9999 | 122.0999 | 105.402 | 122.0999
WHIB1B | WHIB1D | 0 | 2.93 | Cable | 0.0962 | 0.2778 | 3.373 | 140 | 129.5 | 111.79 | 129.5
WHIB1C | WHIB1E | 3.57 | 0 | OHL | 0.3644 | 0.8354 | 0.177 | 131.9999 | 122.0999 | 105.402 | 122.0999
WHIB1D | WHIB1F | 3.57 | 0 | OHL | 0.3644 | 0.8354 | 0.177 | 131.9999 | 122.0999 | 105.402 | 122.0999
WHIB1E | WHIB1G | 0 | 0.44 | Cable | 2.52 | 7.26 | 0.506 | 140 | 129.5 | 111.79 | 129.5
WHIB1F | WHIB1H | 0 | 0.44 | Cable | 2.52 | 7.26 | 0.506 | 140 | 129.5 | 111.79 | 129.5
WHIB1G | GRIF1T | 14.17 | 0 | OHL | 1.4475 | 3.3186 | 0.703 | 131.9999 | 122.0999 | 105.402 | 122.0999
WHIB1H | GRIF1S | 14.17 | 0 | OHL | 1.4475 | 3.3186 | 0.703 | 131.9999 | 122.0999 | 105.402 | 122.0999
WIOW1Q | WOHI1Q | 3.4 | 0 | OHL | 0.075 | 0.29 | 3.908 | 174.0001 | 160.9501 | 138.9391 | 160.9501
WIOW1R | WOHI1R | 3.4 | 0 | OHL | 0.075 | 0.29 | 3.908 | 174.0001 | 160.9501 | 138.9391 | 160.9501

## B-2-1b
Table B.2.1b - SPT Circuits ETYS Yr1 - 2014/15 | [11 empty] | Back To Menu
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
AREC1- | MAHI1- | 7.615 | 1.613 | Composite | 0.35 | 1.349 | 2.438 | 214 | 198 | 171 | 198
AUCH2- | MAHI2- | 14.5 | 0 | OHL | 0.112 | 0.809 | 3.028 | 570 | 527 | 455 | 527
AUCW1- | HADH1- | 18 | 0 | OHL | 1.83 | 3.88 | 0.96 | 140 | 129 | 112 | 129
AUCW1- | MAYB1- | 0 | 0.07 | Cable | 0 | 0.009 | 0.0682 | 169 | 156 | 135 | 156
AYR-2Q | COYW2S | 9.37 | 0 | OHL | 0.047 | 0.384 | 2.605 | 955 | 883 | 763 | 883
AYR-2R | COYW2T | 9.37 | 0 | OHL | 0.047 | 0.384 | 2.605 | 955 | 883 | 763 | 883
BAGA1Q | BONN1- | 18.3 | 0 | OHL | 0.791 | 3.901 | 0.994 | 146 | 135 | 117 | 135
BAGA1Q | DRCR1Q | 4.71 | 3.39 | Composite | 0.556 | 1.429 | 10.5 | 146 | 135 | 117 | 135
BAGA1R | BONN1- | 18.4 | 0 | OHL | 1.184 | 3.906 | 0.95 | 146 | 135 | 117 | 135
BAGA1R | DRCR1R | 4.71 | 3.38 | Composite | 0.556 | 1.429 | 10.5 | 146 | 135 | 117 | 135
BAIN1- | BONN1- | 7.02 | 0.28 | Composite | 0.307 | 1.508 | 1.304 | 114 | 105 | 91 | 105
BAIN1- | BONN1- | 7.02 | 0.08 | Composite | 0.303 | 1.491 | 0.644 | 114 | 105 | 91 | 105
BERW1Q | ECCL1- | 21.54 | 0.31 | Composite | 2.183 | 4.862 | 1.635 | 132 | 122 | 105 | 122
BERW1R | ECCL1- | 21.54 | 0.27 | Composite | 2.182 | 4.86 | 1.543 | 132 | 122 | 105 | 122
BLKL1- | WISH1- | 11.46 | 0 | OHL | 0.7 | 1.917 | 0.355 | 161 | 149 | 129 | 149
BONB1J | BONN1- | 21.45 | 0 | OHL | 2.19 | 5.01 | 1.07 | 120 | 111 | 96 | 111
BONB1K | BONN1- | 21.58 | 0 | OHL | 2.18 | 4.97 | 1.06 | 120 | 111 | 96 | 111
BONN1- | CUMB1Q | 10.89 | 0 | OHL | 0.47 | 2.318 | 0.591 | 135 | 125 | 108 | 125
BONN1- | CUMB1R | 10.89 | 0 | OHL | 0.842 | 1.852 | 0.515 | 135 | 125 | 108 | 125
BONN1- | STIR1Q | 12.37 | 0 | OHL | 0.464 | 2.587 | 0.658 | 183 | 169 | 146 | 169
BONN1- | STIR1R | 12.17 | 0.17 | Composite | 0.464 | 2.587 | 0.658 | 183 | 169 | 146 | 169
BONN2A | DENN2- | 4 | 0 | OHL | 0.0182 | 0.182 | 1.018 | 955 | 883 | 763 | 883
BONN2B | DENN2- | 4 | 0 | OHL | 0.0182 | 0.182 | 1.018 | 955 | 883 | 763 | 883
BRAE1G | BRAP1- | 2.5 | 0 | OHL | 0.034 | 0.256 | 3.909 | 250 | 231 | 200 | 231
BRAE1G | GOVA1R | 0 | 3.5 | Cable | 0.152 | 0.239 | 6.934 | 125 | 116 | 100 | 116
BRAE1P | GOVA1Q | 0 | 3.5 | Cable | 0.152 | 0.239 | 6.934 | 125 | 116 | 100 | 116
BRAE1P | PAIS1Q | 4.52 | 0 | OHL | 0.092 | 0.745 | 1.162 | 268 | 248 | 214 | 248
BRAP1- | ERSK1Q | 4.97 | 4.58 | Composite | 0.677 | 1.419 | 14.361 | 121 | 112 | 97 | 112
BRAP1- | ERSK1R | 3.39 | 6.42 | Composite | 0.762 | 1.46 | 7.938 | 102 | 94 | 81 | 94
BRAP1- | PAIS1R | 7.02 | 0 | OHL | 0.127 | 0.986 | 5.558 | 274 | 253 | 219 | 253
BROX1Q | CURR1- | 10.34 | 0 | OHL | 1.072 | 2.387 | 0.541 | 132 | 122 | 105 | 122
BROX1R | CURR1- | 10.34 | 0 | OHL | 1.072 | 2.387 | 0.541 | 132 | 122 | 105 | 122
BUSB2- | GIFF2Q | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 255 | 220 | 255
BUSB2- | GIFF2R | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 255 | 220 | 255
BUSB2- | NEIL2- | 20.03 | 0 | OHL | 0.1 | 0.82 | 5.56 | 1090 | 1008 | 870 | 1008
BUSB2- | STHA2A | 14.99 | 0 | OHL | 0.078 | 0.642 | 4.351 | 750 | 694 | 599 | 694
CAFA1Q | KEOO1- | 2.58 | 0 | OHL | 0.258 | 0.584 | 0.126 | 132 | 122 | 105 | 122
CATY1Q | DALM1- | 3.5 | 0 | OHL | 0.098 | 0.245 | 4.119 | 95 | 88 | 76 | 88
CATY1R | DALM1- | 3.5 | 0 | OHL | 0.098 | 0.245 | 4.119 | 95 | 88 | 76 | 88
CHAP1- | DUMF1- | 26.9 | 0 | OHL | 1.156 | 5.698 | 1.451 | 171 | 158 | 137 | 158
CHAP1- | DUMF1- | 26.9 | 0.17 | Composite | 1.16 | 5.712 | 2.014 | 171 | 158 | 137 | 158
CHAP1- | ECCF1J | 6.57 | 0.18 | Composite | 0.671 | 1.486 | 0.601 | 72 | 67 | 57 | 67
CHAP1- | ECCF1K | 6.57 | 0.13 | Composite | 0.675 | 1.49 | 0.721 | 72 | 67 | 57 | 67
CHAP1- | GRNA1- | 12.83 | 0.35 | Composite | 1.313 | 2.925 | 0.663 | 132 | 122 | 105 | 122
CHAP1- | GRNA1- | 12.83 | 0.35 | Composite | 1.313 | 2.925 | 0.663 | 132 | 122 | 105 | 122
CHAP1- | HAKB1- | 14.72 | 0 | OHL | 1.535 | 3.472 | 0.754 | 132 | 122 | 105 | 122
CHAS2Q | DALM2Q | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 172 | 149 | 172
CHAS2R | DALM2R | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 172 | 149 | 172
CLYM2- | DALM2Q | 4.21 | 0 | OHL | 0.022 | 0.184 | 1.245 | 750 | 694 | 599 | 694
CLYM2- | DALM2R | 4.21 | 0.1 | Composite | 0.023 | 0.186 | 1.916 | 695 | 643 | 555 | 643
CLYM2- | EERH2- | 9.17 | 0 | OHL | 0.024 | 0.321 | 2.887 | 1500 | 1387 | 1198 | 1387
CLYM2- | EKIL2Q | 5.62 | 0 | OHL | 0.026 | 0.219 | 1.386 | 1120 | 1036 | 894 | 1036
CLYM2- | EKIL2R | 5.62 | 0 | OHL | 0.026 | 0.219 | 1.386 | 1120 | 1036 | 894 | 1036
CLYM2- | LOAN2- | 54.69 | 0 | OHL | 0.137 | 1.917 | 17.578 | 1500 | 1387 | 1198 | 1387
CLYN2Q | ELVA2Q | 6.2 | 0 | OHL | 0.032 | 0.174 | 26.956 | 476 | 440 | 380 | 440
CLYS2R | ELVA2R | 7.17 | 0 | OHL | 0.058 | 0.079 | 24.356 | 291 | 269 | 232 | 269
COAL1- | LINM1Q | 5.77 | 3.2 | Composite | 0.246 | 1.521 | 3.108 | 134 | 124 | 107 | 124
COAL1- | LINM1R | 5.77 | 3.14 | Composite | 0.244 | 1.516 | 3.055 | 134 | 124 | 107 | 124
COAL4- | ELVA4- | 26.71 | 0 | OHL | 0.047 | 0.508 | 15.991 | 2210 | 2044 | 1765 | 2044
COAL4- | STHA4- | 21.73 | 0 | OHL | 0.038 | 0.413 | 13.017 | 2210 | 2044 | 1765 | 2044
COAT2Q | NEAR2Q | 3.4 | 4.9 | Composite | 0.047 | 0.26 | 16.299 | 176 | 163 | 141 | 163
COAT2R | NEAR2R | 3.4 | 4.9 | Composite | 0.047 | 0.26 | 16.299 | 176 | 163 | 141 | 163
COCK2- | KAIM2- | 18.29 | 0 | OHL | 0.092 | 0.756 | 5.119 | 1090 | 1008 | 870 | 1008
COCK2- | SMEA2- | 9.51 | 0 | OHL | 0.048 | 0.396 | 2.683 | 1090 | 1008 | 870 | 1008
COCK4Q | ECCL4- | 65.9 | 0 | OHL | 0.156 | 1.313 | 36.4 | 1090 | 1008 | 870 | 1008
COCK4R | ECCL4- | 65.89 | 0 | OHL | 0.156 | 1.313 | 36.4 | 1090 | 1008 | 870 | 1008
COYL1- | COYT1T | 4.37 | 0.27 | Composite | 0.466 | 1.037 | 0.235 | 113 | 105 | 90 | 105
COYL1- | MAYT1T | 9.19 | 0.57 | Composite | 0.978 | 2.179 | 0.494 | 114 | 105 | 91 | 105
COYL2- | COYW2S | 1.34 | 0 | OHL | 0.008 | 0.062 | 0.417 | 710 | 657 | 567 | 657
COYL2- | COYW2T | 1.32 | 0 | OHL | 0.008 | 0.062 | 0.417 | 955 | 883 | 763 | 883
COYL2- | MAHI2- | 49.5 | 0 | OHL | 0.381 | 2.762 | 10.335 | 690 | 638 | 551 | 638
COYT1T | KILS1- | 18 | 0 | OHL | 1.517 | 3.994 | 0.924 | 132 | 122 | 105 | 122
COYT1T | MAYB1- | 17.98 | 0 | OHL | 1.82 | 4.072 | 0.912 | 132 | 122 | 105 | 122
COYW2S | KILS2- | 13.37 | 0 | OHL | 0.068 | 0.561 | 3.8 | 955 | 883 | 763 | 883
COYW2T | KILS2- | 13.37 | 0 | OHL | 0.068 | 0.561 | 3.8 | 955 | 883 | 763 | 883
CROO1Q | NEIL1- | 12.78 | 0 | OHL | 0.544 | 2.682 | 0.683 | 229 | 212 | 183 | 212
CROO1R | NEIL1- | 12.56 | 0.22 | Composite | 0.544 | 2.682 | 0.683 | 229 | 212 | 183 | 212
CRUA2Q | DALL2- | 8.1572 | 0.40282 | Composite | 0.04 | 0.36 | 4.14 | 283 | 262 | 226 | 262
CRUA2R | DALL2- | 8.1572 | 0.40282 | Composite | 0.04 | 0.36 | 4.14 | 283 | 262 | 226 | 262
CRYR4- | FALL4- | 13.86 | 0 | OHL | 0.019 | 0.249 | 8.291 | 1250 | 1156 | 998 | 1156
CRYR4- | TORN4- | 9.36 | 1.97 | Composite | 0.012 | 0.194 | 50.549 | 935 | 865 | 747 | 865
CUPA1Q | LEVT1Q | 13.27 | 0 | OHL | 1.337 | 2.979 | 0.675 | 143 | 132 | 114 | 132
CUPA1R | LEVT1R | 13.27 | 0 | OHL | 1.337 | 2.979 | 0.675 | 143 | 132 | 114 | 132
CURR1- | GORG1Q | 2.52 | 4.7 | Composite | 0.266 | 0.926 | 9.204 | 111 | 103 | 89 | 103
CURR1- | GORG1R | 2.52 | 4.68 | Composite | 0.266 | 0.926 | 9.204 | 111 | 103 | 89 | 103
CURR1- | LING1Q | 10.9195 | 1.1805 | Composite | 1.179 | 2.57 | 2.961 | 132 | 122 | 105 | 122
CURR1- | LING1R | 11.13 | 1.1 | Composite | 1.179 | 2.57 | 2.961 | 132 | 122 | 105 | 122
CURR2- | GRMO2- | 42.18 | 0 | OHL | 0.211 | 1.731 | 11.739 | 1090 | 1008 | 870 | 1008
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.046 | 0.373 | 2.527 | 1090 | 1008 | 870 | 1008
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.046 | 0.373 | 2.527 | 1090 | 1008 | 870 | 1008
CURR2- | KINC2- | 55.82 | 0 | OHL | 0.277 | 2.269 | 15.382 | 1090 | 1008 | 870 | 1008
CURR2- | SIGH2Q | 1.54 | 1.7 | Composite | 0.017 | 0.084 | 10.273 | 120 | 111 | 96 | 111
CURR2- | SIGH2R | 1.54 | 1.67 | Composite | 0.017 | 0.084 | 10.273 | 120 | 111 | 96 | 111
DALL2- | INVR2- | 22.55 | 0 | OHL | 0.102 | 0.925 | 6.198 | 570 | 527 | 455 | 527
DALL2- | WIYH2- | 79.15 | 0 | OHL | 0.358 | 3.247 | 21.756 | 570 | 527 | 455 | 527
DALM1- | SANX1Q | 0 | 4.3 | Cable | 0.098 | 0.287 | 4.943 | 224 | 207 | 179 | 207
DALM1- | SANX1R | 0 | 5.9 | Cable | 0.167 | 0.295 | 7.751 | 155 | 143 | 124 | 143
DENN2- | LAMB2- | 32.18 | 0 | OHL | 0.1468 | 1.4204 | 8.4153 | 955 | 883 | 763 | 883
DENN2- | LOAN2- | 21.35 | 0 | OHL | 0.049 | 0.8363 | 6.3429 | 1910 | 1767 | 1525 | 1767
DENN2R | LAMB2T | 32.18 | 0 | OHL | 0.1468 | 1.4204 | 8.4153 | 955 | 883 | 763 | 883
DENN2R | LOAN2- | 21.35 | 0 | OHL | 0.049 | 0.8363 | 6.3429 | 1910 | 1767 | 1525 | 1767
DEVM1- | ERSK1Q | 16.5 | 0 | OHL | 1.767 | 3.937 | 0.893 | 132 | 122 | 105 | 122
DEVM1- | SPAV1Q | 7.51 | 0.12 | Composite | 0.76 | 1.692 | 0.384 | 107 | 99 | 85 | 99
DEVM1- | SPAV1R | 7.52 | 0 | OHL | 0.76 | 1.692 | 0.384 | 107 | 99 | 85 | 99
DEVM4- | WIYH4Q | 28.895 | 2e-06 | Composite | 0.0469 | 0.5745 | 17.0811 | 1000 | 925 | 798 | 925
DEVO1- | STIR1Q | 8.88 | 0 | OHL | 0.382 | 2.131 | 0.542 | 221 | 204 | 176 | 204
DEVO1- | WFIE1B | 31.8 | 0 | OHL | 3.212 | 7.155 | 1.622 | 162 | 150 | 129 | 150
DEWP2Q | WHHO2Q | 0 | 2.4 | Cable | 0.0154 | 0.0541 | 7.5038 | 276 | 256 | 221 | 256
DEWP2R | WHHO2R | 0 | 2.55 | Cable | 0.0164 | 0.0575 | 7.9728 | 276 | 256 | 221 | 256
DRUM2Q | WIYH2- | 2.46 | 0.29 | Composite | 0.012 | 0.106 | 3.877 | 120 | 111 | 96 | 111
DRUM2R | WIYH2- | 2.46 | 0 | OHL | 0.012 | 0.098 | 0.667 | 120 | 111 | 96 | 111
DUMF1- | TONG1Q | 43.58 | 0 | OHL | 4.447 | 10.71 | 2.18 | 132 | 122 | 105 | 122
DUNB1Q | INWI1Q | 7.94 | 3.66 | Composite | 0.919 | 1.97 | 7.885 | 110 | 102 | 88 | 102
DUNB1R | INWI1R | 7.94 | 3.66 | Composite | 0.919 | 1.97 | 7.885 | 110 | 102 | 88 | 102
DUNE1- | GALA1- | 23.64 | 0 | OHL | 1.397 | 5.514 | 1.171 | 152 | 141 | 121 | 141
DUNE1- | SMEA1- | 17.8254 | 0.53 | Composite | 1.065 | 4.207 | 1.527 | 152 | 141 | 121 | 141
DUNF1Q | INKE1Q | 7.58 | 0.09 | Composite | 0.776 | 1.726 | 0.574 | 132 | 122 | 105 | 122
DUNF1Q | MOSM1- | 10.46 | 0 | OHL | 0.579 | 2.408 | 0.58 | 215 | 199 | 172 | 199
DUNF1R | INKE1R | 7.58 | 0.09 | Composite | 0.776 | 1.726 | 0.574 | 132 | 122 | 105 | 122
DUNF1R | MOSM1- | 10.46 | 0 | OHL | 0.579 | 2.408 | 0.58 | 215 | 199 | 172 | 199
DUNO1Q | WHTB1S | 18.1 | 0 | OHL | 2.45 | 4.05 | 0.85 | 99 | 92 | 79 | 92
DUNO1R | WHTB1T | 18.1 | 0 | OHL | 2.45 | 4.05 | 0.85 | 99 | 92 | 79 | 92
EAST1Q | GLLE1- | 1.69 | 0 | OHL | 0.172 | 0.39 | 0.084 | 132 | 122 | 105 | 122
ECCL1- | GALA1- | 30.56 | 0.24 | Composite | 3.121 | 7.037 | 1.843 | 132 | 122 | 105 | 122
ECCL1- | GALA1- | 31 | 0.15 | Composite | 3.075 | 6.943 | 1.956 | 132 | 122 | 105 | 122
ECCL4- | STWB4Q | 7.39 | 0 | OHL | 0.006 | 0.121 | 5.111 | 2770 | 2562 | 2212 | 2562
ECCL4- | STWB4R | 7.39 | 0 | OHL | 0.006 | 0.121 | 5.111 | 2770 | 2562 | 2212 | 2562
ECCL4- | TORN4- | 34.2 | 1.99 | Composite | 0.05 | 0.653 | 64.3609 | 945 | 874 | 755 | 874
ECCL4- | TORN4- | 34.2 | 1.99 | Composite | 0.05 | 0.653 | 64.3609 | 945 | 874 | 755 | 874
EERH2- | LOAN2- | 46.43 | 0 | OHL | 0.118 | 1.637 | 14.957 | 1500 | 1387 | 1198 | 1387
EERH2- | NEAR2Q | 15.34 | 0 | OHL | 0.077 | 0.632 | 4.283 | 950 | 879 | 759 | 879
EKIL2Q | EKIL2S | 5.17 | 0 | OHL | 0.035 | 0.3 | 1.374 | 865 | 800 | 691 | 800
EKIL2Q | STHA2A | 4.79 | 0 | OHL | 0.026 | 0.219 | 1.386 | 1050 | 971 | 838 | 971
EKIL2R | EKIL2T | 5.17 | 0.1 | Composite | 0.035 | 0.3 | 1.374 | 480 | 444 | 383 | 444
EKIL2R | STHA2B | 4.79 | 0 | OHL | 0.026 | 0.219 | 1.386 | 1050 | 971 | 838 | 971
EKIS2- | NEIL2- | 29.32 | 0 | OHL | 0.145 | 1.192 | 8.084 | 1090 | 1008 | 870 | 1008
EKIS2- | STHA2B | 5.58 | 0 | OHL | 0.032 | 0.26 | 1.764 | 955 | 883 | 763 | 883
EKIS2- | WLEE2- | 0 | 6 | Cable | 0.034 | 0.101 | 25.635 | 378 | 350 | 302 | 350
EKIS2- | WLEX2- | 16.68 | 0 | OHL | 0.088 | 0.346 | 70.948 | 340 | 315 | 271 | 315
ELDE1Q | JOHN1Q | 2.55 | 0.24 | Composite | 0.12 | 0.559 | 0.684 | 229 | 212 | 183 | 212
ELDE1Q | NEIL1- | 3.82 | 0.18 | Composite | 0.166 | 0.816 | 0.208 | 229 | 212 | 183 | 212
ELDE1R | JOHN1R | 2.55 | 0.24 | Composite | 0.121 | 0.561 | 0.73 | 229 | 212 | 183 | 212
ELDE1R | NEIL1- | 3.82 | 0.23 | Composite | 0.166 | 0.816 | 0.208 | 229 | 212 | 183 | 212
ELVA4- | GRNA4- | 65.54 | 0 | OHL | 0.114 | 1.245 | 39.2409 | 2210 | 2044 | 1765 | 2044
ELVA4- | MOFF4- | 23.5 | 0 | OHL | 0.041 | 0.446 | 14.069 | 2210 | 2044 | 1765 | 2044
ELVA4- | STHA4- | 48.56 | 0 | OHL | 0.084 | 0.923 | 29.071 | 2210 | 2044 | 1765 | 2044
ESST1- | PART1Q | 0 | 6.9 | Cable | 0.137 | 0.641 | 9.143 | 210 | 194 | 168 | 194
ESST1- | WIYH1- | 2.09 | 1.38 | Composite | 0.131 | 0.187 | 8.407 | 128 | 118 | 102 | 118
ESST1Q | PART1R | 0 | 6.84 | Cable | 0.136 | 0.635 | 9.062 | 203 | 188 | 162 | 188
ESST1Q | WIYH1- | 0 | 3.16 | Cable | 0.178 | 0.334 | 7.691 | 203 | 188 | 162 | 188
ESST1R | KIER1R | 0 | 4.56 | Cable | 0.133 | 0.19 | 8.531 | 100 | 93 | 80 | 93
ESST1R | WIYH1- | 0 | 3.59 | Cable | 0.071 | 0.299 | 5.168 | 233 | 216 | 186 | 216
FALL4- | SMEA4R | 31.1 | 0 | OHL | 0.043 | 0.558 | 18.603 | 1250 | 1156 | 998 | 1156
FIFE1A | WFIE1A | 0 | 0.69 | Cable | 0.031 | 0.498 | 1.935 | 130 | 120 | 104 | 120
FIFE1B | WFIE1B | 0 | 0.69 | Cable | 0.031 | 0.498 | 1.935 | 130 | 120 | 104 | 120
FINN1Q | PART1Q | 0 | 2.95 | Cable | 0.274 | 0.429 | 1.905 | 100 | 93 | 80 | 93
FINN1R | PART1R | 0 | 2.95 | Cable | 0.274 | 0.429 | 1.905 | 100 | 93 | 80 | 93
GALA1- | HAWI1B | 23.55 | 0 | OHL | 1.211 | 2.684 | 7.57 | 132 | 122 | 105 | 122
GARB1Q | HELE1- | 15.1 | 0 | OHL | 1.54 | 3.52 | 0.75 | 132 | 122 | 105 | 122
GARB1R | STLE1- | 27.37 | 0 | OHL | 2.77 | 6.33 | 1.34 | 132 | 122 | 105 | 122
GARB1S | GARE1S | 4.92 | 0 | OHL | 0.5 | 1.15 | 0.24 | 132 | 122 | 105 | 122
GARB1T | GARE1T | 5.22 | 0 | OHL | 0.51 | 1.17 | 0.25 | 132 | 122 | 105 | 122
GARE1S | WHTL1S | 1.68 | 0 | OHL | 0.18 | 0.4 | 0.08 | 100 | 93 | 80 | 93
GARE1S | WIYH1- | 35.5 | 0.41 | Composite | 3.574 | 7.946 | 2.476 | 109 | 101 | 87 | 101
GARE1T | WHTL1T | 1.67 | 0 | OHL | 0.17 | 0.4 | 0.08 | 100 | 93 | 80 | 93
GARE1T | WIYH1- | 35.51 | 0 | OHL | 3.596 | 7.94 | 2.306 | 109 | 101 | 87 | 101
GLLE1- | KEOO1- | 7.68 | 0 | OHL | 0.746 | 1.655 | 0.376 | 132 | 122 | 105 | 122
GLLE1- | NETS1- | 30.04 | 0 | OHL | 3.034 | 6.759 | 1.532 | 125 | 116 | 100 | 116
GLLE1- | NETS1- | 30.04 | 0 | OHL | 3.035 | 6.767 | 1.759 | 125 | 116 | 100 | 116
GLLE1- | TONG1- | 33.1 | 0 | OHL | 3.39 | 7.678 | 1.662 | 132 | 122 | 105 | 122
GLLU1Q | NETS1- | 22 | 0 | OHL | 2.227 | 4.961 | 1.125 | 49 | 45 | 39 | 45
GLLU1R | NETS1- | 22 | 0 | OHL | 2.186 | 4.849 | 1.082 | 49 | 45 | 39 | 45
GLNI1- | MOSM1- | 1.41 | 0.09 | Composite | 0.074 | 0.243 | 0.716 | 171 | 158 | 137 | 158
GLNI1- | MOSM1- | 1.41 | 0.11 | Composite | 0.078 | 0.328 | 0.647 | 130 | 120 | 104 | 120
GLNI1- | REDH1- | 10.27 | 0 | OHL | 1.014 | 2.259 | 0.512 | 157 | 145 | 125 | 145
GLNI1- | WFIE1B | 7.07 | 0 | OHL | 0.718 | 1.6 | 0.363 | 132 | 122 | 105 | 122
GLNI1- | WFIE1B | 7.07 | 0 | OHL | 0.718 | 1.6 | 0.363 | 132 | 122 | 105 | 122
GLRB2- | GLRO2- | 14.53 | 0 | OHL | 0.06 | 0.53 | 3.37 | 955 | 883 | 763 | 883
GLRO2- | WFIE2- | 11.92 | 0 | OHL | 0.061 | 0.496 | 3.311 | 955 | 883 | 763 | 883
GORG1Q | TELR1Q | 0 | 3.74 | Cable | 0.395 | 0.271 | 6.4 | 80 | 74 | 64 | 74
GORG1R | TELR1R | 0 | 3.72 | Cable | 0.395 | 0.271 | 6.4 | 80 | 74 | 64 | 74
GOVA1Q | HAGR1Q | 0 | 4.2 | Cable | 0.218 | 0.262 | 6.322 | 70 | 65 | 56 | 65
GOVA1R | HAGR1R | 0 | 4.11 | Cable | 0.187 | 0.225 | 3.587 | 69 | 64 | 55 | 64
GRMO2- | KINC2- | 14.96 | 0 | OHL | 0.072 | 0.591 | 4.01 | 1050 | 971 | 838 | 971
GRNA1- | HAWI1- | 55.35 | 0 | OHL | 5.574 | 12.417 | 2.815 | 132 | 122 | 105 | 122
GRNA1- | JUNV1- | 4.74 | 0 | OHL | 0.51 | 1.136 | 0.258 | 132 | 122 | 105 | 122
GRNA4- | HAKB4B | 1.97 | 0 | OHL | 0.003 | 0.037 | 1.177 | 2210 | 2044 | 1765 | 2044
HAKB4- | MOFF4- | 43.79 | 0 | OHL | 0.076 | 0.832 | 26.218 | 2210 | 2044 | 1765 | 2044
HARE1- | MOFF1- | 15.33 | 0 | OHL | 0.304 | 1.375 | 21.563 | 223 | 206 | 178 | 206
HAWI1- | JUNV1- | 50.34 | 0 | OHL | 5.034 | 11.252 | 3.182 | 132 | 122 | 105 | 122
HELE1- | WIYH1- | 24.71 | 0.44 | Composite | 2.545 | 5.65 | 2.089 | 109 | 101 | 87 | 101
HUER1- | HUNF1Q | 0 | 0.18 | Cable | 0.003 | 0.016 | 0.396 | 146 | 135 | 117 | 135
HUER1- | HUNF1R | 0 | 0.1 | Cable | 0.003 | 0.016 | 0.264 | 146 | 135 | 117 | 135
HUER1- | JUNA1T | 0 | 3.62 | Cable | 0.052 | 0.365 | 12.94 | 175 | 162 | 140 | 162
HUER4- | DEVM4- | 50.628 | 2e-06 | Composite | 0.0897 | 1.031 | 29.1026 | 1390 | 1286 | 1110 | 1286
HUER4- | KILS4- | 59.125 | 2e-06 | Composite | 0.0836 | 1.1482 | 35.509 | 2030 | 1878 | 1621 | 1878
HUER4- | STHA4- | 94.113 | 2e-06 | Composite | 0.153 | 1.8835 | 54.821 | 2000 | 1850 | 1597 | 1850
HUNF1Q | KILW1R | 12.85 | 3.06 | Composite | 0.624 | 2.926 | 7.806 | 146 | 135 | 117 | 135
HUNF1R | SACO1R | 8.5613 | 3.0487 | Composite | 0.459 | 2.11 | 7.598 | 146 | 135 | 117 | 135
INVB2A | INVR2- | 1 | 0 | OHL | 0 | 0.011 | 0 | 1000 | 925 | 799 | 925
INVB2B | INVR2- | 1 | 0 | OHL | 0 | 0.011 | 0 | 1000 | 925 | 799 | 925
INVR2- | WIYH2- | 55.6 | 0 | OHL | 0.256 | 2.322 | 15.557 | 570 | 527 | 455 | 527
INWI1Q | TORN1- | 0 | 1.15 | Cable | 0.038 | 0.061 | 2.365 | 110 | 102 | 88 | 102
INWI1R | TORN1- | 0 | 1.12 | Cable | 0.038 | 0.061 | 2.365 | 110 | 102 | 88 | 102
JUNA1T | KILW1Q | 12.4 | 0 | OHL | 0.533 | 2.629 | 0.67 | 146 | 135 | 117 | 135
JUNA1T | SACO1Q | 8.14 | 0 | OHL | 0.368 | 1.813 | 0.462 | 151 | 140 | 121 | 140
KAIM2- | SMEA2- | 8.64 | 0 | OHL | 0.044 | 0.36 | 2.436 | 1090 | 1008 | 870 | 1008
KAIM2- | WHHO2Q | 0 | 6.45 | Cable | 0.0415 | 0.1455 | 20.1665 | 276 | 256 | 221 | 256
KAIM2- | WHHO2R | 1.42 | 4.8 | Composite | 0.04 | 0.1403 | 19.4474 | 276 | 256 | 221 | 256
KEOO1- | MAYT1T | 34.23 | 0 | OHL | 3.457 | 7.702 | 1.746 | 114 | 105 | 91 | 105
KIER1Q | WIYH1- | 2.09 | 4.18 | Composite | 0.334 | 0.647 | 8.017 | 100 | 93 | 80 | 93
KILB1Q | WIYH1- | 0 | 3.38 | Cable | 0.098 | 0.209 | 4.333 | 139 | 129 | 111 | 129
KILB1R | WIYH1- | 0 | 3.29 | Cable | 0.115 | 0.199 | 8.02 | 139 | 129 | 111 | 129
KILS1- | MEAD1B | 11.4 | 1.18 | Composite | 0.874 | 2.581 | 2.166 | 162 | 150 | 129 | 150
KILS2- | KILT2Q | 3.56 | 0.45 | Composite | 0.022 | 0.156 | 3.875 | 280 | 259 | 224 | 259
KILS2- | KILT2R | 3.56 | 0.45 | Composite | 0.022 | 0.156 | 3.875 | 280 | 259 | 224 | 259
KILS4- | STHA4- | 34.948 | 2e-06 | Composite | 0.0694 | 0.7346 | 19.2897 | 2000 | 1850 | 1597 | 1850
KILW1Q | MEAD1- | 13.8 | 0 | OHL | 0.736 | 3.039 | 0.743 | 146 | 135 | 117 | 135
KILW1R | MEAD1- | 13.8 | 0 | OHL | 0.736 | 3.039 | 0.743 | 146 | 135 | 117 | 135
KINB2J | KINC2- | 10.57 | 0 | OHL | 0.05 | 0.43 | 7.18 | 760 | 703 | 607 | 703
KINB2K | KINC2- | 10.22 | 0.35 | Composite | 0.05 | 0.43 | 2.93 | 910 | 842 | 727 | 842
KINC2- | LOAN2Q | 4.28 | 0.31 | Composite | 0.022 | 0.189 | 6.1 | 760 | 703 | 607 | 703
KINC2- | LOAN2R | 4.28 | 0.17 | Composite | 0.022 | 0.185 | 4.465 | 620 | 573 | 495 | 573
LAMB2- | LAMB2T | 0 | 1 | Cable | 0 | 0.011 | 0 | 1120 | 1036 | 894 | 1036
LAMB2- | PORD2Q | 3.94 | 0 | OHL | 0.02 | 0.162 | 1.097 | 955 | 883 | 763 | 883
LAMB2- | PORD2R | 3.94 | 0.18 | Composite | 0.021 | 0.164 | 2.199 | 300 | 278 | 240 | 278
LAMB2- | WIYH2- | 17.88 | 0 | OHL | 0.09 | 0.738 | 5.002 | 955 | 883 | 763 | 883
LAMB2T | WIYH2- | 17.88 | 0 | OHL | 0.09 | 0.738 | 5.002 | 950 | 879 | 759 | 879
LEVE1Q | LEVT1Q | 2.16 | 0 | OHL | 0.218 | 0.486 | 0.11 | 143 | 132 | 114 | 132
LEVE1R | LEVT1R | 2.16 | 0.1 | Composite | 0.223 | 0.496 | 0.25 | 143 | 132 | 114 | 132
LEVT1Q | REDH1- | 8.61 | 0 | OHL | 0.896 | 1.995 | 0.452 | 143 | 132 | 114 | 132
LEVT1R | WFIE1B | 18.8 | 0 | OHL | 1.866 | 4.157 | 0.942 | 143 | 132 | 114 | 132
LOAN2- | LOAN2Q | -- | -- | -- | 0.0047 | 1.9355 | 0 | 620 | 574 | 495 | 574
LOAN2- | LOAN2R | -- | -- | -- | 0.0047 | 1.9355 | 0 | 620 | 574 | 495 | 574
LOAN2- | MOSM2L | 26.39 | 0 | OHL | 0.132 | 1.078 | 9.002 | 760 | 703 | 607 | 703
LOAN2- | WFIE2- | 29.01 | 0.15 | Composite | 0.147 | 1.2 | 9.431 | 760 | 703 | 607 | 703
MAYB1- | MAYT1T | 12.61 | 0.31 | Composite | 1.3 | 2.896 | 0.656 | 132 | 122 | 105 | 122
MEAD1- | MEAD1B | 1 | 0 | OHL | 0 | 0.011 | 0 | 100 | 93 | 80 | 93
MEAD1- | MEAD1Q | 1 | 0 | OHL | 0.023 | 0.032 | 0.314 | 100 | 93 | 80 | 93
MEAD1- | MEAD1R | 1 | 0 | OHL | 0.023 | 0.032 | 0.314 | 100 | 93 | 80 | 93
MOSH1Q | MOSM1- | 0 | 1.03 | Cable | 0.048 | 0.063 | 2.012 | 132 | 122 | 105 | 122
MOSH1R | MOSM1- | 0 | 0.96 | Cable | 0.044 | 0.057 | 1.826 | 132 | 122 | 105 | 122
MOSM2L | MOSM2Q | 5.3 | 0 | OHL | 0.027 | 0.217 | 1.447 | 955 | 883 | 763 | 883
MOSM2Q | MOSM2T | 5.3 | 0 | OHL | 0.027 | 0.217 | 1.447 | 955 | 883 | 763 | 883
MOSM2T | WFIE2- | 3 | 0 | OHL | 0.015 | 0.123 | 0.819 | 955 | 883 | 763 | 883
NEAR2Q | WISH2- | 16.1 | 0 | OHL | 0.079 | 0.646 | 4.38 | 955 | 883 | 763 | 883
NEAR2R | WISH2- | 16.1 | 0 | OHL | 0.079 | 0.646 | 4.38 | 285 | 264 | 228 | 264
NEIL1- | NEIL1C | 0 | 0.28 | Cable | 0 | 0.011 | 0 | 334 | 309 | 267 | 309
NEIL1- | PAIS1Q | 8.29 | 0.29 | Composite | 0.184 | 1.469 | 0.534 | 268 | 248 | 214 | 248
NEIL1- | PAIS1R | 8.35 | 0 | OHL | 0.184 | 1.469 | 0.534 | 268 | 248 | 214 | 248
NEIL2- | NEIL2C | 0 | 0.2 | Cable | 0.001 | 0.011 | 1.492 | 1140 | 1055 | 910 | 1055
NEIL2- | WIYH2R | 25.434 | 2e-06 | Composite | 0.1068 | 1.1268 | 6.671 | 955 | 883 | 763 | 883
NEIL4Q | HUER4- | 35.782 | 2e-06 | Composite | 0.0707 | 0.7505 | 19.8193 | 1350 | 1249 | 1078 | 1249
PAIS1Q | PAIS1S | 1.87 | 0 | OHL | 0.047 | 0.38 | 0.138 | 460 | 426 | 367 | 426
PAIS1R | PAIS1T | 1.87 | 0 | OHL | 0.047 | 0.38 | 0.138 | 460 | 426 | 367 | 426
POOB2Q | SHRU2Q | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 250 | 216 | 250
POOB2Q | SMEA2- | 7.79 | 0.19 | Composite | 0.044 | 0.34 | 6.693 | 360 | 333 | 287 | 333
POOB2R | SHRU2R | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 250 | 216 | 250
POOB2R | SMEA2- | 7.79 | 0.12 | Composite | 0.044 | 0.34 | 6.693 | 360 | 333 | 287 | 333
PORD2Q | WGEO2Q | 0 | 1.83 | Cable | 0.017 | 0.056 | 12.236 | 305 | 282 | 244 | 282
PORD2R | WGEO2R | 0 | 2.15 | Cable | 0.014 | 0.049 | 10.691 | 305 | 282 | 244 | 282
REDH1- | WFIE1A | 10.09 | 0 | OHL | 0.971 | 2.162 | 0.49 | 157 | 145 | 125 | 145
SMEA2- | WISH2- | 61.77 | 0 | OHL | 0.312 | 2.556 | 17.328 | 950 | 879 | 759 | 879
SMEA4Q | STHA4- | 75.76 | 0 | OHL | 0.176 | 1.446 | 43.893 | 1390 | 1286 | 1110 | 1286
SMEA4Q | TORN4- | 54 | 1.94 | Composite | 0.077 | 0.998 | 78.212 | 1250 | 1156 | 998 | 1156
STHA2A | WISH2- | 11.61 | 0 | OHL | 0.062 | 0.504 | 3.418 | 1050 | 971 | 838 | 971
STIR1Q | STIR1S | 1.97 | 0 | OHL | 0.086 | 0.426 | 0.108 | 229 | 212 | 183 | 212
STIR1R | STIR1T | 1.97 | 0.18 | Composite | 0.088 | 0.431 | 0.289 | 229 | 212 | 183 | 212
STIR1R | WFIE1A | 40.8 | 0 | OHL | 3.594 | 9.286 | 2.164 | 162 | 150 | 129 | 150
STLE1- | WIYH1- | 12.81 | 0.3 | Composite | 1.499 | 3.056 | 1.185 | 109 | 101 | 87 | 101
WFIB2- | WFIE2- | 22.28 | 0 | OHL | 0.11 | 0.93 | 5.9 | 950 | 879 | 759 | 879
WHTB1S | WHTL1S | 2.05 | 0 | OHL | 0.23 | 0.39 | 0.08 | 100 | 93 | 80 | 93
WHTB1T | WHTL1T | 2.05 | 0 | OHL | 0.23 | 0.39 | 0.08 | 100 | 93 | 80 | 93
WIYH2- | WIYH2R | -- | -- | -- | 0.005 | 1.5 | 0 | 1000 | 925 | 799 | 925

## B-2-1c
Table B.2.1c - NGET Circuits ETYS Yr1 - 2014/15 | [11 empty] | Back To Menu
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
BROM1A | ELTH11 | 1 | 0 | OHL | 0.358 | 0.546 | 16.884 | 274 | 253.45 | 218.789 | 253.45
HARK13 | JUNV1* | 1 | 0 | OHL | 1.194 | 2.729 | 0.743 | 111 | 102.675 | 71.0665 | 102.675
IROA11 | OLDS11 | 1 | 0 | OHL | 0.298 | 2.366 | 3.543 | 455 | 420.875 | 291.4525 | 420.875
IROA11 | OLDS12 | 1 | 0 | OHL | 0.297 | 2.361 | 2.693 | 455 | 420.875 | 291.4525 | 420.875
IROA12 | OLDS11 | 1 | 0 | OHL | 0.28 | 2.224 | 2.643 | 455 | 420.875 | 291.4525 | 420.875
IROA13 | OLDS12 | 1 | 0 | OHL | 0.28 | 2.224 | 2.643 | 455 | 420.875 | 291.4525 | 420.875
LITT14 | LITT11 | -- | -- | Series Reactor | 0.25 | 20 | 0 | 90 | 90 | 90 | 90
USKM11 | USKM11 | -- | -- | Series Reactor | 0.25 | 20 | 0 | 90 | 90 | 90 | 90
WALP12 | WALP11 | -- | -- | Series Reactor | 0.15 | 12 | 0 | 90 | 90 | 90 | 90
WIMB11 | WIMB12 | -- | -- | Series Reactor | 0.24627 | 19.7 | 0 | 90 | 90 | 90 | 90
WIMB11 | WIMB12 | -- | -- | Series Reactor | 0.25 | 20 | 0 | 90 | 90 | 90 | 90
WYLF11 | PERH11 | 1 | 0 | OHL | 0.435 | 3.172 | 17.6099 | 330 | 305.25 | 239.55 | 305.25
WYLF12 | PERH11 | 1 | 0 | OHL | 0.435 | 3.177 | 17.772 | 330 | 305.25 | 239.55 | 305.25
ABHA41 | EXET41 | 49.051 | 0 | OHL | 0.1055 | 1.0264 | 26.9062 | 1390 | 1285.75 | 1109.915 | 1285.75
ABHA41 | LAGA41 | 26.121 | 0 | OHL | 0.0559 | 0.5444 | 14.3938 | 1390 | 1285.75 | 1109.915 | 1285.75
ABHA42 | EXET41 | 48.785 | 0 | OHL | 0.1049 | 1.0209 | 26.7606 | 1390 | 1285.75 | 1109.915 | 1285.75
ABHA42 | LAGA41 | 26.121 | 0 | OHL | 0.0559 | 0.5444 | 14.3938 | 1390 | 1285.75 | 1109.915 | 1285.75
ABTH21 | PYLE21 | 35.388 | 0 | OHL | 0.1819 | 1.4523 | 9.9528 | 935 | 864.875 | 746.5975 | 864.875
ABTH21 | TREM21 | 46.451 | 0 | OHL | 0.2267 | 2.1393 | 11.8321 | 680 | 629 | 542.98 | 629
ABTH21 | UPPB22 | 26.996 | 0 | OHL | 0.1234 | 1.1426 | 7.3237 | 955 | 883.375 | 762.5675 | 883.375
ABTH22 | COWT2A | 13.318 | 0 | OHL | 0.0503 | 0.5449 | 3.758 | 935 | 864.875 | 746.5975 | 864.875
ABTH22 | UPPB21 | 27.035 | 0.547 | Composite | 0.1245 | 1.1595 | 13.2801 | 770 | 712.25 | 614.845 | 712.25
ALDW21 | BRIN21 | 17.961 | 0 | OHL | 0.1442 | 0.7628 | 4.8487 | 625 | 578.125 | 499.0625 | 578.125
ALDW21 | WMEL21 | 8.96 | 0 | OHL | 0.0409 | 0.3891 | 2.3695 | 955 | 883.375 | 762.5675 | 883.375
ALVE4A | INDQ41 | 97.176 | 0 | OHL | 0.2123 | 1.9366 | 56.1432 | 1390 | 1285.75 | 1109.915 | 1285.75
ALVE4A | TAUN41 | 73.293 | 0 | OHL | 0.1576 | 1.5337 | 40.2038 | 1390 | 1285.75 | 1109.915 | 1285.75
ALVE4B | INDQ41 | 97.294 | 0 | OHL | 0.2126 | 1.9391 | 56.2071 | 1390 | 1285.75 | 1109.915 | 1285.75
ALVE4B | TAUN42 | 73.298 | 0 | OHL | 0.1576 | 1.5338 | 40.2065 | 1390 | 1285.75 | 1109.915 | 1285.75
AMEM41 | ECLA41 | 35.315 | 0 | OHL | 0.0702 | 0.7046 | 20.3809 | 1390 | 1285.75 | 1109.915 | 1285.75
AMEM41 | IVER41 | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 1390 | 1285.75 | 1109.915 | 1285.75
AMEM42 | ECLA41 | 35.315 | 0 | OHL | 0.0702 | 0.7046 | 20.3809 | 2010 | 1859.25 | 1604.985 | 1859.25
AMEM42 | IVER42 | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 2010 | 1859.25 | 1604.985 | 1859.25
AXMI41 | CHIC42 | 39.5 | 0 | OHL | 0.0429 | 0.687 | 26.0389 | 2780 | 2571.5 | 2219.83 | 2571.5
AXMI41 | EXET41 | 36.184 | 0 | OHL | 0.0393 | 0.6293 | 23.853 | 2770 | 2562.25 | 2211.845 | 2562.25
BAGB21 | MAGA21 | 12.629 | 1.389 | parallel Composite | 0.0435 | 0.5216 | 17.0509 | 1200 | 1110 | 958.2 | 1110
BAGB21 | SWAN4* | 18.21 | 1.439 | parallel Composite | 0.0625 | 0.7488 | 19.1165 | 1100 | 1017.5 | 878.35 | 1017.5
BARK21 | BARP22 | 2.6 | 0.39 | Composite | 0.0106 | 0.1154 | 4.5169 | 850 | 786.25 | 678.725 | 786.25
BARK21 | REBR22 | 10.879 | 0 | OHL | 0.0411 | 0.4451 | 3.0706 | 1130 | 1045.25 | 902.305 | 1045.25
BARK22 | BARP21 | 2.6 | 0.39 | Composite | 0.0106 | 0.1154 | 4.5169 | 850 | 786.25 | 678.725 | 786.25
BARK22 | REBR21 | 10.854 | 0 | OHL | 0.041 | 0.4441 | 3.0636 | 1210 | 1119.25 | 966.185 | 1119.25
BARK41 | LAKE4* | 13.593 | 0 | OHL | 0.0212 | 0.2618 | 8.1224 | 3100 | 2867.5 | 2475.35 | 2867.5
BARK41 | LAKE4B | 13.593 | 0 | OHL | 0.0212 | 0.2618 | 8.1224 | 2890 | 2673.25 | 2307.665 | 2673.25
BARK41 | WHAM41 | 9.662 | 0 | OHL | 0.0176 | 0.1972 | 5.4519 | 2010 | 1859.25 | 1604.985 | 1859.25
BARK41 | WHAM41 | 9.662 | 0.124 | Composite | 0.0176 | 0.1977 | 10.2631 | 2010 | 1859.25 | 1604.985 | 1859.25
BARK41 | WTHU4* | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2010 | 1859.25 | 1604.985 | 1859.25
BARK41 | WTHU4A | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2010 | 1859.25 | 1604.985 | 1859.25
BEDD21 | CHSI21 | 17.836 | 0.286 | Composite | 0.0692 | 0.7576 | 7.8243 | 945 | 874.125 | 754.5825 | 874.125
BEDD21 | WIMB21 | 8.5 | 0.968 | Composite | 0.0409 | 0.3915 | 11.7005 | 860 | 795.5 | 686.71 | 795.5
BEDD22 | CHSI21 | 17.836 | 0.137 | Composite | 0.0689 | 0.7539 | 6.2735 | 760 | 703 | 606.86 | 703
BEDD23 | WIMB21 | 8.5 | 0.582 | Composite | 0.0398 | 0.3821 | 8.4754 | 995 | 920.375 | 794.5075 | 920.375
BEDD4A | ROWD42 | 0 | 11.676 | Cable | 0.0079 | 0.138 | 127.4459 | 1310 | 1211.75 | 1046.035 | 1211.75
BEDD4B | ROWD41 | 0 | 11.676 | Cable | 0.0105 | 0.0957 | 210.168 | 1410 | 1304.25 | 1125.885 | 1304.25
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 883.375 | 762.5675 | 883.375
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 883.375 | 762.5675 | 883.375
BESW21 | FECK21 | 35.814 | 0 | OHL | 0.1425 | 1.5095 | 9.7917 | 955 | 883.375 | 762.5675 | 883.375
BESW21 | OCKH21 | 56.939 | 0.631 | Composite | 0.2306 | 2.3887 | 22.6237 | 820 | 758.5 | 654.77 | 758.5
BICF41 | WALP41 | 37.775 | 0 | OHL | 0.0335 | 0.6488 | 25.3895 | 3190 | 2950.75 | 2547.215 | 2950.75
BICF41 | WBUR41 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3330 | 3080.25 | 2659.005 | 3080.25
BICF42 | SPLN41 | 20.109 | 0 | OHL | 0.0191 | 0.355 | 13.187 | 3160 | 2923 | 2523.26 | 2923
BICF42 | WBUR42 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3330 | 3080.25 | 2659.005 | 3080.25
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 883.375 | 762.5675 | 883.375
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 883.375 | 762.5675 | 883.375
BIRK21 | LISD2* | 0 | 12.891 | Cable | 0.0271 | 0.2978 | 125.0427 | 750 | 693.75 | 598.875 | 693.75
BISW21 | FECK21 | 22.83 | 0 | OHL | 0.0938 | 0.9633 | 6.2301 | 955 | 883.375 | 762.5675 | 883.375
BISW21 | KITW21 | 24.226 | 0 | OHL | 0.0932 | 1.0024 | 6.7545 | 955 | 883.375 | 762.5675 | 883.375
BISW21 | KITW21 | 27.111 | 0 | OHL | 0.1054 | 1.1236 | 7.5448 | 955 | 883.375 | 762.5675 | 883.375
BISW21 | PENN21 | 30.172 | 0 | OHL | 0.1233 | 1.2726 | 8.2379 | 1040 | 962 | 830.44 | 962
BLYT21 | STEW21 | 26.779 | 0 | OHL | 0.1472 | 1.3916 | 5.9965 | 680 | 629 | 542.98 | 629
BLYT21 | STEW21 | 26.711 | 0 | OHL | 0.1469 | 1.388 | 5.9813 | 680 | 629 | 542.98 | 629
BLYT21 | TYNE21 | 16.818 | 0 | OHL | 0.0742 | 0.7144 | 4.5642 | 1240 | 1147 | 990.14 | 1147
BLYT21 | TYNE2A | 16.866 | 0 | OHL | 0.0744 | 0.7164 | 4.5772 | 1240 | 1147 | 990.14 | 1147
BLYT4* | HEDD4A | 26.636 | 0.121 | Composite | 0.0427 | 0.514 | 18.017 | 1100 | 1017.5 | 878.35 | 1017.5
BLYT4* | HEDD4B | 26.636 | 0.49 | Composite | 0.043 | 0.5195 | 24.1166 | 1100 | 1017.5 | 878.35 | 1017.5
BODE41 | BODE41 | 0 | 0.25 | Cable | 0.0002 | 0.003 | 2.7288 | 500 | 462.5 | 399.25 | 462.5
BODE41 | BODE41 | 0 | 0.25 | Cable | 0.0002 | 0.003 | 2.7288 | 500 | 462.5 | 399.25 | 462.5
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 2780 | 2571.5 | 2219.83 | 2571.5
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 2770 | 2562.25 | 2211.845 | 2562.25
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 2780 | 2571.5 | 2219.83 | 2571.5
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 2780 | 2571.5 | 2219.83 | 2571.5
BOTW41 | FAWL41 | 7.479 | 3.57 | Composite | 0.0102 | 0.1509 | 59.5766 | 1110 | 1026.75 | 886.335 | 1026.75
BOTW41 | LOVE41 | 14.672 | 0 | OHL | 0.013 | 0.252 | 9.8617 | 2780 | 2571.5 | 2219.83 | 2571.5
BRAI4A | BRFO41 | 48.267 | 0 | OHL | 0.0524 | 0.8395 | 31.8178 | 2780 | 2571.5 | 2219.83 | 2571.5
BRAI4A | RAYL41 | 32.993 | 0 | OHL | 0.0292 | 0.5667 | 22.175 | 2780 | 2571.5 | 2219.83 | 2571.5
BRAI4B | PELH41 | 65.942 | 0 | OHL | 0.0716 | 1.1469 | 43.4688 | 2780 | 2571.5 | 2219.83 | 2571.5
BRAI4B | RAYL41 | 33.032 | 0 | OHL | 0.0293 | 0.5674 | 22.2011 | 2780 | 2571.5 | 2219.83 | 2571.5
BRAW21 | ELLA21 | 16.802 | 0.081 | Composite | 0.0769 | 0.7134 | 5.4384 | 760 | 703 | 606.86 | 703
BRAW21 | KIRK21 | 17.279 | 4.547 | Composite | 0.0844 | 0.855 | 54.1379 | 760 | 703 | 606.86 | 703
BRAW21 | MONF21 | 51.155 | 0 | OHL | 0.1174 | 1.8824 | 15.9388 | 1200 | 1110 | 958.2 | 1110
BRAW4A | PADI41 | 59.3 | 0 | OHL | 0.0754 | 1.1321 | 35.9226 | 1000 | 925 | 798.5 | 925
BRED21 | MACC21 | 19.612 | 0 | OHL | 0.0895 | 0.8305 | 5.3251 | 950 | 878.75 | 758.575 | 878.75
BRED21 | SMAN21 | 10.004 | 5.629 | parallel Composite | 0.0513 | 0.4604 | 46.7619 | 850 | 786.25 | 678.725 | 786.25
BRED21 | STAL21 | 15.054 | 0 | OHL | 0.0687 | 0.6374 | 4.087 | 1090 | 1008.25 | 870.365 | 1008.25
BRFO41 | BRFO41 | 0 | 0.2 | Cable | 0 | 0 | 0 | 3340 | 3089.5 | 2666.99 | 3089.5
BRFO41 | NORM41 | 61.576 | 0.1 | Composite | 0.1325 | 1.2896 | 35.7771 | 1590 | 1470.75 | 1269.615 | 1470.75
BRFO41 | NORM41 | 61.576 | 0.1 | Composite | 0.1325 | 1.2896 | 35.7771 | 1590 | 1470.75 | 1269.615 | 1470.75
BRFO41 | PELH41 | 69.301 | 0 | OHL | 0.0752 | 1.2053 | 45.6836 | 3100 | 2867.5 | 2475.35 | 2867.5
BRFO41 | SIZE41 | 43.331 | 0 | OHL | 0.047 | 0.7537 | 28.5643 | 2780 | 2571.5 | 2219.83 | 2571.5
BRFO41 | SIZE41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2780 | 2571.5 | 2219.83 | 2571.5
BRFO41 | SIZE41 | 43.331 | 0 | OHL | 0.047 | 0.7537 | 28.5643 | 2780 | 2571.5 | 2219.83 | 2571.5
BRFO41 | SIZE41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2780 | 2571.5 | 2219.83 | 2571.5
BRIM2A | TOTT21 | 7.437 | 0.311 | Composite | 0.0345 | 0.3234 | 5.3982 | 1090 | 1008.25 | 870.365 | 1008.25
BRIM2A | WALX22 | 5.865 | 0 | OHL | 0.0268 | 0.2482 | 1.5911 | 1090 | 1008.25 | 870.365 | 1008.25
BRIM2B | TOTT24 | 7.305 | 0.393 | Composite | 0.0341 | 0.3201 | 6.2537 | 1090 | 1008.25 | 870.365 | 1008.25
BRIM2B | WALX22 | 5.997 | 0 | OHL | 0.0274 | 0.2538 | 1.6269 | 1090 | 1008.25 | 870.365 | 1008.25
BRIM2C | TOTT22 | 7.455 | 0.235 | Composite | 0.0344 | 0.3223 | 4.5788 | 1090 | 1008.25 | 870.365 | 1008.25
BRIM2C | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1090 | 1008.25 | 870.365 | 1008.25
BRIM2D | TOTT23 | 7.455 | 0.384 | Composite | 0.0347 | 0.3264 | 6.1984 | 1090 | 1008.25 | 870.365 | 1008.25
BRIM2D | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1090 | 1008.25 | 870.365 | 1008.25
BRIN21 | CHTE21 | 22.464 | 0.22 | Composite | 0.0519 | 0.8305 | 9.3505 | 935 | 864.875 | 746.5975 | 864.875
BRIN21 | JORD21 | 13.257 | 1.489 | Composite | 0.0647 | 0.5918 | 16.0432 | 555 | 513.375 | 443.1675 | 513.375
BRIN21 | NORL22 | 13.257 | 2.845 | Composite | 0.0708 | 0.6085 | 24.8202 | 420 | 388.5 | 335.37 | 388.5
BRIN21 | TEMP21 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 883.375 | 762.5675 | 883.375
BRIN21 | TEMP22 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 883.375 | 762.5675 | 883.375
BRIN22 | CHTE21 | 22.375 | 0 | OHL | 0.0513 | 0.8236 | 6.9689 | 1200 | 1110 | 958.2 | 1110
BRIN22 | THUR21 | 5.704 | 0 | OHL | 0.0599 | 0.2384 | 1.5621 | 625 | 578.125 | 499.0625 | 578.125
BRIN22 | TINP21 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 685 | 633.625 | 546.9725 | 633.625
BRIN22 | TINP22 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 685 | 633.625 | 546.9725 | 633.625
BRIN41 | THOM41 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2550 | 2358.75 | 2036.175 | 2358.75
BRLE41 | DIDC41 | 37.691 | 5.7 | parallel Composite | 0.0419 | 0.6724 | 87.0663 | 2780 | 2571.5 | 2219.83 | 2571.5
BRLE41 | DIDC41 | 37.691 | 5.7 | parallel Composite | 0.0419 | 0.6719 | 134.3668 | 2280 | 2109 | 1820.58 | 2109
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 2780 | 2571.5 | 2219.83 | 2571.5
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 2780 | 2571.5 | 2219.83 | 2571.5
BRLE41 | MELK41 | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8621 | 1390 | 1285.75 | 1109.915 | 1285.75
BRLE41 | MELK41 | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8621 | 1390 | 1285.75 | 1109.915 | 1285.75
BRLE41 | WWEY41 | 49.375 | 0 | OHL | 0.0789 | 0.9496 | 29.6904 | 2200 | 2035 | 1756.7 | 2035
BRLE41 | WWEY42 | 49.375 | 0 | OHL | 0.0789 | 0.9496 | 29.6904 | 2200 | 2035 | 1756.7 | 2035
BURW41 | PELH41 | 42.934 | 0 | OHL | 0.0381 | 0.7374 | 28.8562 | 3030 | 2802.75 | 2419.455 | 2802.75
BURW41 | PELH41 | 42.782 | 0 | OHL | 0.0379 | 0.7348 | 28.7545 | 3100 | 2867.5 | 2475.35 | 2867.5
BURW41 | WALP41 | 51.189 | 0 | OHL | 0.0454 | 0.8792 | 34.4056 | 3100 | 2867.5 | 2475.35 | 2867.5
BURW41 | WALP41 | 51.183 | 0 | OHL | 0.0454 | 0.8791 | 34.4016 | 3100 | 2867.5 | 2475.35 | 2867.5
BUSH21 | DRAK21 | 38.153 | 0 | OHL | 0.146 | 1.6016 | 10.4839 | 955 | 883.375 | 762.5675 | 883.375
BUSH21 | PENN21 | 21.653 | 0 | OHL | 0.0824 | 0.9078 | 5.9595 | 1040 | 962 | 830.44 | 962
BUSH21 | WIEN21 | 5.197 | 4.318 | Composite | 0.0311 | 0.3404 | 48.3427 | 760 | 703 | 606.86 | 703
BUST21 | DRAK21 | 34.592 | 0 | OHL | 0.0793 | 1.2733 | 10.7739 | 1200 | 1110 | 958.2 | 1110
BUST21 | DRAK21 | 34.537 | 0 | OHL | 0.0792 | 1.2713 | 10.7569 | 1200 | 1110 | 958.2 | 1110
BUST21 | NECH21 | 2.648 | 7.673 | Composite | 0.0251 | 0.3262 | 84.1239 | 725 | 670.625 | 578.9125 | 670.625
BUST21 | NECH21 | 2.648 | 7.673 | Composite | 0.0251 | 0.3262 | 84.1239 | 725 | 670.625 | 578.9125 | 670.625
CANT41 | SELL41 | 26.711 | 0.257 | Composite | 0.0417 | 0.5138 | 26.0013 | 2370 | 2192.25 | 1892.445 | 2192.25
CANT41 | SELL41 | 26.711 | 0.257 | Composite | 0.0417 | 0.5138 | 26.0013 | 2370 | 2192.25 | 1892.445 | 2192.25
CAPE41 | DEES42 | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3580 | 3311.5 | 2858.63 | 3311.5
CAPE41 | FROD41 | 18.315 | 0 | OHL | 0.0198 | 0.2912 | 13.2878 | 2780 | 2571.5 | 2219.83 | 2571.5
CAPE42 | DEES41 | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3580 | 3311.5 | 2858.63 | 3311.5
CAPE42 | FROD41 | 18.404 | 0 | OHL | 0.0199 | 0.2926 | 13.3521 | 2780 | 2571.5 | 2219.83 | 2571.5
CARE21 | COWT2A | 27.881 | 0 | OHL | 0.1533 | 1.4488 | 6.2406 | 680 | 629 | 542.98 | 629
CARE21 | USKM22 | 19.94 | 0 | OHL | 0.1096 | 1.0362 | 4.4651 | 680 | 629 | 542.98 | 629
CARR21 | SMAN21 | 10.747 | 0.23 | Composite | 0.0475 | 0.476 | 5.3274 | 835 | 772.375 | 666.7475 | 772.375
CARR21 | SMAN21 | 9.294 | 0.133 | Composite | 0.0414 | 0.4101 | 3.8882 | 835 | 772.375 | 666.7475 | 772.375
CARR41 | DAIN41 | 3.352 | 0 | OHL | 0.0059 | 0.0653 | 1.9782 | 3100 | 2867.5 | 2475.35 | 2867.5
CARR41 | KEAR41 | 13.154 | 0 | OHL | 0.0225 | 0.2574 | 7.7626 | 2210 | 2044.25 | 1764.685 | 2044.25
CARR41 | PEWO41 | 56.9 | 0 | OHL | 0.0988 | 1.1179 | 33.4403 | 2170 | 2007.25 | 1732.745 | 2007.25
CARR42 | DAIN41 | 2.036 | 0 | OHL | 0.0037 | 0.0405 | 1.1791 | 750 | 693.75 | 598.875 | 693.75
CARR43 | DAIN41 | 2.063 | 0 | OHL | 0.0032 | 0.0397 | 1.2352 | 750 | 693.75 | 598.875 | 693.75
CELL41 | DAIN41 | 53.412 | 2.31 | parallel Composite | 0.0843 | 1.0314 | 76.88 | 2510 | 2321.75 | 2004.235 | 2321.75
CELL41 | DRAK41 | 45.012 | 0 | OHL | 0.0719 | 0.8657 | 27.0666 | 2180 | 2016.5 | 1740.73 | 2016.5
CELL41 | DRAK41 | 45.564 | 0 | OHL | 0.0728 | 0.8763 | 27.3975 | 2180 | 2016.5 | 1740.73 | 2016.5
CELL41 | MACC41 | 31.617 | 0 | OHL | 0.0494 | 0.6068 | 18.9766 | 3100 | 2867.5 | 2475.35 | 2867.5
CHIC41 | EXET41 | 75.92 | 0 | OHL | 0.0824 | 1.3205 | 50.0469 | 2780 | 2571.5 | 2219.83 | 2571.5
CHIC41 | MANN41 | 53.913 | 0 | OHL | 0.0585 | 0.9377 | 35.5401 | 3070 | 2839.75 | 2451.395 | 2839.75
CHIC42 | MANN41 | 54.066 | 0 | OHL | 0.0587 | 0.9404 | 35.6406 | 3070 | 2839.75 | 2451.395 | 2839.75
CHSI21 | WWEY21 | 15.318 | 0 | OHL | 0.0519 | 0.6229 | 4.351 | 1320 | 1221 | 1054.02 | 1221
CHSI21 | WWEY22 | 15.347 | 0 | OHL | 0.052 | 0.6241 | 4.3592 | 1320 | 1221 | 1054.02 | 1221
CHTE21 | HIGM21 | 43.651 | 0 | OHL | 0.1214 | 1.8002 | 12.2369 | 1380 | 1276.5 | 1101.93 | 1276.5
CHTE21 | HIGM21 | 43.792 | 0 | OHL | 0.1218 | 1.806 | 12.2763 | 1380 | 1276.5 | 1101.93 | 1276.5
CILF21 | UPPB21 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 750 | 693.75 | 598.875 | 693.75
CILF22 | UPPB22 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 750 | 693.75 | 598.875 | 693.75
CILF41 | IMPP41 | 25.119 | 0 | OHL | 0.0273 | 0.4396 | 16.4758 | 2780 | 2571.5 | 2219.83 | 2571.5
CILF41 | RASS41 | 26.901 | 0 | OHL | 0.0292 | 0.4679 | 17.7332 | 2780 | 2571.5 | 2219.83 | 2571.5
CILF41 | SWAN41 | 61.595 | 0 | OHL | 0.0668 | 1.0713 | 40.6034 | 2780 | 2571.5 | 2219.83 | 2571.5
CILF41 | SWAN41 | 60 | 0 | OHL | 0.0651 | 1.0436 | 39.5528 | 2780 | 2571.5 | 2219.83 | 2571.5
CILF41 | SWAN42 | 61.655 | 0 | OHL | 0.0669 | 1.0724 | 40.6428 | 3180 | 2941.5 | 2539.23 | 2941.5
CILF41 | WHSO4A | 35.208 | 0 | OHL | 0.0383 | 0.6151 | 23.1262 | 2780 | 2571.5 | 2219.83 | 2571.5
CITR41 | CITR41 | 0 | 0.1 | Cable | 0.0001 | 0.0008 | 1.8 | 1730 | 1600.25 | 1381.405 | 1600.25
CITR41 | CITR41 | 0 | 0.1 | Cable | 0.0001 | 0.0008 | 1.8 | 1570 | 1452.25 | 1253.645 | 1452.25
CITR41 | SJOW41 | 0 | 7.243 | Cable | 0.0065 | 0.0594 | 130.374 | 1280 | 1184 | 1022.08 | 1184
CITR41 | SJOW41 | 0 | 6.776 | Cable | 0.0061 | 0.0556 | 121.968 | 1280 | 1184 | 1022.08 | 1184
CITR41 | WHAM4A | 0 | 9.54 | Cable | 0.0086 | 0.0782 | 171.72 | 1280 | 1184 | 1022.08 | 1184
CITR41 | WHAM4B | 0 | 9.39 | Cable | 0.0085 | 0.077 | 169.02 | 1280 | 1184 | 1022.08 | 1184
CLEH41 | CANT41 | 14.7 | 0 | OHL | 0.0229 | 0.282 | 8.8214 | 3100 | 2867.5 | 2475.35 | 2867.5
CLEH41 | KEMS41 | 13.5 | 0 | OHL | 0.021 | 0.259 | 8.1013 | 3100 | 2867.5 | 2475.35 | 2867.5
CONQ41 | DAIN41 | 60.331 | 0 | OHL | 0.094 | 1.1575 | 36.2038 | 2890 | 2673.25 | 2307.665 | 2673.25
COSO41 | RAYL41 | 13.913 | 0 | OHL | 0.0217 | 0.2669 | 8.3485 | 2890 | 2673.25 | 2307.665 | 2673.25
COSO41 | TILB4B | 12.363 | 0 | OHL | 0.0193 | 0.2372 | 7.419 | 2890 | 2673.25 | 2307.665 | 2673.25
COTT41 | EASO41 | 135.486 | 0 | OHL | 0.147 | 2.3565 | 89.3125 | 2780 | 2571.5 | 2219.83 | 2571.5
COTT41 | GREN41 | 129.478 | 0 | OHL | 0.2293 | 2.5548 | 75.7188 | 2010 | 1859.25 | 1604.985 | 1859.25
COTT41 | KEAD41 | 34.479 | 0 | OHL | 0.0577 | 0.669 | 20.523 | 2210 | 2044.25 | 1764.685 | 2044.25
COTT41 | KEAD41 | 34.628 | 0 | OHL | 0.058 | 0.672 | 20.6091 | 2210 | 2044.25 | 1764.685 | 2044.25
COTT41 | STAY41 | 27.788 | 0.5 | parallel Composite | 0.0506 | 0.5544 | 21.5604 | 2210 | 2044.25 | 1764.685 | 2044.25
COTT42 | EASO41 | 135.23 | 0 | OHL | 0.1467 | 2.352 | 89.1444 | 2780 | 2571.5 | 2219.83 | 2571.5
COTT42 | STAY41 | 27.698 | 0 | OHL | 0.0441 | 0.5297 | 16.7334 | 2210 | 2044.25 | 1764.685 | 2044.25
COTT42 | WBUR42 | 6.76 | 0 | OHL | 0.0096 | 0.1298 | 4.0616 | 3330 | 3080.25 | 2659.005 | 3080.25
COVE21 | NECH21 | 30.715 | 0 | OHL | 0.0705 | 1.1304 | 9.5678 | 1200 | 1110 | 958.2 | 1110
COVE21 | RATS2A | 64.863 | 0.5 | Composite | 0.2171 | 2.6384 | 23.342 | 1000 | 925 | 798.5 | 925
COWL41 | CULJ41 | 6.496 | 0 | OHL | 0.007 | 0.113 | 4.2822 | 2780 | 2571.5 | 2219.83 | 2571.5
COWL41 | DIDC41 | 11.503 | 0 | OHL | 0.0125 | 0.2001 | 7.5827 | 2780 | 2571.5 | 2219.83 | 2571.5
COWL41 | ECLA41 | 36.301 | 0 | OHL | 0.0394 | 0.6314 | 23.9301 | 2780 | 2571.5 | 2219.83 | 2571.5
COWL41 | LEIB4A | 52.495 | 0 | OHL | 0.0538 | 0.9095 | 34.8125 | 2780 | 2571.5 | 2219.83 | 2571.5
COWL41 | MITY41 | 100.105 | 2.092 | Composite | 0.1418 | 1.8493 | 98.0706 | 1180 | 1091.5 | 942.23 | 1091.5
COWL41 | WALH41 | 89.553 | 2.092 | Composite | 0.113 | 1.6366 | 92.0801 | 1180 | 1091.5 | 942.23 | 1091.5
COWT2A | PYLE21 | 22.6 | 0 | OHL | 0.1334 | 0.9291 | 6.3441 | 935 | 864.875 | 746.5975 | 864.875
CREB21 | SAEN21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1750 | 1618.75 | 1397.375 | 1618.75
CREB22 | HEDO21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1750 | 1618.75 | 1397.375 | 1618.75
CREB41 | GART4A | 32.081 | 0 | OHL | 0.0348 | 0.558 | 21.1475 | 2770 | 2562.25 | 2211.845 | 2562.25
CREB41 | GART4B | 32.109 | 0 | OHL | 0.0348 | 0.5585 | 21.1659 | 3070 | 2839.75 | 2451.395 | 2839.75
CREB41 | THTO41 | 29.809 | 0 | OHL | 0.0264 | 0.512 | 20.0362 | 3070 | 2839.75 | 2451.395 | 2839.75
CREB41 | THTO42 | 29.671 | 0 | OHL | 0.0263 | 0.5096 | 19.9438 | 3070 | 2839.75 | 2451.395 | 2839.75
CULJ41 | DIDC41 | 4.898 | 0 | OHL | 0.0053 | 0.0852 | 3.2288 | 2780 | 2571.5 | 2219.83 | 2571.5
DAIN41 | CARR41 | 2.545 | 0 | OHL | 0.004 | 0.0488 | 1.5263 | 2170 | 2007.25 | 1732.745 | 2007.25
DAIN41 | CONQ41 | 60.294 | 0 | OHL | 0.0938 | 1.1562 | 36.2009 | 2890 | 2673.25 | 2307.665 | 2673.25
DAIN41 | MACC41 | 33.593 | 2.4 | parallel Composite | 0.0536 | 0.6516 | 66.7378 | 2400 | 2220 | 1916.4 | 2220
DEES41 | GWYN4* | 30.217 | 0 | OHL | 0.0328 | 0.5256 | 19.9194 | 2780 | 2571.5 | 2219.83 | 2571.5
DEES41 | TREU4A | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2400 | 2220 | 1916.4 | 2220
DEES42 | GWYN4* | 30.217 | 0 | OHL | 0.0328 | 0.5256 | 19.9194 | 2780 | 2571.5 | 2219.83 | 2571.5
DEES42 | TREU4B | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2210 | 2044.25 | 1764.685 | 2044.25
DIDC41 | DIDC41 | 0 | 0 | Series Reactor | 0.0063 | 0.5 | 0 | 2640 | 2442 | 2108.04 | 2442
DINO41 | PENT41 | 0 | 10.762 | Cable | 0.0075 | 0.1184 | 215.24 | 1600 | 1480 | 1277.6 | 1480
DINO41 | PENT41 | 4.545 | 6.183 | Composite | 0.0093 | 0.1402 | 126.9571 | 1620 | 1498.5 | 1293.57 | 1498.5
DRAK41 | HAMH41 | 29.434 | 0 | OHL | 0.0535 | 0.5856 | 17.0415 | 2010 | 1859.25 | 1604.985 | 1859.25
DRAK41 | OLDB4A | 48.818 | 0.5 | Composite | 0.0921 | 0.9799 | 36.5074 | 1000 | 925 | 798.5 | 925
DRAK41 | RATS41 | 32.907 | 0 | OHL | 0.0582 | 0.6532 | 19.1262 | 2010 | 1859.25 | 1604.985 | 1859.25
DRAK41 | RUGE41 | 20.966 | 0 | OHL | 0.0379 | 0.4173 | 12.1495 | 2010 | 1859.25 | 1604.985 | 1859.25
DRAK41 | WILE41 | 16.937 | 0 | OHL | 0.0308 | 0.337 | 9.8147 | 2010 | 1859.25 | 1604.985 | 1859.25
DRAX41 | DRAX42 | 0 | 0 | Series Reactor | 0.006 | 2 | 0 | 1320 | 1221 | 1054.02 | 1221
DRAX41 | EGGB42 | 11.188 | 0.64 | Composite | 0.0128 | 0.2017 | 30.2999 | 2090 | 1933.25 | 1668.865 | 1933.25
DRAX41 | THTO43 | 22.579 | 0 | OHL | 0.0245 | 0.3927 | 14.8844 | 2770 | 2562.25 | 2211.845 | 2562.25
DRAX42 | EGGB41 | 11.188 | 0 | OHL | 0.0124 | 0.1983 | 7.2605 | 2970 | 2747.25 | 2371.545 | 2747.25
DRAX42 | THOM42 | 21.73 | 0 | OHL | 0.0311 | 0.3992 | 13.6444 | 2980 | 2756.5 | 2379.53 | 2756.5
DRAX42 | THTO42 | 22.579 | 0 | OHL | 0.0245 | 0.3927 | 14.8844 | 2780 | 2571.5 | 2219.83 | 2571.5
DUNG41 | NINF41 | 44.056 | 0 | OHL | 0.0391 | 0.7567 | 29.6111 | 3070 | 2839.75 | 2451.395 | 2839.75
DUNG41 | NINF41 | 44.081 | 0 | OHL | 0.0391 | 0.7571 | 29.6278 | 3070 | 2839.75 | 2451.395 | 2839.75
DUNG41 | SELL41 | 25.403 | 0.415 | Composite | 0.0464 | 0.5076 | 29.6616 | 1850 | 1711.25 | 1477.225 | 1711.25
DUNG41 | SELL41 | 25.387 | 0.415 | Composite | 0.0464 | 0.5073 | 29.6523 | 1850 | 1711.25 | 1477.225 | 1711.25
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 525 | 485.625 | 419.2125 | 485.625
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 525 | 485.625 | 419.2125 | 485.625
EALI21 | WISD2A | 0 | 6.075 | Cable | 0.0121 | 0.1391 | 61.5397 | 750 | 693.75 | 598.875 | 693.75
EASO41 | LITB41 | 0 | 1 | Cable | 0.0024 | 0.033 | 45.76 | 1386 | 1282.05 | 1106.721 | 1282.05
EASO41 | WYMO41 | 35.272 | 0 | OHL | 0.0383 | 0.6135 | 23.2517 | 2780 | 2571.5 | 2219.83 | 2571.5
EASO41 | WYMO41 | 35.272 | 0 | OHL | 0.0383 | 0.6135 | 23.2517 | 2780 | 2571.5 | 2219.83 | 2571.5
ECLA41 | LEIB4B | 15.985 | 0 | OHL | 0.0142 | 0.2745 | 10.7445 | 2780 | 2571.5 | 2219.83 | 2571.5
ECLA41 | PAFB4A | 44.72 | 0 | OHL | 0.0814 | 0.8898 | 25.9172 | 2010 | 1859.25 | 1604.985 | 1859.25
ECLA41 | PAFB4B | 44.886 | 0 | OHL | 0.0817 | 0.8931 | 26.0131 | 2010 | 1859.25 | 1604.985 | 1859.25
EGGB41 | MONF4A | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 1000 | 925 | 798.5 | 925
EGGB41 | ROCH4A | 84.875 | 0.7 | Composite | 0.1416 | 1.6214 | 64.456 | 1100 | 1017.5 | 878.35 | 1017.5
EGGB41 | THOM42 | 28.07 | 0.197 | Composite | 0.0293 | 0.4897 | 21.8489 | 2220 | 2053.5 | 1772.67 | 2053.5
EGGB42 | FERR41 | 11.864 | 0 | OHL | 0.0128 | 0.2063 | 7.8228 | 2780 | 2571.5 | 2219.83 | 2571.5
EGGB42 | MONF41 | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 2780 | 2571.5 | 2219.83 | 2571.5
EGGB42 | STSB41 | 48.084 | 0 | OHL | 0.052 | 0.8361 | 31.7071 | 2780 | 2571.5 | 2219.83 | 2571.5
ELLA21 | FERR21 | 45.565 | 0 | OHL | 0.1573 | 1.8245 | 13.1474 | 1320 | 1221 | 1054.02 | 1221
ELLA21 | KIRK21 | 33.995 | 5.044 | Composite | 0.1618 | 1.5765 | 64.0738 | 760 | 703 | 606.86 | 703
ELLA21 | STAL21 | 39.6 | 0 | OHL | 0.1647 | 1.6624 | 10.8691 | 955 | 883.375 | 762.5675 | 883.375
ELST21 | MILH21 | 6.375 | 6.338 | Composite | 0.0548 | 0.3963 | 55.677 | 525 | 485.625 | 419.2125 | 485.625
ELST21 | MILH22 | 6.375 | 6.282 | Composite | 0.0546 | 0.3952 | 55.2004 | 525 | 485.625 | 419.2125 | 485.625
ELST21 | WARL21 | 59.208 | 0.261 | Composite | 0.2449 | 2.4665 | 19.2619 | 760 | 703 | 606.86 | 703
ELST21 | WATS21 | 5.398 | 0.399 | Composite | 0.0254 | 0.2396 | 5.8016 | 760 | 703 | 606.86 | 703
ELST22 | WARL21 | 59.244 | 0.59 | Composite | 0.2456 | 2.4772 | 22.8481 | 760 | 703 | 606.86 | 703
ELST22 | WATS22 | 5.398 | 0.222 | Composite | 0.0251 | 0.2347 | 3.8776 | 760 | 703 | 606.86 | 703
ELST41 | ELST4A | 0 | 0.1 | Cable | 0 | 0 | 0 | 2000 | 1850 | 1597 | 1850
ELST41 | SJOW41 | 0 | 20 | Cable | 0.014 | 0.176 | 244.29 | 1770 | 1637.25 | 1413.345 | 1637.25
ELST42 | SUND42 | 34.706 | 0 | OHL | 0.0749 | 0.6947 | 19.9385 | 1000 | 925 | 798.5 | 925
ELST4A | ELST41 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 2000 | 1850 | 1597 | 1850
ELST4A | SUND41 | 34.834 | 0 | OHL | 0.0752 | 0.6972 | 20.0118 | 1590 | 1470.75 | 1269.615 | 1470.75
ENDE41 | PAFB4A | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2010 | 1859.25 | 1604.985 | 1859.25
ENDE41 | PAFB4B | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2010 | 1859.25 | 1604.985 | 1859.25
ENDE41 | RATS41 | 36.873 | 0 | OHL | 0.0398 | 0.5862 | 26.7543 | 2780 | 2571.5 | 2219.83 | 2571.5
ENDE41 | RATS42 | 36.941 | 0 | OHL | 0.0399 | 0.5872 | 26.8034 | 2780 | 2571.5 | 2219.83 | 2571.5
EXET41 | TAUN41 | 38.147 | 0 | OHL | 0.0694 | 0.759 | 22.1074 | 2010 | 1859.25 | 1604.985 | 1859.25
EXET41 | TAUN42 | 38.107 | 0 | OHL | 0.0693 | 0.7582 | 22.0842 | 2010 | 1859.25 | 1604.985 | 1859.25
FAWL41 | LOVE41 | 22.379 | 3.885 | Composite | 0.0237 | 0.4115 | 74.7979 | 1110 | 1026.75 | 886.335 | 1026.75
FAWL41 | MANN41 | 61.115 | 0 | OHL | 0.066 | 1.0014 | 43.0253 | 2780 | 2571.5 | 2219.83 | 2571.5
FAWL41 | MAWO41 | 18.639 | 0 | OHL | 0.0214 | 0.3062 | 13.1667 | 2420 | 2238.5 | 1932.37 | 2238.5
FECK41 | HAMH41 | 43.314 | 0 | OHL | 0.0783 | 0.862 | 25.076 | 2010 | 1859.25 | 1604.985 | 1859.25
FECK41 | IRON41 | 66.123 | 0 | OHL | 0.123 | 1.3148 | 38.3377 | 2010 | 1859.25 | 1604.985 | 1859.25
FECK41 | MITY41 | 78.649 | 0 | OHL | 0.1527 | 1.5677 | 45.4522 | 1970 | 1822.25 | 1573.045 | 1822.25
FECK41 | WALH41 | 67.986 | 0 | OHL | 0.1237 | 1.3527 | 39.4005 | 1970 | 1822.25 | 1573.045 | 1822.25
FENW4A | DRAX41 | 13.443 | 0 | OHL | 0.0146 | 0.2338 | 8.8618 | 2770 | 2562.25 | 2211.845 | 2562.25
FENW4A | THOM41 | 8.287 | 0 | OHL | 0.0165 | 0.1653 | 4.7826 | 2010 | 1859.25 | 1604.985 | 1859.25
FERR22 | FERR22 | 0 | 0.8161 | Cable | 0.0027 | 0.0204 | 6.0881 | 435 | 402.375 | 347.3475 | 402.375
FERR22 | FERR22 | 0 | 0.70866 | Cable | 0.0065 | 0.0119 | 3.6567 | 183 | 169.275 | 146.1255 | 169.275
FERR22 | MONF21 | 4.485 | 0 | OHL | 0.0103 | 0.1651 | 1.3966 | 1140 | 1054.5 | 910.29 | 1054.5
FERR22 | SKLG21 | 20.033 | 0.685 | Composite | 0.0991 | 0.9874 | 9.8077 | 865 | 800.125 | 690.7025 | 800.125
FERR23 | FERR23 | 0 | 0.72603 | Cable | 0.0024 | 0.0182 | 5.4162 | 435 | 402.375 | 347.3475 | 402.375
FERR2A | FERR23 | 0.586 | 0 | OHL | 0.0013 | 0.0216 | 0.1825 | 1230 | 1137.75 | 982.155 | 1137.75
FERR2A | MONF22 | 3.922 | 0 | OHL | 0.009 | 0.1444 | 1.2212 | 1200 | 1110 | 958.2 | 1110
FERR2B | FERR21 | 0.554 | 0.16 | Composite | 0.002 | 0.0234 | 1.3262 | 1030 | 952.75 | 822.455 | 952.75
FERR2B | SKLG21 | 19.545 | 0.56 | Composite | 0.0975 | 0.9671 | 8.7544 | 865 | 800.125 | 690.7025 | 800.125
FFES21 | TRAW21 | 7.291 | 0.133 | Composite | 0.0771 | 0.3081 | 2.8868 | 480 | 444 | 383.28 | 444
FFES22 | TRAW21 | 7.358 | 0 | OHL | 0.0772 | 0.3075 | 2.0153 | 550 | 508.75 | 439.175 | 508.75
FIDF21 | FIDF23 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 693.75 | 598.875 | 693.75
FIDF21 | FROD22 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1320 | 1221 | 1054.02 | 1221
FIDF22 | FIDF24 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 693.75 | 598.875 | 693.75
FIDF22 | FROD21 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1320 | 1221 | 1054.02 | 1221
FIDF23 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1320 | 1221 | 1054.02 | 1221
FIDF24 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1320 | 1221 | 1054.02 | 1221
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.0748 | 0.8176 | 23.8163 | 2210 | 2044.25 | 1764.685 | 2044.25
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.0748 | 0.8176 | 23.8163 | 2210 | 2044.25 | 1764.685 | 2044.25
FOUR21 | HARK21 | 55.711 | 0 | OHL | 0.3289 | 2.3608 | 15.2112 | 855 | 790.875 | 682.7175 | 790.875
FOUR21 | STEW21 | 27.731 | 0 | OHL | 0.1637 | 1.1751 | 7.5717 | 855 | 790.875 | 682.7175 | 790.875
FROD41 | ROCK41 | 1.197 | 0 | OHL | 0.0022 | 0.0238 | 0.6917 | 1100 | 1017.5 | 878.35 | 1017.5
GART4B | KILL41 | 34.462 | 0 | OHL | 0.038 | 0.6467 | 21.2883 | 3160 | 2923 | 2523.26 | 2923
GRAI41 | GRAI41 | 0 | 0 | Series Reactor | 0.0027 | 2.3091 | 0 | 2000 | 1850 | 1597 | 1850
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2640 | 2442 | 2108.04 | 2442
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2640 | 2442 | 2108.04 | 2442
GRAI41 | KINO41 | 11.507 | 0.8 | parallel Composite | 0.0126 | 0.2028 | 18.5632 | 3100 | 2867.5 | 2475.35 | 2867.5
GRAI41 | MEDW41 | 2.5 | 0 | OHL | 0.0054 | 0.0513 | 1.3945 | 1390 | 1285.75 | 1109.915 | 1285.75
GRAI41 | TILB41 | 26.6424 | 1.805 | Composite | 0.0302 | 0.4832 | 53.6652 | 2000 | 1850 | 1597 | 1850
GREN41 | STAY41 | 101.832 | 0 | OHL | 0.1852 | 2.0259 | 59.0223 | 2510 | 2321.75 | 2004.235 | 2321.75
GREN41 | SUND41 | 39.75 | 0 | OHL | 0.0723 | 0.7909 | 23.0368 | 2010 | 1859.25 | 1604.985 | 1859.25
GREN41 | SUND42 | 39.955 | 0 | OHL | 0.0727 | 0.795 | 23.1553 | 2010 | 1859.25 | 1604.985 | 1859.25
GRIW41 | KEAD41 | 49.379 | 0 | OHL | 0.047 | 0.873 | 32.3362 | 3070 | 2839.75 | 2451.395 | 2839.75
GRIW41 | SHBA41 | 12.673 | 0 | OHL | 0.0127 | 0.2284 | 8.1498 | 2860 | 2645.5 | 2283.71 | 2645.5
GRSA21 | LACK2A | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1100 | 1017.5 | 878.35 | 1017.5
GRSA21 | LACK2B | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1130 | 1045.25 | 902.305 | 1045.25
GRSA21 | WILT2A | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 925 | 798.5 | 925
GRSA21 | WILT2B | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 925 | 798.5 | 925
GRSB21 | LACK21 | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1130 | 1045.25 | 902.305 | 1045.25
GRSB21 | LACK2B | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1130 | 1045.25 | 902.305 | 1045.25
GRSB21 | WILT2C | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 925 | 798.5 | 925
GRSB21 | WILT2D | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 925 | 798.5 | 925
GWYN4* | BODE41 | 0 | 0.8 | Cable | 0.0008 | 0.0094 | 7.6404 | 1060 | 980.5 | 846.41 | 980.5
GWYN4* | BODE41 | 0.5 | 0 | OHL | 0.0005 | 0.0087 | 0.3284 | 2770 | 2562.25 | 2211.845 | 2562.25
GWYN4* | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2780 | 2571.5 | 2219.83 | 2571.5
GWYN4* | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2780 | 2571.5 | 2219.83 | 2571.5
HACK21 | TOTT21 | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 955 | 883.375 | 762.5675 | 883.375
HACK22 | TOTT22 | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 955 | 883.375 | 762.5675 | 883.375
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1860 | 1720.5 | 1485.21 | 1720.5
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1860 | 1720.5 | 1485.21 | 1720.5
HAMH2A | NECH21 | 10.439 | 0 | OHL | 0.0239 | 0.3843 | 3.2511 | 1000 | 925 | 798.5 | 925
HAMH41 | WILE41 | 84.14 | 0.7 | Composite | 0.1246 | 1.582 | 77.0168 | 2010 | 1859.25 | 1604.985 | 1859.25
HARK22 | STEW21 | 83.682 | 0.117 | Composite | 0.4944 | 3.549 | 23.7211 | 775 | 716.875 | 618.8375 | 716.875
HARK41 | HAKB4- | 9.857 | 0 | OHL | 0.0179 | 0.2011 | 5.5627 | 1970 | 1822.25 | 1573.045 | 1822.25
HARK41 | HAKB4B | 9.857 | 0 | OHL | 0.0179 | 0.2011 | 5.5627 | 1970 | 1822.25 | 1573.045 | 1822.25
HARK41 | HUTT41 | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 3100 | 2867.5 | 2475.35 | 2867.5
HARK41 | HUTT41 | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 3100 | 2867.5 | 2475.35 | 2867.5
HARM21 | HAWP21 | 17.287 | 0 | OHL | 0.0584 | 0.7033 | 4.9126 | 1110 | 1026.75 | 886.335 | 1026.75
HATL21 | HARM21 | 13.983 | 0 | OHL | 0.0476 | 0.5708 | 3.9608 | 1090 | 1008.25 | 870.365 | 1008.25
HATL21 | SALH21 | 7.794 | 0 | OHL | 0.0331 | 0.3358 | 2.0838 | 1370 | 1267.25 | 1093.945 | 1267.25
HATL21 | TODP21 | 18.433 | 0 | OHL | 0.0745 | 0.7795 | 5.0197 | 1150 | 1063.75 | 918.275 | 1063.75
HATL21 | WBOL21 | 49.164 | 0 | OHL | 0.1876 | 2.0311 | 13.7303 | 1090 | 1008.25 | 870.365 | 1008.25
HAWP21 | NORT21 | 30.238 | 0.459 | Composite | 0.0719 | 1.1367 | 14.2369 | 910 | 841.75 | 726.635 | 841.75
HAWP21 | OFFE21 | 9.514 | 0 | OHL | 0.0435 | 0.4027 | 2.5811 | 1090 | 1008.25 | 870.365 | 1008.25
HAWP4A | NORT41 | 30.157 | 0 | OHL | 0.0335 | 0.531 | 19.6771 | 1000 | 925 | 798.5 | 925
HEDD4A | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3330 | 3080.25 | 2659.005 | 3080.25
HEDD4A | STWB4Q | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 2770 | 2562.25 | 2211.845 | 2562.25
HEDD4B | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3330 | 3080.25 | 2659.005 | 3080.25
HEDD4B | STWB4R | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 2770 | 2562.25 | 2211.845 | 2562.25
HEDO21 | SAES21 | 0.605 | 0 | OHL | 0.0017 | 0.0226 | 0.1876 | 1750 | 1618.75 | 1397.375 | 1618.75
HEYS41 | HAMB4A | 25.85 | 0 | OHL | 0.0229 | 0.444 | 17.3733 | 3330 | 3080.25 | 2659.005 | 3080.25
HEYS41 | HAMB4B | 26.02 | 0 | OHL | 0.0231 | 0.4469 | 17.4871 | 3330 | 3080.25 | 2659.005 | 3080.25
HEYS41 | QUER4A | 9.604 | 0 | OHL | 0.0085 | 0.165 | 6.4553 | 3330 | 3080.25 | 2659.005 | 3080.25
HEYS41 | QUER4B | 9.604 | 0 | OHL | 0.0085 | 0.165 | 6.4553 | 3330 | 3080.25 | 2659.005 | 3080.25
HIGM2* | HIGM21 | 0 | 0 | Series Reactor | 0.0115 | 1.0115 | 0 | 750 | 693.75 | 598.875 | 693.75
HIGM21 | THUR2A | 46.867 | 0 | OHL | 0.492 | 1.9585 | 12.7959 | 625 | 578.125 | 499.0625 | 578.125
HIGM41 | WBUR41 | 14.852 | 0.229 | Composite | 0.0241 | 0.291 | 17.0241 | 2210 | 2044.25 | 1764.685 | 2044.25
HIGM4A | STOB41 | 39.671 | 0 | OHL | 0.0722 | 0.7893 | 22.991 | 2150 | 1988.75 | 1716.775 | 1988.75
HINP21 | BRWA2B | 17.867 | 0.68 | Composite | 0.0828 | 0.7752 | 12.2388 | 240 | 222 | 191.64 | 222
HINP22 | BRWA2A | 17.867 | 0.61 | Composite | 0.0827 | 0.7732 | 11.4779 | 240 | 222 | 191.64 | 222
HINP41 | MELK41 | 86.439 | 0 | OHL | 0.1572 | 1.7198 | 50.0946 | 2010 | 1859.25 | 1604.985 | 1859.25
HINP41 | MELK41 | 86.448 | 0 | OHL | 0.1573 | 1.72 | 50.0998 | 2010 | 1859.25 | 1604.985 | 1859.25
HINP41 | TAUN41 | 26.644 | 0 | OHL | 0.0485 | 0.5301 | 15.4408 | 2210 | 2044.25 | 1764.685 | 2044.25
HINP41 | TAUN42 | 26.657 | 0 | OHL | 0.0485 | 0.5304 | 15.4483 | 2210 | 2044.25 | 1764.685 | 2044.25
HUMR41 | GART4A | 37.372 | 0 | OHL | 0.0413 | 0.7015 | 23.0779 | 3160 | 2923 | 2523.26 | 2923
HUMR41 | KILL41 | 2.879 | 0 | OHL | 0.0032 | 0.0543 | 1.7706 | 2770 | 2562.25 | 2211.845 | 2562.25
HURS21 | LITT2A | 5.164 | 2.613 | Composite | 0.0288 | 0.2786 | 27.8693 | 865 | 800.125 | 690.7025 | 800.125
HURS21 | LITT2B | 5.14 | 2.659 | Composite | 0.0288 | 0.2786 | 28.329 | 865 | 800.125 | 690.7025 | 800.125
HURS21 | NEWX21 | 0 | 21.106 | Cable | 0.0422 | 0.4833 | 213.8038 | 890 | 823.25 | 710.665 | 823.25
HURS21 | NEWX21 | 0 | 21.737 | Cable | 0.0435 | 0.4978 | 220.1958 | 890 | 823.25 | 710.665 | 823.25
HUTT41 | QUER4A | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3100 | 2867.5 | 2475.35 | 2867.5
HUTT41 | QUER4B | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3100 | 2867.5 | 2475.35 | 2867.5
IMPP41 | MELK41 | 78.775 | 3.913 | Composite | 0.0882 | 1.4129 | 130.2038 | 1420 | 1313.5 | 1133.87 | 1313.5
INDQ41 | LAND41 | 49.565 | 0 | OHL | 0.1069 | 0.9921 | 28.4755 | 1390 | 1285.75 | 1109.915 | 1285.75
INDQ41 | LAND42 | 49.565 | 0 | OHL | 0.1069 | 0.9921 | 28.4755 | 1390 | 1285.75 | 1109.915 | 1285.75
IROA21 | MELK21 | 33.258 | 0.951 | Composite | 0.1854 | 1.7471 | 15.541 | 580 | 536.5 | 463.13 | 536.5
IROA21 | MELK2A | 33.258 | 0.38 | Composite | 0.1838 | 1.7357 | 10.6817 | 580 | 536.5 | 463.13 | 536.5
IROA21 | WHSO2A | 34.621 | 0 | OHL | 0.2033 | 1.4667 | 9.4554 | 750 | 693.75 | 598.875 | 693.75
IROA21 | WHSO2B | 34.555 | 0 | OHL | 0.2034 | 1.4638 | 9.4375 | 750 | 693.75 | 598.875 | 693.75
IRON41 | LEGA41 | 62.073 | 0 | OHL | 0.0992 | 1.1938 | 37.326 | 2000 | 1850 | 1597 | 1850
IRON41 | PENN41 | 24.617 | 0 | OHL | 0.049 | 0.4912 | 14.2057 | 1000 | 925 | 798.5 | 925
IRON41 | PENN42 | 27.761 | 0 | OHL | 0.0574 | 0.5549 | 15.9847 | 1000 | 925 | 798.5 | 925
IRON41 | RUGE41 | 58.681 | 0 | OHL | 0.1135 | 1.1701 | 33.9042 | 1390 | 1285.75 | 1109.915 | 1285.75
IRON41 | SHRE4A | 15.129 | 0 | OHL | 0.0242 | 0.291 | 9.0974 | 2400 | 2220 | 1916.4 | 2220
IVER21 | NHYD2A | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 420 | 388.5 | 335.37 | 388.5
IVER21 | WWEY22 | 25.652 | 0.342 | Composite | 0.0975 | 1.059 | 10.9579 | 960 | 888 | 766.56 | 888
IVER22 | NHYD2B | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 420 | 388.5 | 335.37 | 388.5
IVER22 | WATS21 | 13.881 | 0.483 | Composite | 0.0643 | 0.601 | 9.0158 | 775 | 716.875 | 618.8375 | 716.875
IVER22 | WATS22 | 13.881 | 0.436 | Composite | 0.0642 | 0.5997 | 8.5049 | 775 | 716.875 | 618.8375 | 716.875
IVER2A | LALE21 | 17.186 | 0.402 | Composite | 0.0656 | 0.7143 | 9.2206 | 595 | 550.375 | 475.1075 | 550.375
JORD21 | NORL21 | 0 | 2.843 | Cable | 0.0109 | 0.0719 | 20.1177 | 420 | 388.5 | 335.37 | 388.5
KEAD41 | GART4B | 5.689 | 0 | OHL | 0.0062 | 0.0989 | 3.7497 | 3180 | 2941.5 | 2539.23 | 2941.5
KEAD41 | KEAP41 | 0.321 | 0 | OHL | 0.0007 | 0.0066 | 0.179 | 1710 | 1581.75 | 1365.435 | 1581.75
KEAD42 | GART4A | 5.711 | 0 | OHL | 0.0062 | 0.0993 | 3.7642 | 3180 | 2941.5 | 2539.23 | 2941.5
KEAD42 | KILL41 | 41.067 | 0 | OHL | 0.0403 | 0.7345 | 26.6033 | 3060 | 2830.5 | 2443.41 | 2830.5
KEAD42 | WBUR41 | 28.266 | 0 | OHL | 0.0307 | 0.4916 | 18.6331 | 3330 | 3080.25 | 2659.005 | 3080.25
KEAD43 | FENW4A | 42.517 | 0 | parallel OHL | 0.0198 | 0.2161 | 24.6399 | 3070 | 2839.75 | 2451.395 | 2839.75
KEAD43 | KEAP42 | 0.433 | 0.42 | Composite | 0.0013 | 0.0151 | 7.1841 | 1710 | 1581.75 | 1365.435 | 1581.75
KEAD43 | WBUR42 | 28.425 | 0 | OHL | 0.0308 | 0.4944 | 18.7376 | 2780 | 2571.5 | 2219.83 | 2571.5
KEAR21 | WHGA21 | 14.509 | 0.129 | Composite | 0.0665 | 0.6177 | 5.3384 | 830 | 767.75 | 662.755 | 767.75
KEAR21 | WHGA21 | 14.509 | 0.241 | Composite | 0.0667 | 0.6208 | 6.5558 | 835 | 772.375 | 666.7475 | 772.375
KEAR41 | PADI41 | 39.101 | 0 | OHL | 0.0567 | 0.7296 | 24.2055 | 2170 | 2007.25 | 1732.745 | 2007.25
KEMS41 | CANT41 | 28.2 | 0 | OHL | 0.0439 | 0.5411 | 16.9228 | 3100 | 2867.5 | 2475.35 | 2867.5
KEMS41 | LOFI4A | 38.035 | 0 | OHL | 0.0721 | 0.7367 | 22.6825 | 1930 | 1785.25 | 1541.105 | 1785.25
KEMS41 | LOFI4B | 37.572 | 0 | OHL | 0.0717 | 0.7289 | 22.3721 | 1930 | 1785.25 | 1541.105 | 1785.25
KIBY21 | LISD21 | 0 | 10.239 | Cable | 0.0173 | 0.2966 | 60.8154 | 760 | 703 | 606.86 | 703
KIBY21 | LISD21 | 0 | 9.518 | Cable | 0.0228 | 0.2008 | 86.3283 | 760 | 703 | 606.86 | 703
KIBY21 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1420 | 1313.5 | 1133.87 | 1313.5
KIBY21 | WASF22 | 10.978 | 0 | OHL | 0.0415 | 0.4491 | 3.0984 | 1520 | 1406 | 1213.72 | 1406
KIBY22 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1380 | 1276.5 | 1101.93 | 1276.5
KIBY22 | WASF21 | 10.945 | 0 | OHL | 0.0414 | 0.4478 | 3.0891 | 1520 | 1406 | 1213.72 | 1406
KILL41 | SHBA41 | 17.05 | 0 | OHL | 0.0179 | 0.3134 | 10.7556 | 2860 | 2645.5 | 2283.71 | 2645.5
KINO41 | KINO41 | 0 | 0 | Series Reactor | 0.0027 | 2 | 0 | 2000 | 1850 | 1597 | 1850
KINO41 | NFLE41 | 23.626 | 0 | OHL | 0.0284 | 0.4216 | 15.2234 | 3100 | 2867.5 | 2475.35 | 2867.5
KINO41 | TILB41 | 15.4784 | 1.835 | Composite | 0.0181 | 0.2893 | 46.9053 | 2000 | 1850 | 1597 | 1850
KIRK2A | SKLG21 | 0 | 8.608 | Cable | 0.0146 | 0.2402 | 93.5689 | 760 | 703 | 606.86 | 703
KITW21 | OCKH21 | 13.738 | 0.222 | Composite | 0.0525 | 0.5743 | 6.2479 | 770 | 712.25 | 614.845 | 712.25
KITW21 | OLDB21 | 7.704 | 0.597 | Composite | 0.0301 | 0.3318 | 8.6639 | 665 | 615.125 | 531.0025 | 615.125
LACK21 | TODP21 | 5.965 | 0 | OHL | 0.0197 | 0.2454 | 1.6695 | 1150 | 1063.75 | 918.275 | 1063.75
LACK41 | NORT41 | 22.443 | 0.25 | Composite | 0.0411 | 0.4523 | 17.404 | 1830 | 1692.75 | 1461.255 | 1692.75
LACK41 | THTO41 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2420 | 2238.5 | 1932.37 | 2238.5
LACK41 | THTO42 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2420 | 2238.5 | 1932.37 | 2238.5
LAKE4* | TILB41 | 13.0448 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2830 | 2617.75 | 2259.755 | 2617.75
LAKE4* | WTHU4E | 2.4188 | 0 | OHL | 0.0038 | 0.0488 | 1.378 | 1940 | 1794.5 | 1549.09 | 1794.5
LAKE4B | TILB41 | 13.0448 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2890 | 2673.25 | 2307.665 | 2673.25
LAKE4B | WTHU4D | 2.5806 | 0 | OHL | 0.004 | 0.0519 | 1.4744 | 1940 | 1794.5 | 1549.09 | 1794.5
LALE21 | WWEY2* | 8.395 | 0 | OHL | 0.0317 | 0.3434 | 2.3695 | 750 | 693.75 | 598.875 | 693.75
LAND41 | LAGA41 | 21.224 | 0 | OHL | 0.0457 | 0.4249 | 12.1895 | 1390 | 1285.75 | 1109.915 | 1285.75
LAND42 | LAGA41 | 21.355 | 0 | OHL | 0.046 | 0.4275 | 12.2646 | 1390 | 1285.75 | 1109.915 | 1285.75
LEGA41 | SHRE4A | 46.944 | 0 | OHL | 0.075 | 0.9028 | 28.2286 | 2000 | 1850 | 1597 | 1850
LEGA41 | TREU4A | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2645.5 | 2283.71 | 2645.5
LEGA41 | TREU4B | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2645.5 | 2283.71 | 2645.5
LEIB4A | SUND42 | 13.428 | 0 | OHL | 0.0119 | 0.2306 | 9.025 | 2780 | 2571.5 | 2219.83 | 2571.5
LEIB4B | SUND41 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0431 | 2780 | 2571.5 | 2219.83 | 2571.5
LISD21 | LISD2* | 0 | 0 | Series Reactor | 0.0173 | 1.387 | 0 | 750 | 693.75 | 598.875 | 693.75
LITT41 | LITT41 | 0 | 0.1 | Cable | 0 | 0 | 0 | 1440 | 1332 | 1149.84 | 1332
LITT41 | LITT41 | 0 | 0.045 | Cable | 0 | 0 | 2.0018 | 3390 | 3135.75 | 2706.915 | 3135.75
LITT41 | LOFI4A | 8.152 | 0 | OHL | 0.0176 | 0.1632 | 4.6834 | 1390 | 1285.75 | 1109.915 | 1285.75
LITT41 | LOFI4B | 8.152 | 0 | OHL | 0.0176 | 0.1632 | 4.6834 | 1390 | 1285.75 | 1109.915 | 1285.75
LITT41 | WTHU4D | 1.801 | 1.853 | Composite | 0.0041 | 0.0566 | 21.302 | 1940 | 1794.5 | 1549.09 | 1794.5
LITT41 | WTHU4E | 1.8467 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3293 | 1940 | 1794.5 | 1549.09 | 1794.5
LOFI4A | ROWD42 | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3474 | 1590 | 1470.75 | 1269.615 | 1470.75
LOFI4B | ROWD41 | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3474 | 1590 | 1470.75 | 1269.615 | 1470.75
LOVE41 | NURS41 | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2770 | 2562.25 | 2211.845 | 2562.25
LOVE41 | NURS4A | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2780 | 2571.5 | 2219.83 | 2571.5
MACC41 | STAL41 | 31.196 | 0 | OHL | 0.0673 | 0.6244 | 17.9212 | 1710 | 1581.75 | 1365.435 | 1581.75
MAGA21 | PYLE21 | 6.238 | 0 | OHL | 0.0211 | 0.2537 | 1.7667 | 1200 | 1110 | 958.2 | 1110
MANN41 | NURS4A | 39.823 | 0 | OHL | 0.043 | 0.6631 | 27.5672 | 2780 | 2571.5 | 2219.83 | 2571.5
MAWO41 | NURS41 | 7.441 | 0 | OHL | 0.0093 | 0.1281 | 5.0417 | 2420 | 2238.5 | 1932.37 | 2238.5
MELK41 | MITY41 | 28.101 | 0 | OHL | 0.0511 | 0.5591 | 16.2853 | 2110 | 1951.75 | 1684.835 | 1951.75
MELK41 | MITY41 | 28.052 | 0 | OHL | 0.051 | 0.5581 | 16.257 | 2110 | 1951.75 | 1684.835 | 1951.75
MELK41 | SEAB41 | 53.558 | 0 | OHL | 0.0598 | 0.9451 | 34.8897 | 2550 | 2358.75 | 2036.175 | 2358.75
MONF21 | POPP21 | 37.709 | 0.141 | Composite | 0.357 | 1.6584 | 11.1383 | 460 | 425.5 | 367.31 | 425.5
MONF22 | POPP21 | 37.826 | 0 | OHL | 0.3573 | 1.6617 | 9.9645 | 550 | 508.75 | 439.175 | 508.75
MONF41 | PADI41 | 87.848 | 0 | OHL | 0.1064 | 1.6286 | 54.7416 | 2520 | 2331 | 2012.22 | 2331
NEEP21 | PITS21 | 0.851 | 3.975 | Composite | 0.0214 | 0.1378 | 26.8236 | 420 | 388.5 | 335.37 | 388.5
NEEP21 | SHEC21 | 0.851 | 4.428 | Composite | 0.0234 | 0.1494 | 29.8542 | 420 | 388.5 | 335.37 | 388.5
NEEP4A | STSB41 | 12.801 | 0 | OHL | 0.0276 | 0.2627 | 7.1402 | 750 | 693.75 | 598.875 | 693.75
NEWX21 | NEWX21 | 0 | 0.15 | Cable | 0.0003 | 0.0034 | 1.5195 | 1140 | 1054.5 | 910.29 | 1054.5
NEWX21 | WIMB21 | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 825 | 763.125 | 658.7625 | 763.125
NEWX21 | WIMB21 | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 820 | 758.5 | 654.77 | 758.5
NFLE41 | WTHU4* | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2000 | 1850 | 1597 | 1850
NFLE41 | WTHU4A | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2000 | 1850 | 1597 | 1850
NORL21 | PITS21 | 0 | 10.751 | Cable | 0.0473 | 0.2752 | 71.9242 | 420 | 388.5 | 335.37 | 388.5
NORL22 | SHEC21 | 0 | 4.372 | Cable | 0.0192 | 0.1119 | 29.2487 | 420 | 388.5 | 335.37 | 388.5
NORM41 | WALP41 | 79.138 | 0 | OHL | 0.0702 | 1.3593 | 53.1914 | 3510 | 3246.75 | 2802.735 | 3246.75
NORM41 | WALP41 | 79.046 | 0 | OHL | 0.0701 | 1.3577 | 53.1298 | 3100 | 2867.5 | 2475.35 | 2867.5
NORT22 | SALH21 | 12.178 | 0 | OHL | 0.0464 | 0.526 | 3.2482 | 1370 | 1267.25 | 1093.945 | 1267.25
NORT41 | OSBA41 | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2010 | 1859.25 | 1604.985 | 1859.25
NORT41 | OSBA42 | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2010 | 1859.25 | 1604.985 | 1859.25
NORT41 | SPEN41 | 21.134 | 2 | Composite | 0.0276 | 0.4066 | 12.7287 | 2550 | 2358.75 | 2036.175 | 2358.75
NORT41 | SPEN42 | 21.134 | 2 | Composite | 0.0276 | 0.4066 | 12.7287 | 2550 | 2358.75 | 2036.175 | 2358.75
OCKH21 | WIEN2* | 4.623 | 0.283 | Composite | 0.0216 | 0.202 | 4.2819 | 240 | 222 | 191.64 | 222
OCKH2A | WIEN21 | 4.67 | 0 | OHL | 0.0213 | 0.1977 | 1.2665 | 955 | 883.375 | 762.5675 | 883.375
OFFE21 | WBOL21 | 8.207 | 0 | OHL | 0.0375 | 0.3474 | 2.2265 | 1090 | 1008.25 | 870.365 | 1008.25
OSBA41 | THTO43 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2780 | 2571.5 | 2219.83 | 2571.5
OSBA42 | THTO41 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2770 | 2562.25 | 2211.845 | 2562.25
PADI41 | PEWO41 | 37.608 | 0 | OHL | 0.0556 | 0.7049 | 23.1778 | 2170 | 2007.25 | 1732.745 | 2007.25
PELH41 | RYEH4A | 23.015 | 0 | OHL | 0.025 | 0.4003 | 15.1704 | 2780 | 2571.5 | 2219.83 | 2571.5
PELH41 | RYEH4B | 23.439 | 0 | OHL | 0.0254 | 0.4077 | 15.4489 | 2780 | 2571.5 | 2219.83 | 2571.5
PELH41 | SUND42 | 45.13 | 0 | OHL | 0.0487 | 0.752 | 31.2185 | 3180 | 2941.5 | 2539.23 | 2941.5
PELH41 | WYMO41 | 26.856 | 0 | OHL | 0.029 | 0.4469 | 18.6034 | 2770 | 2562.25 | 2211.845 | 2562.25
PEMB41 | SWAN42 | 84.57 | 0 | OHL | 0.0918 | 1.4709 | 55.7496 | 2780 | 2571.5 | 2219.83 | 2571.5
PEMB41 | WALH41 | 218.076 | 5.468 | parallel Composite | 0.2375 | 3.8124 | 207.646 | 2780 | 2571.5 | 2219.83 | 2571.5
PENT41 | TRAW41 | 45.1 | 6.308 | Composite | 0.0634 | 0.9563 | 131.5194 | 1130 | 1045.25 | 902.305 | 1045.25
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2780 | 2571.5 | 2219.83 | 2571.5
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2780 | 2571.5 | 2219.83 | 2571.5
PEWO21 | WASF22 | 23.521 | 0 | OHL | 0.0889 | 0.9623 | 6.6386 | 1520 | 1406 | 1213.72 | 1406
PEWO22 | WASF21 | 23.481 | 0 | OHL | 0.0887 | 0.9606 | 6.6274 | 1520 | 1406 | 1213.72 | 1406
PEWO41 | HAMB4A | 19.698 | 0.752 | parallel Composite | 0.0308 | 0.3917 | 24.9792 | 2470 | 2284.75 | 1972.295 | 2284.75
PEWO41 | HAMB4B | 19.698 | 0.592 | parallel Composite | 0.0308 | 0.3911 | 20.9006 | 2470 | 2284.75 | 1972.295 | 2284.75
PITS21 | TEMP21 | 0 | 6.69 | Cable | 0.0294 | 0.1713 | 44.7561 | 420 | 388.5 | 335.37 | 388.5
PITS21 | WIBA21 | 0 | 2.324 | Cable | 0.0077 | 0.0581 | 17.337 | 440 | 407 | 351.34 | 407
PYLE21 | PYLE21 | 0 | 0.1 | Cable | 0.0001 | 0.0025 | 0.676 | 525 | 485.625 | 419.2125 | 485.625
PYLE21 | PYLE21 | 0 | 0.25 | Cable | 0.0004 | 0.0063 | 1.69 | 525 | 485.625 | 419.2125 | 485.625
QUER4A | PEWO41 | 31.939 | 0 | OHL | 0.0498 | 0.6128 | 19.1665 | 3100 | 2867.5 | 2475.35 | 2867.5
QUER4B | PEWO41 | 32.087 | 0 | OHL | 0.05 | 0.6156 | 19.2551 | 3100 | 2867.5 | 2475.35 | 2867.5
RASS41 | WALH41 | 72.788 | 5.269 | parallel Composite | 0.0799 | 1.2847 | 109.6583 | 2780 | 2571.5 | 2219.83 | 2571.5
RATS41 | STAY4A | 43.614 | 0 | OHL | 0.0793 | 0.8678 | 25.2762 | 2150 | 1988.75 | 1716.775 | 1988.75
RATS41 | WILE41 | 21.748 | 0.216 | Composite | 0.0397 | 0.435 | 16.174 | 1310 | 1211.75 | 1046.035 | 1211.75
RATS42 | STOB41 | 26.72 | 0.179 | Composite | 0.0487 | 0.5326 | 21.4031 | 2150 | 1988.75 | 1716.775 | 1988.75
RATS42 | WILE41 | 21.684 | 0 | OHL | 0.0394 | 0.4314 | 12.5666 | 2010 | 1859.25 | 1604.985 | 1859.25
RAYL41 | TILB4A | 20.499 | 0 | OHL | 0.0319 | 0.3933 | 12.3014 | 2890 | 2673.25 | 2307.665 | 2673.25
REBR21 | TOTT22 | 3.305 | 11.448 | parallel Composite | 0.0174 | 0.2151 | 125.3726 | 1210 | 1119.25 | 966.185 | 1119.25
REBR22 | TOTT21 | 3.305 | 9.678 | parallel Composite | 0.0166 | 0.2027 | 106.1327 | 1210 | 1119.25 | 966.185 | 1119.25
ROCH21 | STAL21 | 31.256 | 0 | OHL | 0.1235 | 1.3183 | 8.54 | 1320 | 1221 | 1054.02 | 1221
ROCH21 | WHGA21 | 11.489 | 0.238 | Composite | 0.0529 | 0.4929 | 5.7034 | 905 | 837.125 | 722.6425 | 837.125
ROCH21 | WHGA21 | 11.489 | 0.257 | Composite | 0.053 | 0.4934 | 5.9099 | 840 | 777 | 670.74 | 777
RYEH4* | RYEH4A | 0.264 | 0 | OHL | 0.0006 | 0.0053 | 0.1512 | 1710 | 1581.75 | 1365.435 | 1581.75
RYEH4* | RYEH4B | 0.215 | 0 | OHL | 0.0005 | 0.0043 | 0.1232 | 1710 | 1581.75 | 1365.435 | 1581.75
RYEH41 | RYEH4B | 0.137 | 0 | OHL | 0.0001 | 0.0024 | 0.0903 | 2780 | 2571.5 | 2219.83 | 2571.5
RYEH41 | WALX41 | 5.324 | 0 | OHL | 0.0058 | 0.0926 | 3.5096 | 2780 | 2571.5 | 2219.83 | 2571.5
RYEH4A | WALX42 | 5.461 | 0 | OHL | 0.0059 | 0.095 | 3.6 | 2780 | 2571.5 | 2219.83 | 2571.5
SAEN21 | SAES21 | 0.484 | 0 | OHL | 0.0013 | 0.018 | 0.1501 | 1520 | 1406 | 1213.72 | 1406
SEAB41 | WHSO4A | 30.426 | 3.89 | Composite | 0.0374 | 0.5858 | 97.4265 | 1420 | 1313.5 | 1133.87 | 1313.5
SELL41 | SELL41 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 1860 | 1720.5 | 1485.21 | 1720.5
SHRE4B | SHRE4A | 0.054 | 0 | OHL | 0.0001 | 0.001 | 0.0324 | 9999 | 9249.075 | 7984.2015 | 9249.075
SING41 | KINO41 | 17.685 | 0 | OHL | 0.0192 | 0.3076 | 11.6582 | 2890 | 2673.25 | 2307.665 | 2673.25
SING41 | NFLE41 | 5.941 | 0 | OHL | 0.0093 | 0.114 | 3.5652 | 2890 | 2673.25 | 2307.665 | 2673.25
SJOW21 | TOTT23 | 0 | 16.368 | Cable | 0.0295 | 0.3601 | 177.9201 | 870 | 804.75 | 694.695 | 804.75
SJOW21 | TOTT24 | 0 | 16.508 | Cable | 0.0297 | 0.3632 | 179.4419 | 870 | 804.75 | 694.695 | 804.75
SJOW2A | WISD21 | 0 | 7.399 | Cable | 0.0133 | 0.1628 | 80.4271 | 750 | 693.75 | 598.875 | 693.75
SJOW2B | WISD22 | 0 | 7.399 | Cable | 0.0133 | 0.1628 | 80.4271 | 750 | 693.75 | 598.875 | 693.75
SJOW41 | SJOW41 | 0 | 0.3 | Cable | 0.0002 | 0.0035 | 3.2746 | 240 | 222 | 191.64 | 222
SPEN41 | STEW41 | 37.795 | 0.126 | Composite | 0.0498 | 0.7386 | 24.4993 | 2470 | 2284.75 | 1972.295 | 2284.75
SPEN42 | SPEN42 | 0 | 0.131 | Cable | 0.0001 | 0.0015 | 1.4299 | 240 | 222 | 191.64 | 222
SPEN42 | STEW41 | 37.795 | 0 | OHL | 0.0497 | 0.7368 | 22.4165 | 2470 | 2284.75 | 1972.295 | 2284.75
SPLN41 | WALP41 | 29.234 | 0 | OHL | 0.0272 | 0.5117 | 19.3195 | 3190 | 2950.75 | 2547.215 | 2950.75
SSHI21 | TYNE2A | 7.028 | 0 | OHL | 0.031 | 0.2985 | 1.9072 | 1240 | 1147 | 990.14 | 1147
SSHI21 | WBOL21 | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 1090 | 1008.25 | 870.365 | 1008.25
STAH4A | HAMB4A | 3.926 | 0 | OHL | 0.0085 | 0.0806 | 2.1967 | 1710 | 1581.75 | 1365.435 | 1581.75
STAH4B | HAMB4B | 3.926 | 0 | OHL | 0.0085 | 0.0806 | 2.1967 | 1710 | 1581.75 | 1365.435 | 1581.75
STAL41 | STSB4A | 28.555 | 5.057 | Composite | 0.0343 | 0.5535 | 95.384 | 1650 | 1526.25 | 1317.525 | 1526.25
STAL42 | THOM42 | 71.245 | 4.978 | Composite | 0.0791 | 1.2942 | 122.4093 | 1330 | 1230.25 | 1062.005 | 1230.25
STEW21 | STEW21 | 0 | 0.068 | Cable | 0.0002 | 0.0014 | 0.5787 | 240 | 222 | 191.64 | 222
STEW21 | STEW21 | 0 | 0.435 | Cable | 0.0007 | 0.0116 | 2.5837 | 855 | 790.875 | 682.7175 | 790.875
STEW21 | STEW21 | 0 | 0.1 | Cable | 0.0001 | 0.0025 | 0.5159 | 1200 | 1110 | 958.2 | 1110
SUND41 | WYMO41 | 18.156 | 0 | OHL | 0.0196 | 0.302 | 12.5826 | 3050 | 2821.25 | 2435.425 | 2821.25
SUTB41 | WALP41 | 3.85 | 0 | OHL | 0.008 | 0.0773 | 2.2055 | 1450 | 1341.25 | 1157.825 | 1341.25
SWAN41 | PEMB41 | 83.975 | 0 | OHL | 0.0911 | 1.4606 | 55.3574 | 2780 | 2571.5 | 2219.83 | 2571.5
SWAN41 | PEMB41 | 84.697 | 0 | OHL | 0.0919 | 1.4731 | 55.833 | 2780 | 2571.5 | 2219.83 | 2571.5
SWAN41 | SWAN4* | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 750 | 693.75 | 598.875 | 693.75
SWAN42 | SWAN4A | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 750 | 693.75 | 598.875 | 693.75
TEMP22 | WIBA21 | 0 | 3.607 | Cable | 0.0159 | 0.0923 | 24.1308 | 420 | 388.5 | 335.37 | 388.5
THOM21 | WMEL21 | 24.346 | 0.947 | Composite | 0.113 | 1.0789 | 16.0317 | 765 | 707.625 | 610.8525 | 707.625
THOM4* | WMEL21 | 24.413 | 0.8 | Composite | 0.1126 | 1.0793 | 10.588 | 765 | 707.625 | 610.8525 | 707.625
THOM42 | BRIN41 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2520 | 2331 | 2012.22 | 2331
THUR2A | THUR21 | 4.653 | 0 | OHL | 0.0488 | 0.1944 | 1.2745 | 550 | 508.75 | 439.175 | 508.75
THUR2A | WMEL21 | 16.348 | 0 | OHL | 0.0746 | 0.7099 | 4.3235 | 955 | 883.375 | 762.5675 | 883.375
TILB21 | WARL21 | 13.065 | 0 | OHL | 0.0597 | 0.553 | 3.5441 | 1180 | 1091.5 | 942.23 | 1091.5
TILB22 | WARL21 | 12.897 | 0 | OHL | 0.059 | 0.5459 | 3.4987 | 1120 | 1036 | 894.32 | 1036
TILB41 | TILB4B | 0.0589 | 0 | OHL | 0.0001 | 0.0011 | 0.0353 | 3100 | 2867.5 | 2475.35 | 2867.5
TILB4A | TILB41 | 0.05808 | 0 | OHL | 0.0001 | 0.0012 | 0.033 | 3100 | 2867.5 | 2475.35 | 2867.5
TRAW41 | TREU4A | 64.278 | 0 | OHL | 0.1001 | 1.2332 | 38.5742 | 3100 | 2867.5 | 2475.35 | 2867.5
TRAW41 | TREU4B | 64.278 | 0 | OHL | 0.1001 | 1.2332 | 38.5742 | 3100 | 2867.5 | 2475.35 | 2867.5
TREM21 | USKM23 | 15.048 | 0 | OHL | 0.0854 | 0.7095 | 3.7487 | 695 | 642.875 | 554.9575 | 642.875
TYNE21 | WBOL21 | 11.399 | 0 | OHL | 0.051 | 0.4835 | 3.093 | 1090 | 1008.25 | 870.365 | 1008.25
USKM21 | USKM23 | 0.692 | 0 | OHL | 0.0038 | 0.036 | 0.1546 | 695 | 642.875 | 554.9575 | 642.875
USKM21 | WHSO21 | 5.841 | 0 | OHL | 0.0345 | 0.2401 | 1.6394 | 1010 | 934.25 | 806.485 | 934.25
USKM21 | WHSO22 | 5.849 | 0 | OHL | 0.0345 | 0.2405 | 1.6417 | 1010 | 934.25 | 806.485 | 934.25
USKM22 | USKM21 | 0.391 | 0 | OHL | 0.0039 | 0.0167 | 0.1052 | 680 | 629 | 542.98 | 629
USKM22 | WHSO22 | 5.851 | 0 | OHL | 0.0322 | 0.304 | 1.3103 | 680 | 629 | 542.98 | 629
USKM23 | WHSO21 | 5.562 | 0 | OHL | 0.0306 | 0.289 | 1.2455 | 695 | 642.875 | 554.9575 | 642.875
WBUR41 | WBUR42 | 0 | 0 | Series Reactor | 0.0026 | 2.3169 | 0 | 1500 | 1387.5 | 1197.75 | 1387.5
WHSO41 | WHSO4A | 0.077 | 0 | OHL | 0.0001 | 0.0013 | 0.0506 | 3420 | 3163.5 | 2730.87 | 3163.5
WIMB21 | WISD2B | 0 | 20.669 | Cable | 0.0413 | 0.4733 | 209.377 | 740 | 684.5 | 590.89 | 684.5
WTHU4D | WTHU4D | 0 | 0 | Series Reactor | 0 | 1 | 0 | 1940 | 1794.5 | 1549.09 | 1794.5
WTHU4E | WTHU4E | 0 | 0 | Series Reactor | 0 | 1 | 0 | 1940 | 1794.5 | 1549.09 | 1794.5

## B-2-1d
Table B.2.1d - Offshore Transmission Circuits 2014/15 | [10 empty] | Back To Menu
OFTO | Node 1 | Node 2 | Voltage (kV) | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA)
TC Barrow OFTO Limited | BOSW1* | BOSW1* | 132 | 0 | 26.9 | Cable | 1.544 | 2.161 | 22.087 | 126
TC Barrow OFTO Limited | BOSW1* | HEYS1* | 132 | 0 | 2.633 | Cable | 0.074 | 0.219 | 2.292 | 128
- | GGON1* | IGOF1* | 132 | 0 | 45 | Cable | 1.02 | 3.0599 | 1.776 | 180
- | GGON1* | IGOF1* | 132 | 0 | 45.165 | Cable | 1.0234 | 3.0701 | 1.782 | 180
- | IGOF1* | IGOF1* | 132 | 0 | 17 | Cable | 0.36 | 1.07 | 0.6224 | 300
- | IGOF1* | GGON1* | 132 | 0 | 45 | Cable | 1.02 | 3.0599 | 1.776 | 180
TC Gunfleet Sands OFTO Ltd | GUNS1* | GUNS3* | 132 | 0 | 3.8 | Cable | 0.0653 | 0.3483 | 4.5678 | 182
TC Gunfleet Sands OFTO Ltd | GUNS1* | GUNS3* | 132 | 0 | 7.5 | Cable | 0.2656 | 0.478 | 11.2974 | 182
- | GWYN1* | GWYN11 | 132 | 0 | 1 | Cable | 1.15 | 2.88 | 34.8 | 228.6307
- | GWYN1* | GWYN12 | 132 | 0 | 1 | Cable | 0.0149 | 0.0854 | 45.3026 | 450
- | GWYN11 | GWYN1* | 132 | 0 | 1 | Cable | 0.0149 | 0.0854 | 45.3026 | 450
- | GWYN11 | GWYN1* | 132 | 0 | 1 | Cable | 1.15 | 2.88 | 34.8 | 228.6307
- | GWYN11 | GWYN1* | 132 | 0 | 1 | Cable | 1.15 | 2.88 | 34.8 | 228.6307
- | GWYN11 | GWYN1* | 132 | 0 | 1 | Cable | 1.15 | 2.88 | 34.8 | 330
- | GWYN12 | GWYN1* | 132 | 0 | 1 | Cable | 1.15 | 2.88 | 34.8 | 228.6307
- | GWYN12 | GWYN1* | 132 | 0 | 1 | Cable | 1.15 | 2.88 | 34.8 | 330
- | HEDN1* | WERW8* | 132 | 0 | 25 | Cable | 1.0761 | 1.9657 | 19.4324 | 94
- | HEDN1* | WERW8* | 132 | 0 | 25 | Cable | 1.0761 | 1.9657 | 19.4324 | 94
- | HUMG81 | HUMG81 | 132 | 0 | 36 | Cable | 0.3276 | 3.6108 | 80.4564 | 200
- | HUMG82 | HUMG82 | 132 | 0 | 36 | Cable | 0.3276 | 3.6108 | 80.4564 | 200
- | LONO1* | LOAW1* | 150 | 0 | 53.798 | Cable | 1.65 | 3.11 | 63.06 | 779
- | LONO1* | LOAW1* | 150 | 0 | 53.848 | Cable | 1.65 | 3.11 | 63.06 | 1000
- | LONO1* | LOAW1* | 150 | 0 | 52.657 | Cable | 1.61 | 3.04 | 61.68 | 1000
- | LONO1* | LOAW1* | 150 | 0 | 52.682 | Cable | 1.61 | 3.04 | 61.68 | 1000
- | LOAW3* | LOAW3* | 150 | 0 | 53 | Cable | 1.61 | 3.04 | 61.68 | 1000
- | LOAW3* | LOAW3* | 150 | 0 | 53 | Cable | 1.61 | 3.04 | 61.68 | 1000
TC Ormonde OFTO Ltd | ORMO8* | HEYS11 | 132 | 0 | 3.1 | Cable | 0.0694 | 0.2153 | 4.0556 | 165
TC Ormonde OFTO Ltd | ORMO8* | ORMO8* | 132 | 0 | 43 | Cable | 1.382 | 2.9614 | 48.9587 | 165
TC Robin Rigg OFTO Ltd | RORE1* | RREW1* | 132 | 0 | 14.3 | Cable | 0.3632 | 0.5992 | 22.2551 | 136
TC Robin Rigg OFTO Ltd | RORW1* | RRWW1* | 132 | 0 | 14.3 | Cable | 0.3632 | 0.5992 | 22.2551 | 136
Blue Transmission Sheringham Shoal Ltd | SHSW1* | SHSW1* | 132 | 0 | 22 | Cable | 0.40404 | 1.7929 | 0.00099909 | 360
Blue Transmission Sheringham Shoal Ltd | SHSW1* | SHSW1* | 132 | 0 | 0.4 | Cable | 0.012397 | 0.025253 | 1.73e-05 | 360
Blue Transmission Sheringham Shoal Ltd | SHSW1* | SHSW1* | 132 | 0 | 22.4 | Cable | 0.80992 | 1.5427 | 0.00080735 | 360
Blue Transmission Walney 1 Ltd | WAAW8* | HEYS11 | 132 | 0 | 47.5 | Cable | 1.3699 | 2.4667 | 58.612 | 204
Blue Transmission Walney 2 Ltd | WABW8* | STAH11 | 132 | 0 | 50 | Cable | 1.442 | 2.5965 | 61.6968 | 183
- | WODS8* | WODS1* | 132 | 0 | 2 | Cable | 0.663 | 1.9978 | 69.3823 | 268.4679
- | WODS8* | WODS1* | 132 | 0 | 2 | Cable | 0.663 | 1.9978 | 69.3823 | 268.4679
- | WODS8* | WODS1* | 132 | 0 | 30 | Cable | 0.6221 | 1.4692 | 153.2695 | 250
- | WODS8* | WODS1* | 132 | 0 | 30 | Cable | 0.6221 | 1.4692 | 153.2695 | 250

## B-2-2a
Table B.2.2a - SHE Transmission Circuit Changes 2015/16 to 2023/24 | [13 empty] | Back To Menu
Node 1 | Node 2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Winter Rating (MVA) | Autumn Rating (MVA) | Summer Rating (MVA) | Spring Rating (MVA)
BEAU1J | DUCC1J | 2015 | Addition | 0 | 3.2 | Cable | 0.0226 | 0.1238 | 10.818 | 444.0008 | 410.7008 | 354.5347 | 410.7008
BEAU1K | DUCC1K | 2015 | Addition | 0 | 3.2 | Cable | 0.0226 | 0.1238 | 10.818 | 444.0008 | 410.7008 | 354.5347 | 410.7008
BEAU2K | STRW20 | 2015 | Addition | 142.51 | 0 | OHL | 0.8915 | 7.4976 | 29.988 | 702.001 | 649.351 | 560.5478 | 649.351
BLHI2J | KINT2K | 2015 | Addition | 51.4999 | 0 | OHL | 0.302 | 2.106 | 14.322 | 934.9996 | 864.8746 | 746.5972 | 864.8746
BRAC2J | BRAC2K | 2015 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
BRAC2J | TUMM2K | 2015 | Addition | 62.8 | 0 | OHL | 0.172 | 2.544 | 17.947 | 1910 | 1766.75 | 1525.135 | 1766.75
BRAC2K | BONB2J | 2015 | Addition | 10.1 | 0 | OHL | 0.028 | 0.409 | 2.886 | 1910 | 1766.75 | 1525.135 | 1766.75
CAAD1Q | CRSS1J | 2015 | Addition | 13.5 | 0 | OHL | 0.319 | 2.865 | 0.741 | 447.9996 | 414.3996 | 357.7277 | 414.3996
CAAD1R | CRSS1K | 2015 | Addition | 13.5 | 0 | OHL | 0.319 | 2.865 | 0.741 | 447.9996 | 414.3996 | 357.7277 | 414.3996
CLAS2- | BLHI2K | 2015 | Addition | 9.77 | 0 | OHL | 0.0573 | 0.3995 | 2.717 | 934.9996 | 864.8746 | 746.5972 | 864.8746
CLAS2- | KINT2J | 2015 | Addition | 41.73 | 0 | OHL | 0.2447 | 1.7065 | 11.605 | 934.9996 | 864.8746 | 746.5972 | 864.8746
CORI1J | LUIC1Q | 2015 | Addition | 9.9 | 0 | OHL | 0.232 | 2.16 | 0.523 | 463.9992 | 429.1992 | 370.5033 | 429.1992
CORI1K | LUIC1R | 2015 | Addition | 9.9 | 0 | OHL | 0.232 | 2.16 | 0.523 | 463.9992 | 429.1992 | 370.5033 | 429.1992
CRSS1J | CRSS1K | 2015 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
CRSS2A | CRSS2C | 2015 | Addition | 0 | 1.2 | Cable | 0.0136 | 0.0343 | 3.284 | 240.0001 | 222.0001 | 191.6401 | 222.0001
CRSS2B | CRSS2D | 2015 | Addition | 0 | 1.2 | Cable | 0.0136 | 0.0343 | 3.284 | 240.0001 | 222.0001 | 191.6401 | 222.0001
CRSS2C | HUNE2C | 2015 | Addition | 0 | 41.4 | Cable | 0.7106 | 1.2367 | 85.262 | 250.0001 | 231.2501 | 199.625 | 231.2501
CRSS2D | HUNE2D | 2015 | Addition | 0 | 41.4 | Cable | 0.7106 | 1.2367 | 85.262 | 250.0001 | 231.2501 | 199.625 | 231.2501
DOUN2- | GORW2- | 2015 | Addition | 58.1 | 0 | OHL | 0.4621 | 3.1663 | 12.268 | 535.0006 | 494.8756 | 427.198 | 494.8756
DOUN2- | STRW20 | 2015 | Addition | 10.69 | 0 | OHL | 0.0669 | 0.5626 | 2.25 | 702.0011 | 649.351 | 560.5478 | 649.351
FOYE2- | KNOC2J | 2015 | Addition | 24 | 0 | OHL | 0.141 | 0.943 | 6.912 | 934.9996 | 864.8746 | 746.5972 | 864.8746
FOYE2- | KNOC2K | 2015 | Addition | 24 | 0 | OHL | 0.141 | 0.943 | 6.912 | 934.9996 | 864.8746 | 746.5972 | 864.8746
INVE1J | ACHR1R | 2015 | Addition | 21.17 | 0 | OHL | 3.002 | 4.9754 | 1.035 | 99.0001 | 91.5751 | 79.0516 | 91.5751
LUIC1Q | ORRI1S | 2015 | Addition | 5.1 | 0 | OHL | 0.12 | 1.113 | 0.269 | 463.9992 | 429.1992 | 370.5033 | 429.1992
LUIC1R | ORRI1T | 2015 | Addition | 5.1 | 0 | OHL | 0.12 | 1.113 | 0.269 | 463.9992 | 429.1992 | 370.5033 | 429.1992
ORRI1S | DUCC1J | 2015 | Addition | 10.3 | 0 | OHL | 0.2419 | 2.2469 | 0.544 | 463.9992 | 429.1992 | 370.5033 | 429.1992
ORRI1T | DUCC1K | 2015 | Addition | 10.3 | 0 | OHL | 0.2419 | 2.2469 | 0.544 | 463.9992 | 429.1992 | 370.5033 | 429.1992
PORA1Q | ANSU1- | 2015 | Addition | 24.27 | 0 | OHL | 3.442 | 5.705 | 1.186 | 99.0001 | 91.5751 | 79.0516 | 91.5751
PORA1Q | CRSS1Q | 2015 | Addition | 48.3 | 0 | OHL | 6.8386 | 11.356 | 2.352 | 99.0001 | 91.5751 | 79.0516 | 91.5751
PORA1R | ACHR1R | 2015 | Addition | 14.23 | 0 | OHL | 2.018 | 3.3446 | 0.695 | 99.0001 | 91.5751 | 79.0516 | 91.5751
PORA1R | CRSS1R | 2015 | Addition | 48.3 | 0 | OHL | 6.8386 | 11.356 | 2.352 | 99.0001 | 91.5751 | 79.0516 | 91.5751
STRW11 | STRW12 | 2015 | Addition | 0 | 12 | Cable | 0.264 | 1.02 | 13.79 | 176.9999 | 163.725 | 141.3345 | 163.725
TUMM4- | BONB4- | 2015 | Addition | 72.9 | 0 | OHL | 0.094 | 1.396 | 44.078 | 2779.9968 | 2571.4971 | 2219.8275 | 2571.4971
TUMM4- | FAUG4- | 2015 | Addition | 77.2 | 0 | OHL | 0.1 | 1.478 | 46.678 | 2779.997 | 2571.4972 | 2219.8276 | 2571.4972
BLHI2J | BERB2Q | 2015 | Change | 46.9 | 0 | OHL | 0.275 | 1.918 | 13.043 | 934.9996 | 864.8746 | 746.5972 | 864.8746
BLHI2K | DAAS2- | 2015 | Change | 32.2 | 0 | OHL | 0.189 | 1.317 | 8.955 | 934.9996 | 864.8746 | 746.5972 | 864.8746
ELGI1Q | NAIR1Q | 2015 | Change | 35.4 | 0 | OHL | 3.4978 | 8.0281 | 3.176 | 126 | 116.55 | 100.611 | 116.55
ELGI1Q | NAIR1Q | 2015 | Change | 34.1 | 1.3 | Composite | 3.4978 | 8.0281 | 3.1757 | 126 | 116.55 | 100.611 | 116.55
ELGI1R | NAIR1R | 2015 | Change | 35.4 | 0 | OHL | 3.4978 | 8.0281 | 3.176 | 126 | 116.55 | 100.611 | 116.55
ELGI1R | NAIR1R | 2015 | Change | 34.1 | 1.3 | Composite | 3.4978 | 8.0281 | 3.1757 | 126 | 116.55 | 100.611 | 116.55
KNOC2J | BERB2Q | 2015 | Change | 42.7 | 0 | OHL | 0.251 | 1.746 | 11.875 | 934.9996 | 864.8746 | 746.5972 | 864.8746
KNOC2J | KNOC2L | 2015 | Change | 0 | 1.29 | Cable | 0.002 | 0.031 | 7.356 | 929.9983 | 860.2484 | 742.6036 | 860.2484
KNOC2K | DAAS2- | 2015 | Change | 57.4 | 0 | OHL | 0.337 | 2.348 | 15.963 | 934.9996 | 864.8746 | 746.5972 | 864.8746
KNOC2M | KNOC2K | 2015 | Change | 0 | 1.47 | Cable | 0.002 | 0.036 | 8.382 | 929.9983 | 860.2484 | 742.6036 | 860.2484
BEAU1J | ORRI1S | 2015 | Removed | 2.2545 | 11.2455 | Composite | 1.36 | 3.2 | 0.64 | 126 | 116.55 | 100.611 | 116.55
BEAU1K | ORRI1T | 2015 | Removed | 2.2545 | 11.2455 | Composite | 1.36 | 3.2 | 0.64 | 126 | 116.55 | 100.611 | 116.55
BEAU2K | DOUN2- | 2015 | Removed | 153.2 | 0 | OHL | 0.9584 | 8.0602 | 32.238 | 702.001 | 649.351 | 560.5478 | 649.351
BLHI2J | KINT2K | 2015 | Removed | 0 | 51.5 | Cable | 0.6 | 2.21 | 13.66 | 524.998 | 485.6232 | 419.2109 | 485.6232
BLHI2K | KINT2J | 2015 | Removed | 0 | 51.5 | Cable | 0.6 | 2.21 | 13.66 | 524.998 | 485.6232 | 419.2109 | 485.6232
BRAC1Q | BONB1J | 2015 | Removed | 9.6127 | 0.0873 | Composite | 0.98 | 2.23 | 0.48 | 126 | 116.55 | 100.611 | 116.55
BRAC1Q | ERRO1J | 2015 | Removed | 57.5 | 0 | OHL | 5.87 | 13.41 | 2.86 | 131.9999 | 122.0999 | 105.402 | 122.0999
BRAC1R | BONB1K | 2015 | Removed | 9.6127 | 0.0873 | Composite | 0.98 | 2.23 | 0.48 | 126 | 116.55 | 100.611 | 116.55
BRAC1R | ERRO1K | 2015 | Removed | 57.5 | 0 | OHL | 5.87 | 13.41 | 2.86 | 131.9999 | 122.0999 | 105.402 | 122.0999
CAAD1Q | PORA1Q | 2015 | Removed | 61.8 | 0 | OHL | 8.75 | 14.53 | 3.01 | 99.0001 | 91.5751 | 79.0516 | 91.5751
CAAD1R | PORA1R | 2015 | Removed | 61.8 | 0 | OHL | 8.75 | 14.53 | 3.01 | 99.0001 | 91.5751 | 79.0516 | 91.5751
CORI1J | LUIC1Q | 2015 | Removed | 0.23572 | 9.6643 | Composite | 1.0238 | 2.4031 | 0.482 | 126 | 116.55 | 100.611 | 116.55
CORI1K | LUIC1R | 2015 | Removed | 0.23572 | 9.6643 | Composite | 1.0238 | 2.4031 | 0.482 | 126 | 116.55 | 100.611 | 116.55
DOUN2- | GORW2- | 2015 | Removed | 58.1 | 0 | OHL | 0.4621 | 3.1663 | 12.268 | 535.0006 | 494.8756 | 427.198 | 494.8756
FAUG1- | TUMM1T | 2015 | Removed | 77.2 | 0 | OHL | 0.917 | 13.576 | 5.083 | 916.9989 | 848.224 | 732.2236 | 848.224
FOYE2- | KNOC2K | 2015 | Removed | 24 | 0 | OHL | 0.28 | 1.029 | 6.35 | 524.998 | 485.6232 | 419.2109 | 485.6232
FOYE2- | KNOC2J | 2015 | Removed | 24 | 0 | OHL | 0.28 | 1.029 | 6.35 | 524.998 | 485.6232 | 419.2109 | 485.6232
INVE1J | PORA1R | 2015 | Removed | 35.4 | 0 | OHL | 5.02 | 8.32 | 1.73 | 99.0001 | 91.5751 | 79.0516 | 91.5751
LUIC1Q | ORRI1S | 2015 | Removed | 1.4484 | 3.6516 | Composite | 0.53 | 1.23 | 0.25 | 126 | 116.55 | 100.611 | 116.55
LUIC1R | ORRI1T | 2015 | Removed | 1.4484 | 3.6516 | Composite | 0.53 | 1.23 | 0.25 | 126 | 116.55 | 100.611 | 116.55
PORA1Q | ANSU1- | 2015 | Removed | 24.27 | 0 | OHL | 3.442 | 5.705 | 1.186 | 99.0001 | 91.5751 | 79.0516 | 91.5751
TUMM1J | TUMM1T | 2015 | Removed | 0 | 0.2 | Cable | 0.002 | 0.015 | 0.39 | 150 | 138.75 | 119.775 | 138.75
STRW11 | STRW13 | 2016 | Addition | 0 | 12 | Cable | 0.264 | 1.02 | 13.79 | 176.9999 | 163.725 | 141.3345 | 163.725
ARBR1Q | DENS1Q | 2016 | Change | 14.4 | 0 | OHL | 0.61 | 3.08 | 0.75 | 182.9999 | 169.2749 | 146.1254 | 169.2749
ARBR1R | TEAL1- | 2016 | Change | 23.2 | 0 | OHL | 0.99 | 4.97 | 1.2 | 182.9999 | 169.2749 | 146.1254 | 169.2749
DENS1Q | TEAL1- | 2016 | Change | 8.7 | 0 | OHL | 0.37 | 1.86 | 0.45 | 182.9999 | 169.2749 | 146.1254 | 169.2749
DUDH1Q | GLAG1Q | 2016 | Change | 0 | 1.6 | Cable | 0.036 | 0.0955 | 2.207 | 155 | 129 | 129 | 129
DUDH1R | GLAG1R | 2016 | Change | 0 | 1.6 | Cable | 0.036 | 0.0955 | 2.207 | 155 | 129 | 129 | 129
ALNE1Q | FYRI1J | 2017 | Addition | 1.2896 | 0.0104 | Composite | 0.06 | 0.28 | 0.07 | 229.0011 | 211.826 | 182.8574 | 211.826
ALNE1R | FYRI1K | 2017 | Addition | 1.2896 | 0.0104 | Composite | 0.06 | 0.28 | 0.07 | 229.0011 | 211.826 | 182.8574 | 211.826
ARDR2Q | FYRI2J | 2017 | Addition | 1.8 | 0 | OHL | 0.0113 | 0.0947 | 0.379 | 702.0011 | 649.351 | 560.5478 | 649.351
ARDR2Q | LOCB2K | 2017 | Addition | 32.4 | 0 | OHL | 0.2027 | 1.7046 | 6.818 | 702.001 | 649.351 | 560.5478 | 649.351
BEAU2J | FYRI2J | 2017 | Addition | 31.7 | 0 | OHL | 0.1983 | 1.6678 | 6.671 | 702.001 | 649.351 | 560.5478 | 649.351
BEAU2K | FYRI2K | 2017 | Addition | 31.64 | 0 | OHL | 0.1979 | 1.6645 | 6.657 | 702.0011 | 649.351 | 560.5478 | 649.351
BEAU4- | EISE1- | 2017 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0003 | 92.5003 | 79.8502 | 92.5003
BLHI1J | BLHI1K | 2017 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
BLHI2A | DAAS2- | 2017 | Addition | 32.2 | 0 | OHL | 0.189 | 1.317 | 8.955 | 934.9996 | 864.8746 | 746.5972 | 864.8746
BLHI2B | BERB2Q | 2017 | Addition | 46.9 | 0 | OHL | 0.275 | 1.918 | 13.043 | 934.9996 | 864.8746 | 746.5972 | 864.8746
BLHI2B | BLHI2K | 2017 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0.01 | 100.0002 | 92.5002 | 79.8502 | 92.5002
BLHI2J | BLHI2A | 2017 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0.01 | 100.0002 | 92.5002 | 79.8502 | 92.5002
BROR1Q | LOCB1K | 2017 | Addition | 22.12 | 0 | OHL | 2.2511 | 5.1536 | 1.096 | 126 | 116.55 | 100.611 | 116.55
FARI1K | DUNM1- | 2017 | Addition | 0 | 11 | Cable | 1.122 | 2.563 | 0.539 | 161.9999 | 149.8499 | 129.357 | 149.8499
FOYE2- | FARI2K | 2017 | Addition | 10 | 0 | OHL | 0.0588 | 0.3929 | 2.88 | 934.9996 | 864.8746 | 746.5972 | 864.8746
FOYE2- | KNOC2J | 2017 | Addition | 24 | 0 | OHL | 0.141 | 0.943 | 6.912 | 934.9996 | 864.8746 | 746.5972 | 864.8746
FYRI1J | FYRI1K | 2017 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
FYRI2K | LOCB2J | 2017 | Addition | 34.23 | 0 | OHL | 0.2141 | 1.8007 | 7.202 | 702.001 | 649.351 | 560.5478 | 649.351
KNOC2J | DAAS2- | 2017 | Addition | 57.4 | 0 | OHL | 0.337 | 2.348 | 15.963 | 934.9996 | 864.8746 | 746.5972 | 864.8746
KNOC2K | BERB2Q | 2017 | Addition | 42.7 | 0 | OHL | 0.251 | 1.746 | 11.875 | 934.9996 | 864.8746 | 746.5972 | 864.8746
KNOC2K | FARI2K | 2017 | Addition | 14 | 0 | OHL | 0.0822 | 0.5501 | 4.032 | 934.9996 | 864.8746 | 746.5972 | 864.8746
LOCB1J | LOCB1K | 2017 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
LOCB2J | LOCB2K | 2017 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
MYBS1Q | LOCB1J | 2017 | Addition | 81.61 | 0 | OHL | 8.2998 | 19.0008 | 4.028 | 126 | 116.55 | 100.611 | 116.55
SHIN1- | LOCB1J | 2017 | Addition | 12.19 | 0 | OHL | 1.2402 | 2.8392 | 0.602 | 126 | 116.55 | 100.611 | 116.55
SHIN1- | LOCB1K | 2017 | Addition | 12.18 | 0 | OHL | 1.239 | 2.8364 | 0.604 | 126 | 116.55 | 100.611 | 116.55
STRB2- | LOCB2K | 2017 | Addition | 18.9 | 0 | OHL | 0.1503 | 1.0299 | 3.991 | 535.0006 | 494.8756 | 427.198 | 494.8756
STRW20 | LOCB2J | 2017 | Addition | 76.6501 | 0 | OHL | 0.4795 | 4.0324 | 16.128 | 702.001 | 649.351 | 560.5478 | 649.351
ALNE1Q | MOTA1Q | 2017 | Removed | 1.2896 | 0.0104 | Composite | 0.06 | 0.28 | 0.07 | 229.0011 | 211.826 | 182.8574 | 211.826
ALNE1R | MOTA1R | 2017 | Removed | 1.2896 | 0.0104 | Composite | 0.06 | 0.28 | 0.07 | 229.0011 | 211.826 | 182.8574 | 211.826
ARDR2Q | STRB2- | 2017 | Removed | 51.3 | 0 | OHL | 0.408 | 2.7957 | 10.832 | 535.0006 | 494.8756 | 427.198 | 494.8756
ARDR2Q | BEAU2J | 2017 | Removed | 33.5 | 0 | OHL | 0.2664 | 1.8257 | 7.073 | 535.0006 | 494.8756 | 427.198 | 494.8756
BEAU2K | STRW20 | 2017 | Removed | 142.51 | 0 | OHL | 0.8915 | 7.4976 | 29.988 | 702.001 | 649.351 | 560.5478 | 649.351
BLHI2J | BERB2Q | 2017 | Removed | 46.9 | 0 | OHL | 0.275 | 1.918 | 13.043 | 934.9996 | 864.8746 | 746.5972 | 864.8746
BLHI2K | DAAS2- | 2017 | Removed | 32.2 | 0 | OHL | 0.189 | 1.317 | 8.955 | 934.9996 | 864.8746 | 746.5972 | 864.8746
BROR1Q | SHIN1- | 2017 | Removed | 34.3 | 0 | OHL | 3.49 | 7.99 | 1.7 | 126 | 116.55 | 100.611 | 116.55
FOYE2- | KNOC2K | 2017 | Removed | 24 | 0 | OHL | 0.141 | 0.943 | 6.912 | 934.9996 | 864.8746 | 746.5972 | 864.8746
FOYE2- | KNOC2J | 2017 | Removed | 24 | 0 | OHL | 0.141 | 0.943 | 6.912 | 934.9996 | 864.8746 | 746.5972 | 864.8746
KNOC2J | BERB2Q | 2017 | Removed | 42.7 | 0 | OHL | 0.251 | 1.746 | 11.875 | 934.9996 | 864.8746 | 746.5972 | 864.8746
KNOC2K | DAAS2- | 2017 | Removed | 57.4 | 0 | OHL | 0.337 | 2.348 | 15.963 | 934.9996 | 864.8746 | 746.5972 | 864.8746
MYBS1Q | SHIN1- | 2017 | Removed | 93.8 | 0 | OHL | 9.54 | 21.84 | 4.63 | 126 | 116.55 | 100.611 | 116.55
ALLT1Q | TOMT1J | 2018 | Addition | 0 | 12 | Cable | 0.12 | 2.8 | 0.588 | 150 | 138.75 | 119.775 | 138.75
BASK2A | BASK2B | 2018 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 92.5 | 79.85 | 92.5
BEAU1J | KNOC1J | 2018 | Addition | 18 | 0 | OHL | 0.707 | 3.776 | 0.979 | 229.0011 | 211.826 | 182.8574 | 211.826
BEAU1K | KNOC1J | 2018 | Addition | 18 | 0 | OHL | 0.707 | 3.776 | 0.979 | 229.0011 | 211.826 | 182.8574 | 211.826
BLHI1J | DORE11 | 2018 | Addition | 20 | 0 | OHL | 0.786 | 4.196 | 1.09 | 279.9995 | 258.9995 | 223.5796 | 258.9995
BLHI1K | DORE12 | 2018 | Addition | 20 | 0 | OHL | 0.786 | 4.196 | 1.09 | 279.9995 | 258.9995 | 223.5796 | 258.9995
BLHI4- | BLHI4R | 2018 | Addition | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 1271.9973 | 1176.5975 | 1015.6899 | 1176.5975
BOAG1Q | TOMT1K | 2018 | Addition | 14.1 | 0 | OHL | 1.436 | 3.2912 | 0.698 | 131.9999 | 122.0999 | 105.402 | 122.0999
BOAG1R | TOMT1J | 2018 | Addition | 14.1 | 0 | OHL | 1.436 | 3.2912 | 0.698 | 131.9999 | 122.0999 | 105.402 | 122.0999
CASS1Q | SALA1- | 2018 | Addition | 0 | 6 | Cable | 0.61 | 1.4 | 0.3 | 150 | 138.75 | 119.775 | 138.75
DORE11 | DORE12 | 2018 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0.01 | 100.0001 | 92.5001 | 79.8501 | 92.5001
DOUN2- | THSO2J | 2018 | Addition | 15.4 | 0 | OHL | 0.0901 | 0.839 | 3.28 | 964.9978 | 892.623 | 770.5508 | 892.623
DOUN2- | THSO2K | 2018 | Addition | 15.4 | 0 | OHL | 0.0901 | 0.839 | 3.28 | 964.9978 | 892.623 | 770.5508 | 892.623
DOUN2A | DOUN2B | 2018 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 92.5 | 79.85 | 92.5
DOUN2B | DOUN2C | 2018 | Addition | 0 | 2 | Cable | 0.0226 | 0.0571 | 5.474 | 240.0001 | 222.0001 | 191.6401 | 222.0001
DOUN2C | DOUN2D | 2018 | Addition | 0 | 70 | Cable | 1.2015 | 2.091 | 144.1601 | 240.0001 | 222.0001 | 191.6401 | 222.0001
DOUN2D | BASK2B | 2018 | Addition | 0 | 1 | Cable | 0.0113 | 0.0286 | 2.737 | 240.0001 | 222.0001 | 191.6401 | 222.0001
FAAR1Q | TOMT1K | 2018 | Addition | 16 | 0 | OHL | 1.6291 | 3.7338 | 0.792 | 131.9999 | 122.0999 | 105.402 | 122.0999
FAAR1R | TOMT1J | 2018 | Addition | 16 | 0 | OHL | 1.6291 | 3.7338 | 0.792 | 131.9999 | 122.0999 | 105.402 | 122.0999
FAUG1- | MILS1Q | 2018 | Addition | 0 | 6 | Cable | 0.6083 | 1.3941 | 0.296 | 111 | 102.675 | 88.6335 | 102.675
GILB1J | GILB1K | 2018 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
GILB1J | MEYG1- | 2018 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
KNOC2J | TOMT2K | 2018 | Addition | 24 | 0 | OHL | 0.109 | 0.996 | 6.53 | 955 | 883.375 | 762.5675 | 883.375
KNOC2K | TOMT2J | 2018 | Addition | 24 | 0 | OHL | 0.109 | 0.996 | 6.53 | 955 | 883.375 | 762.5675 | 883.375
LOCL1S | MILS1Q | 2018 | Addition | 0 | 2.5 | Cable | 0.2533 | 0.5806 | 0.123 | 111 | 102.675 | 88.6335 | 102.675
MYBS1Q | SPIT1J | 2018 | Addition | 3.99 | 0 | OHL | 0.4077 | 0.9346 | 0.198 | 126 | 116.55 | 100.611 | 116.55
MYBS1R | SPIT1J | 2018 | Addition | 0 | 3.99 | Cable | 0.4077 | 0.9346 | 0.198 | 126 | 116.55 | 100.611 | 116.55
MYBS1S | SPIT1K | 2018 | Addition | 0 | 5 | Cable | 0.1174 | 1.0907 | 0.264 | 463.9992 | 429.1992 | 370.5033 | 429.1992
MYBS1T | SPIT1K | 2018 | Addition | 5 | 0 | OHL | 0.1174 | 1.0907 | 0.264 | 463.9992 | 429.1992 | 370.5033 | 429.1992
SHET1J | SHET1R | 2018 | Addition | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 719.9992 | 665.9993 | 574.9194 | 665.9993
SPIT2J | SPIT2K | 2018 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
SPIT2K | SPIT2R | 2018 | Addition | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 960.0013 | 888.0012 | 766.561 | 888.0012
THSO1J | GILB1J | 2018 | Addition | 24 | 0 | OHL | 0.9547 | 5.244 | 1.279 | 335.0011 | 309.8761 | 267.4984 | 309.8761
THSO1J | THSO1K | 2018 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
THSO1K | GILB1K | 2018 | Addition | 24 | 0 | OHL | 0.9547 | 5.244 | 1.279 | 335.0011 | 309.8761 | 267.4984 | 309.8761
THSO2J | SPIT2J | 2018 | Addition | 12.1 | 0 | OHL | 0.0708 | 0.659 | 2.577 | 964.9978 | 892.623 | 770.5508 | 892.623
THSO2K | SPIT2K | 2018 | Addition | 12.1 | 0 | OHL | 0.0708 | 0.659 | 2.577 | 964.9978 | 892.623 | 770.5508 | 892.623
TOMT1K | TOMT1J | 2018 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
TOMT2K | TOMT2J | 2018 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
TEAL2J | WFIB2- | 2018 | Change | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 1090 | 1030 | 925 | 1030
TEAL2K | GLRB2- | 2018 | Change | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 1090 | 1030 | 925 | 1030
BEAU1J | FAAR1Q | 2018 | Removed | 30.1 | 0 | OHL | 3.065 | 7.025 | 1.49 | 131.9999 | 122.0999 | 105.402 | 122.0999
BEAU1K | FAAR1R | 2018 | Removed | 30.1 | 0 | OHL | 3.065 | 7.025 | 1.49 | 131.9999 | 122.0999 | 105.402 | 122.0999
BOAG1Q | FAAR1Q | 2018 | Removed | 30.1 | 0 | OHL | 3.065 | 7.025 | 1.49 | 131.9999 | 122.0999 | 105.402 | 122.0999
BOAG1R | FAAR1R | 2018 | Removed | 30.1 | 0 | OHL | 3.065 | 7.025 | 1.49 | 131.9999 | 122.0999 | 105.402 | 122.0999
DOUN1- | THSO1Q | 2018 | Removed | 15.4 | 0 | OHL | 1.57 | 3.6 | 0.76 | 131.9999 | 122.0999 | 105.402 | 122.0999
DOUN1- | THSO1R | 2018 | Removed | 15.4 | 0 | OHL | 1.57 | 3.6 | 0.76 | 131.9999 | 122.0999 | 105.402 | 122.0999
FAUG1- | LOCL1S | 2018 | Removed | 0 | 8.5 | Cable | 0.8616 | 1.9747 | 0.419 | 111 | 102.675 | 88.6335 | 102.675
MYBS1Q | MYBS1S | 2018 | Removed | 0 | 1 | Cable | 0 | 0.01 | 0 | 998.9996 | 924.0746 | 797.7012 | 924.0746
MYBS1R | MYBS1T | 2018 | Removed | 0 | 1 | Cable | 0 | 0.01 | 0 | 998.9996 | 924.0746 | 797.7012 | 924.0746
MYBS1S | THSO1Q | 2018 | Removed | 16.1 | 0 | OHL | 1.64 | 3.75 | 0.79 | 126 | 116.55 | 100.611 | 116.55
MYBS1T | THSO1R | 2018 | Removed | 16.1 | 0 | OHL | 1.64 | 3.75 | 0.79 | 126 | 116.55 | 100.611 | 116.55
ALYT2Q | TEAL2J | 2020 | Addition | 0 | 16.2 | Cable | 0.0728 | 0.6682 | 4.379 | 955 | 883.375 | 762.5675 | 883.375
ALYT2R | TEAL2K | 2020 | Addition | 0 | 16.2 | Cable | 0.0728 | 0.6682 | 4.379 | 955 | 883.375 | 762.5675 | 883.375
ALYT4- | FETT4Q | 2020 | Addition | 67.35 | 0 | OHL | 0.1442 | 1.32 | 38.759 | 1590.0019 | 1470.7517 | 1269.6165 | 1470.7517
ALYT4- | FETT4R | 2020 | Addition | 67.35 | 0 | OHL | 0.1442 | 1.32 | 38.759 | 1590.0019 | 1470.7517 | 1269.6165 | 1470.7517
ALYT4- | KINB4J | 2020 | Addition | 69.98 | 0 | OHL | 0.1497 | 1.3716 | 40.273 | 1590.0019 | 1470.7517 | 1269.6165 | 1470.7517
ALYT4- | KINB4K | 2020 | Addition | 69.98 | 0 | OHL | 0.1497 | 1.3716 | 40.273 | 1590.0019 | 1470.7517 | 1269.6165 | 1470.7517
BEAU1W | BEAU1X | 2020 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
BEAU1W | CULL1Q | 2020 | Addition | 3.542 | 10.458 | Composite | 1.43 | 3.28 | 0.69 | 111 | 102.675 | 88.6335 | 102.675
BEAU1W | DUCC1J | 2020 | Addition | 0 | 3.2 | Cable | 0.0226 | 0.1238 | 10.818 | 444.0008 | 410.7008 | 354.5347 | 410.7008
BEAU1X | DUCC1K | 2020 | Addition | 0 | 3.2 | Cable | 0.0226 | 0.1238 | 10.818 | 444.0008 | 410.7008 | 354.5347 | 410.7008
BEAU1X | KIOR1Q | 2020 | Addition | 1.2402 | 0.0598 | Composite | 0.13 | 0.29 | 0.06 | 111 | 102.675 | 88.6335 | 102.675
BEAU4- | BEAU4R | 2020 | Addition | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 100.0003 | 92.5003 | 79.8502 | 92.5003
BEAU4- | FAUG4J | 2020 | Addition | 48.6 | 0 | OHL | 0.063 | 0.931 | 29.386 | 2779.9968 | 2571.4971 | 2219.8275 | 2571.4971
BLHI1J | KEIT1K | 2020 | Addition | 0 | 4 | Cable | 0.2234 | 0.8328 | 0.224 | 203.0001 | 187.7751 | 162.0955 | 187.7751
BLHI1K | BLHI1M | 2020 | Addition | 0 | 3 | Cable | 0.1675 | 0.6246 | 0.168 | 203.0001 | 187.7751 | 162.0955 | 187.7751
BLHI1K | KEIT1J | 2020 | Addition | 0 | 4 | Cable | 0.2234 | 0.8328 | 0.224 | 203.0001 | 187.7751 | 162.0955 | 187.7751
BLHI1M | GLFA1- | 2020 | Addition | 39.3 | 0 | OHL | 3.995 | 9.157 | 1.947 | 126 | 116.55 | 100.611 | 116.55
BLHI2J | KEIT2Q | 2020 | Addition | 0 | 2.4 | Cable | 0.0124 | 0.053 | 7.983 | 349 | 322.825 | 278.6765 | 322.825
BLHI2K | KEIT2R | 2020 | Addition | 0 | 2.4 | Cable | 0.0124 | 0.053 | 7.983 | 349 | 322.825 | 278.6765 | 322.825
BLHI4- | BEAT4- | 2020 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0003 | 92.5003 | 79.8502 | 92.5003
BLHI4- | ROTI4- | 2020 | Addition | 35.4 | 0 | OHL | 0.0758 | 0.6938 | 20.373 | 1590.0019 | 1470.7517 | 1269.6165 | 1470.7517
BLHI4- | ROTI4- | 2020 | Addition | 35.4 | 0 | OHL | 0.0758 | 0.6938 | 20.373 | 1590.0019 | 1470.7517 | 1269.6165 | 1470.7517
BRAC2J | CROB2- | 2020 | Addition | 45.84 | 0 | OHL | 0.1256 | 1.8571 | 13.101 | 1910 | 1766.75 | 1525.135 | 1766.75
DALN1Q | DALN1R | 2020 | Addition | 0 | 4 | Cable | 0.14 | 0.312 | 3.943 | 127 | 117.475 | 101.4095 | 117.475
DUGR1Q | DUGR1J | 2020 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
FARI1J | COGA1- | 2020 | Addition | 0 | 15 | Cable | 1.53 | 3.495 | 0.735 | 161.9999 | 149.8499 | 129.357 | 149.8499
FASN2- | FAUG2J | 2020 | Addition | 24.384 | 1.016 | Composite | 0.069 | 1.029 | 7.259 | 1910 | 1766.75 | 1525.135 | 1766.75
FAUG1J | DUGR1J | 2020 | Addition | 150 | 0 | OHL | 8.38 | 31.23 | 8.4 | 203.0001 | 187.7751 | 162.0955 | 187.7751
FAUG1J | FAUG1K | 2020 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
FAUG2J | FAUG2K | 2020 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
FAUG2J | TUMM2J | 2020 | Addition | 77.2 | 0 | OHL | 0.211 | 3.128 | 22.063 | 1910 | 1766.75 | 1525.135 | 1766.75
FAUG4J | FAUG4K | 2020 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0003 | 92.5003 | 79.8502 | 92.5003
FETT1- | FETT1R | 2020 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
FETT4Q | FETT4R | 2020 | Addition | 0 | 1 | Cable | 0.001 | 0.001 | 0 | 100.0003 | 92.5003 | 79.8502 | 92.5003
FIDD1Q | FETT1- | 2020 | Addition | 0 | 10 | Cable | 0.558 | 2.082 | 0.559 | 203.0001 | 187.7751 | 162.0955 | 187.7751
FIDD1R | FOGG1R | 2020 | Addition | 0 | 25.4 | Cable | 3.004 | 6.157 | 1.238 | 112 | 103.6 | 89.432 | 103.6
FIDD1S | FETT1R | 2020 | Addition | 0 | 10 | Cable | 0.558 | 2.082 | 0.559 | 203.0001 | 187.7751 | 162.0955 | 187.7751
FOYE2- | FARI2J | 2020 | Addition | 10 | 0 | OHL | 0.0588 | 0.3929 | 2.88 | 934.9996 | 864.8746 | 746.5972 | 864.8746
GRAR1J | EISE1- | 2020 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
GRAR1J | GRAR1J_1 | 2020 | Addition | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
GRAR1J | GRAR1Q | 2020 | Addition | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
GRAR1J | MUAI1K | 2020 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
KEIT1J | AULW1S | 2020 | Addition | 0 | 11 | Cable | 1.473 | 2.441 | 0.571 | 83 | 76.775 | 66.2755 | 76.775
KEIT1J | MACD1Q | 2020 | Addition | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 102.675 | 88.6335 | 102.675
KEIT1K | MACD1R | 2020 | Addition | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 102.675 | 88.6335 | 102.675
KINT4- | FETT4Q | 2020 | Addition | 32.15 | 0 | OHL | 0.0688 | 0.6301 | 18.499 | 1590.0019 | 1470.7517 | 1269.6165 | 1470.7517
KINT4- | FETT4R | 2020 | Addition | 32.15 | 0 | OHL | 0.0688 | 0.6301 | 18.499 | 1590.0019 | 1470.7517 | 1269.6165 | 1470.7517
KNOC2J | FARI2J | 2020 | Addition | 14 | 0 | OHL | 0.0822 | 0.5501 | 4.032 | 934.9996 | 864.8746 | 746.5972 | 864.8746
LAIR1K | DALN1Q | 2020 | Addition | 0 | 14 | Cable | 1.428 | 3.262 | 0.686 | 131.9999 | 122.0999 | 105.402 | 122.0999
LAIR1Q | LAIR1K | 2020 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
LAIR2K | LOCB2K | 2020 | Addition | 20 | 0 | OHL | 0.086 | 0.818 | 5.56 | 1160.0008 | 1073.0007 | 926.2606 | 1073.0007
LAIR2Q | LAIR2K | 2020 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
LAIR2Q | LOCB2J | 2020 | Addition | 20 | 0 | OHL | 0.086 | 0.818 | 5.56 | 1160.0008 | 1073.0007 | 926.2606 | 1073.0007
NEDE4J | MORF4- | 2020 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0003 | 92.5003 | 79.8502 | 92.5003
PEHE4- | NEDE4J | 2020 | Addition | 23.65 | 0 | OHL | 0.0506 | 0.4635 | 13.611 | 1584.9997 | 1466.1247 | 1265.6223 | 1466.1247
PEHE4- | NEDE4K | 2020 | Addition | 23.65 | 0 | OHL | 0.0506 | 0.4635 | 13.611 | 1584.9997 | 1466.1247 | 1265.6223 | 1466.1247
ROTI4- | KINT4- | 2020 | Addition | 23.2 | 0 | OHL | 0.0496 | 0.4547 | 13.352 | 1590.0019 | 1470.7517 | 1269.6165 | 1470.7517
ROTI4- | KINT4- | 2020 | Addition | 23.2 | 0 | OHL | 0.0496 | 0.4547 | 13.352 | 1590.0019 | 1470.7517 | 1269.6165 | 1470.7517
ROTI4- | NEDE4J | 2020 | Addition | 23.65 | 0 | OHL | 0.0506 | 0.4635 | 13.611 | 1584.9997 | 1466.1247 | 1265.6223 | 1466.1247
ROTI4- | NEDE4K | 2020 | Addition | 23.65 | 0 | OHL | 0.0506 | 0.4635 | 13.611 | 1584.9997 | 1466.1247 | 1265.6223 | 1466.1247
TEAL2J | FOFF2- | 2020 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
TOMT1K | GLKY1- | 2020 | Addition | 0 | 3 | Cable | 0.4 | 0.67 | 0.16 | 83 | 76.775 | 66.2755 | 76.775
TOMT1K | TOMN1J | 2020 | Addition | 0 | 13 | Cable | 1.33 | 3.03 | 0.637 | 111 | 102.675 | 88.6335 | 102.675
TUMM2K | CROB2- | 2020 | Addition | 16.96 | 0 | OHL | 0.0464 | 0.6869 | 4.846 | 1910 | 1766.75 | 1525.135 | 1766.75
TUMM4- | FAUG4J | 2020 | Addition | 77.2 | 0 | OHL | 0.1 | 1.478 | 46.678 | 2779.997 | 2571.4972 | 2219.8276 | 2571.4972
DOUN2- | GORW2- | 2020 | Change | 58.1 | 0 | OHL | 0.3634 | 3.0569 | 12.226 | 702.001 | 649.351 | 560.5478 | 649.351
GORW2- | STRB2- | 2020 | Change | 10.3 | 0 | OHL | 0.0644 | 0.5419 | 2.167 | 702.0011 | 649.351 | 560.5478 | 649.351
STRB2- | LOCB2K | 2020 | Change | 18.9 | 0 | OHL | 0.1182 | 0.9944 | 3.977 | 702.0011 | 649.351 | 560.5478 | 649.351
TUMM4- | BONB4- | 2020 | Change | 72.9 | 0 | OHL | 0.094 | 1.396 | 44.078 | 2779.9968 | 2571.4971 | 2219.8275 | 2571.4971
BEAU1J | CULL1Q | 2020 | Removed | 3.542 | 10.458 | Composite | 1.43 | 3.28 | 0.69 | 111 | 102.675 | 88.6335 | 102.675
BEAU1J | DUCC1J | 2020 | Removed | 0 | 3.2 | Cable | 0.0226 | 0.1238 | 10.818 | 444.0008 | 410.7008 | 354.5347 | 410.7008
BEAU1K | DUCC1K | 2020 | Removed | 0 | 3.2 | Cable | 0.0226 | 0.1238 | 10.818 | 444.0008 | 410.7008 | 354.5347 | 410.7008
BEAU1K | KIOR1Q | 2020 | Removed | 1.2402 | 0.0598 | Composite | 0.13 | 0.29 | 0.06 | 111 | 102.675 | 88.6335 | 102.675
BEAU4- | FAUG4- | 2020 | Removed | 48.6 | 0 | OHL | 0.063 | 0.931 | 29.386 | 2779.9968 | 2571.4971 | 2219.8275 | 2571.4971
BEAU4- | EISE1- | 2020 | Removed | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0003 | 92.5003 | 79.8502 | 92.5003
BLHI2J | PEHERS | 2020 | Removed | 82.72 | 0 | OHL | 0.42 | 3.576 | 21.598 | 1090.0017 | 1008.2515 | 870.3663 | 1008.2515
BLHI2K | KEIT2Q | 2020 | Removed | 0 | 2.4 | Cable | 0.01 | 0.1 | 0.58 | 1090.0017 | 1008.2515 | 870.3663 | 1008.2515
BRAC2J | TUMM2K | 2020 | Removed | 62.8 | 0 | OHL | 0.172 | 2.544 | 17.947 | 1910 | 1766.75 | 1525.135 | 1766.75
FASN2- | FAUG2- | 2020 | Removed | 24.384 | 1.016 | Composite | 0.069 | 1.029 | 7.259 | 1910 | 1766.75 | 1525.135 | 1766.75
FAUG2- | TUMM2J | 2020 | Removed | 77.2 | 0 | OHL | 0.211 | 3.128 | 22.063 | 1910 | 1766.75 | 1525.135 | 1766.75
FETT2P | FETT2R | 2020 | Removed | 0 | 1 | Cable | 0 | 0.01 | 0 | 999.0019 | 924.0767 | 797.703 | 924.0767
FETT2Q | KINB2J | 2020 | Removed | 137.33 | 0 | OHL | 0.6853 | 5.8914 | 35.895 | 955 | 883.375 | 762.5675 | 883.375
FETT2Q | FETT2R | 2020 | Removed | 0 | 1 | Cable | 0 | 0.01 | 0 | 999.0019 | 924.0767 | 797.703 | 924.0767
FIDD1Q | FIDD1R | 2020 | Removed | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
FIDD1Q | FOGG1R | 2020 | Removed | 0 | 25.4 | Cable | 3.004 | 6.157 | 1.238 | 112 | 103.6 | 89.432 | 103.6
FOYE2- | KNOC2J | 2020 | Removed | 24 | 0 | OHL | 0.141 | 0.943 | 6.912 | 934.9996 | 864.8746 | 746.5972 | 864.8746
KEIT1- | GLFA1- | 2020 | Removed | 41.3 | 0 | OHL | 3.0087 | 6.8969 | 1.466 | 126 | 116.55 | 100.611 | 116.55
KEIT1- | MACD1R | 2020 | Removed | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 102.675 | 88.6335 | 102.675
KEIT1- | MACD1Q | 2020 | Removed | 37.8 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 102.675 | 88.6335 | 102.675
KEIT2Q | KEIT2R | 2020 | Removed | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0002 | 92.5002 | 79.8502 | 92.5002
KEIT2R | KINT2J | 2020 | Removed | 56.2 | 0 | OHL | 0.29 | 2.44 | 14.72 | 1090.0017 | 1008.2515 | 870.3663 | 1008.2515
KINT2K | FETT2Q | 2020 | Removed | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 955 | 883.375 | 762.5675 | 883.375
KINT2K | FETT2P | 2020 | Removed | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 955 | 883.375 | 762.5675 | 883.375
KINT2K | PEHE2Q | 2020 | Removed | 70.5 | 0 | OHL | 0.36 | 3.07 | 18.48 | 1090.0017 | 1008.2515 | 870.3663 | 1008.2515
LAIR1Q | SHIN1- | 2020 | Removed | 0 | 10.5 | Cable | 1.06 | 2.52 | 0.5 | 111 | 102.675 | 88.6335 | 102.675
TEAL2J | KINB2K | 2020 | Removed | 86.18 | 0 | OHL | 0.4329 | 3.735 | 23 | 955 | 883.375 | 762.5675 | 883.375
TEAL2K | FETT2P | 2020 | Removed | 83.55 | 0 | OHL | 0.4226 | 3.6513 | 21.994 | 955 | 883.375 | 762.5675 | 883.375
TUMM4- | FAUG4- | 2020 | Removed | 77.2 | 0 | OHL | 0.1 | 1.478 | 46.678 | 2779.997 | 2571.4972 | 2219.8276 | 2571.4972
BEAU2J | SHIN2J | 2023 | Addition | 62 | 0 | OHL | 0.3348 | 3.1166 | 14.209 | 966.9983 | 894.4735 | 772.1482 | 894.4735
BEAU2K | SHIN2K | 2023 | Addition | 62 | 0 | OHL | 0.3348 | 3.1166 | 14.209 | 966.9983 | 894.4735 | 772.1482 | 894.4735
COGL4- | COGL4J | 2023 | Addition | 0 | 1.95 | Cable | 0.0015 | 0.0264 | 9.165 | 930.0004 | 860.2504 | 742.6053 | 860.2504
COGL4- | COGL4K | 2023 | Addition | 0 | 1.95 | Cable | 0.0015 | 0.0264 | 9.165 | 930.0004 | 860.2504 | 742.6053 | 860.2504
DOUN1- | LIME1- | 2023 | Addition | 0 | 4 | Cable | 0.408 | 0.932 | 0.196 | 131.9999 | 122.0999 | 105.402 | 122.0999
DOUN2- | STRW2Q | 2023 | Addition | 14.2 | 0 | OHL | 0.0888 | 0.7471 | 2.988 | 702.001 | 649.351 | 560.5478 | 649.351
FAUG1J | BEIN1- | 2023 | Addition | 0 | 16 | Cable | 0.806 | 3.313 | 0.896 | 195 | 180.375 | 155.7075 | 180.375
FAUG1K | BHLA1- | 2023 | Addition | 0 | 19 | Cable | 0.957 | 3.934 | 1.063 | 195 | 180.375 | 155.7075 | 180.375
FAUG2J | TUMM2J | 2023 | Addition | 77.2 | 0 | OHL | 0.211 | 3.128 | 22.063 | 1910 | 1766.75 | 1525.135 | 1766.75
FAUG4J | INGA4K | 2023 | Addition | 8.5 | 0 | OHL | 0.0175 | 0.1625 | 4.88 | 1940.0008 | 1794.5008 | 1549.0907 | 1794.5008
FAUG4J | STRL4J | 2023 | Addition | 24.01 | 0 | OHL | 0.0311 | 0.4597 | 14.517 | 2779.997 | 2571.4972 | 2219.8276 | 2571.4972
FAUG4K | INGA4J | 2023 | Addition | 8.5 | 0 | OHL | 0.0175 | 0.1625 | 4.88 | 1940.0008 | 1794.5008 | 1549.0907 | 1794.5008
FWIL1Q | INGA1J | 2023 | Addition | 34.9 | 0 | OHL | 3.55 | 8.11 | 1.73 | 126 | 116.55 | 100.611 | 116.55
FWIL1R | INGA1K | 2023 | Addition | 34.9 | 0 | OHL | 3.55 | 8.11 | 1.73 | 126 | 116.55 | 100.611 | 116.55
FYRI1J | GLEM16 | 2023 | Addition | 0 | 13 | Cable | 1.6907 | 2.8423 | 0.673 | 189.9999 | 175.7499 | 151.7149 | 175.7499
GORW2- | STRW2Q | 2023 | Addition | 43.9 | 0 | OHL | 0.2746 | 2.3098 | 9.238 | 702.0011 | 649.351 | 560.5478 | 649.351
GRAR1J | DRUL1- | 2023 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
GRAR1J | LAGR1- | 2023 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
GRAR1J | STWD1- | 2023 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
INGA1Q | INGA1K | 2023 | Addition | 0 | 2.4 | Cable | 0.25 | 0.58 | 0.12 | 126 | 116.55 | 100.611 | 116.55
INGA4J | COGL4J | 2023 | Addition | 10 | 0 | OHL | 0.0206 | 0.1988 | 5.792 | 1469.9984 | 1359.7486 | 1173.7938 | 1359.7486
INGA4K | COGL4K | 2023 | Addition | 10 | 0 | OHL | 0.0395 | 0.3633 | 11.276 | 1469.9984 | 1359.7486 | 1173.7938 | 1359.7486
NEDE4J | NEDE4K | 2023 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0003 | 92.5003 | 79.8502 | 92.5003
PEHE4- | PEHE4L | 2023 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0003 | 92.5003 | 79.8502 | 92.5003
SHET1J | SHET1M | 2023 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
SHIN2J | LOCB2J | 2023 | Addition | 12 | 0 | OHL | 0.0648 | 0.6034 | 2.751 | 966.9983 | 894.4735 | 772.1482 | 894.4735
SHIN2K | LOCB2K | 2023 | Addition | 12 | 0 | OHL | 0.0648 | 0.6034 | 2.751 | 966.9983 | 894.4735 | 772.1482 | 894.4735
STRL1J | STRL1- | 2023 | Addition | 0 | 10 | Cable | 0.235 | 2.181 | 0.515 | 447.9996 | 414.3996 | 357.7277 | 414.3996
STRW31_1 | STRW32 | 2023 | Addition | 0 | 9 | Cable | 1.656 | 4.419 | 2.151 | 107.3998 | 99.3449 | 85.7588 | 99.3449
TUMM4- | STRL4J | 2023 | Addition | 53.19 | 0 | OHL | 0.0689 | 1.0183 | 32.161 | 2779.997 | 2571.4972 | 2219.8276 | 2571.4972
BROR1Q | LOCB1K | 2023 | Change | 22.1134 | 0.006636 | Composite | 2.2511 | 5.1536 | 1.096 | 126 | 116.55 | 100.611 | 116.55
STRW20 | LOCB2J | 2023 | Change | 76.6501 | 0 | OHL | 0.4795 | 4.0324 | 16.128 | 702.001 | 649.351 | 560.5478 | 649.351
BEAU1L | MOTA1R | 2023 | Removed | 29.2 | 0 | OHL | 2.967 | 6.794 | 1.446 | 126 | 116.55 | 100.611 | 116.55
BEAU1M | MOTA1Q | 2023 | Removed | 29.2 | 0 | OHL | 2.967 | 6.794 | 1.446 | 126 | 116.55 | 100.611 | 116.55
BEAU1P | BEAU1L | 2023 | Removed | 0 | 2.1 | Cable | 0.0689 | 0.1988 | 2.414 | 140 | 129.5 | 111.79 | 129.5
BEAU1Q | BEAU1M | 2023 | Removed | 0 | 2.1 | Cable | 0.0689 | 0.1988 | 2.414 | 140 | 129.5 | 111.79 | 129.5
DOUN2- | GORW2- | 2023 | Removed | 58.1 | 0 | OHL | 0.3634 | 3.0569 | 12.226 | 702.001 | 649.351 | 560.5478 | 649.351
FAUG1- | LOCL1Q | 2023 | Removed | 8.5 | 0 | OHL | 0.87 | 1.98 | 0.42 | 126 | 116.55 | 100.611 | 116.55
FAUG1- | LOCL1R | 2023 | Removed | 8.5 | 0 | OHL | 0.87 | 1.98 | 0.42 | 126 | 116.55 | 100.611 | 116.55
FAUG2J | TUMM2J | 2023 | Removed | 77.2 | 0 | OHL | 0.211 | 3.128 | 22.063 | 1910 | 1766.75 | 1525.135 | 1766.75
FWIL1Q | LOCL1Q | 2023 | Removed | 34.9 | 0 | OHL | 3.55 | 8.11 | 1.73 | 126 | 116.55 | 100.611 | 116.55
FWIL1R | LOCL1R | 2023 | Removed | 34.9 | 0 | OHL | 3.55 | 8.11 | 1.73 | 126 | 116.55 | 100.611 | 116.55
INGA1Q | LOCL1R | 2023 | Removed | 0 | 2.4 | Cable | 0.25 | 0.58 | 0.12 | 126 | 116.55 | 100.611 | 116.55
MOTA1Q | SHIN1- | 2023 | Removed | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 131.9999 | 122.0999 | 105.402 | 122.0999
MOTA1R | SHIN1- | 2023 | Removed | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 126 | 116.55 | 100.611 | 116.55
SHIN1- | LOCB1J | 2023 | Removed | 12.19 | 0 | OHL | 1.2402 | 2.8392 | 0.602 | 126 | 116.55 | 100.611 | 116.55
SHIN1- | LOCB1K | 2023 | Removed | 12.18 | 0 | OHL | 1.239 | 2.8364 | 0.604 | 126 | 116.55 | 100.611 | 116.55
TUMM4- | FAUG4J | 2023 | Removed | 77.2 | 0 | OHL | 0.1 | 1.478 | 46.678 | 2779.997 | 2571.4972 | 2219.8276 | 2571.4972

## B-2-2b
Table B.2.2b - SPT Circuit Changes 2015/16 to 2023/24 | [13 empty] | Back To Menu
Node 1 | Node 2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Winter Rating (MVA) | Autumn Rating (MVA) | Summer Rating (MVA) | Spring Rating (MVA)
BLKX1- | LINM1Q | 2015 | Addition | 12.85 | 5.24 | Composite | 1.194 | 2.501 | 3.861 | 109.9999 | 101.75 | 87.835 | 101.75
BONB2J | DENN2- | 2015 | Addition | 20.2 | 0.275 | Composite | 0.0559 | 0.8594 | 7.9258 | 1031.2483 | 953.9047 | 823.4518 | 953.9047
BONB4- | DENN4- | 2015 | Addition | 20.2 | 0 | OHL | 0.0262 | 0.403 | 11.8293 | 2520.0002 | 2331.0002 | 2012.2202 | 2331.0002
COYL2- | NECU2- | 2015 | Addition | 14.3 | 0 | OHL | 0.0526 | 0.6476 | 3.6679 | 1380.0002 | 1276.5002 | 1101.9301 | 1276.5002
COYL2- | NECU2- | 2015 | Addition | 14.3 | 0 | OHL | 0.0526 | 0.6476 | 3.6679 | 1380.0002 | 1276.5002 | 1101.9301 | 1276.5002
CRUA2Q | DALL2- | 2015 | Addition | 8.56 | 0 | OHL | 0.04 | 0.36 | 4.14 | 283 | 261.775 | 225.9755 | 261.775
CRUA2R | DALL2- | 2015 | Addition | 8.56 | 0 | OHL | 0.04 | 0.36 | 4.14 | 283 | 261.775 | 225.9755 | 261.775
ECCL4A | STWB4Q | 2015 | Addition | 7.39 | 0 | OHL | 0.006 | 0.121 | 5.111 | 2769.9996 | 2562.2496 | 2211.8447 | 2562.2496
ECCL4B | STWB4R | 2015 | Addition | 7.39 | 0 | OHL | 0.006 | 0.121 | 5.111 | 2769.9996 | 2562.2496 | 2211.8447 | 2562.2496
ELVA4- | GRNA4A | 2015 | Addition | 65.54 | 0 | OHL | 0.114 | 1.245 | 39.2409 | 2209.9998 | 2044.2498 | 1764.6849 | 2044.2498
HAKB4- | MOFF4A | 2015 | Addition | 43.79 | 0 | OHL | 0.076 | 0.832 | 26.218 | 2209.9998 | 2044.2498 | 1764.6849 | 2044.2498
HUER4- | HUNE4- | 2015 | Addition | 0 | 0.001 | Cable | 0 | 0 | 0 | 2769.9996 | 2562.2496 | 2211.8447 | 2562.2496
HUER4- | HUNE4- | 2015 | Addition | 0 | 0.001 | Cable | 0 | 0 | 0 | 2769.9996 | 2562.2496 | 2211.8447 | 2562.2496
HUNE2A | HUNE2C | 2015 | Addition | 0 | 3.3 | Cable | 0.034 | 0.118 | 8.5302 | 240.0001 | 222.0001 | 191.6401 | 222.0001
HUNE2B | HUNE2D | 2015 | Addition | 0 | 3.3 | Cable | 0.034 | 0.118 | 8.5302 | 240.0001 | 222.0001 | 191.6401 | 222.0001
ECCL4- | TORN4- | 2015 | Change | 36.19 | 0 | OHL | 0.0487 | 0.6299 | 106.6266 | 1890 | 1748.25 | 1509.165 | 1748.25
ECCL4- | TORN4- | 2015 | Change | 36.19 | 0 | OHL | 0.0487 | 0.6299 | 106.6266 | 1890 | 1748.25 | 1509.165 | 1748.25
BONB1J | BONN1- | 2015 | Removed | 21.45 | 0 | OHL | 2.19 | 5.01 | 1.07 | 120 | 111 | 95.82 | 111
BONB1K | BONN1- | 2015 | Removed | 21.58 | 0 | OHL | 2.18 | 4.97 | 1.06 | 120 | 111 | 95.82 | 111
CRUA2Q | DALL2- | 2015 | Removed | 8.56 | 0 | OHL | 0.04 | 0.36 | 4.14 | 283 | 261.775 | 225.9755 | 261.775
CRUA2R | DALL2- | 2015 | Removed | 8.56 | 0 | OHL | 0.04 | 0.36 | 4.14 | 283 | 261.775 | 225.9755 | 261.775
ECCL4- | STWB4Q | 2015 | Removed | 7.39 | 0 | OHL | 0.006 | 0.121 | 5.111 | 2769.9996 | 2562.2496 | 2211.8447 | 2562.2496
ECCL4- | STWB4R | 2015 | Removed | 7.39 | 0 | OHL | 0.006 | 0.121 | 5.111 | 2769.9996 | 2562.2496 | 2211.8447 | 2562.2496
ELVA4- | GRNA4- | 2015 | Removed | 65.54 | 0 | OHL | 0.114 | 1.245 | 39.2409 | 2209.9998 | 2044.2498 | 1764.6849 | 2044.2498
HAKB4- | MOFF4- | 2015 | Removed | 43.79 | 0 | OHL | 0.076 | 0.832 | 26.218 | 2209.9998 | 2044.2498 | 1764.6849 | 2044.2498
BLAC1- | DUNH1Q | 2016 | Addition | 1.15 | 0 | OHL | 0.029 | 0.2025 | 0.0763 | 386 | 357.05 | 308.221 | 357.05
BLAC1- | DUNH1R | 2016 | Addition | 1.15 | 0 | OHL | 0.029 | 0.2025 | 0.0763 | 386 | 357.05 | 308.221 | 357.05
BLAC1- | GLGL1Q | 2016 | Addition | 0 | 13.6 | Cable | 1.1998 | 2.9137 | 1.3097 | 125 | 115.625 | 99.8125 | 115.625
BLAC1- | GLGL1R | 2016 | Addition | 0 | 13.6 | Cable | 1.1998 | 2.9137 | 1.3097 | 125 | 115.625 | 99.8125 | 115.625
BONN1- | DENN1- | 2016 | Addition | 4.5 | 0 | OHL | 0.409 | 1.0375 | 0.2234 | 131.9999 | 122.0999 | 105.402 | 122.0999
COCK2- | SMEA2R | 2016 | Addition | 9.51 | 0 | OHL | 0.0434 | 0.4198 | 2.4869 | 955 | 883.375 | 762.5675 | 883.375
COYW2S | KILS2- | 2016 | Addition | 13.37 | 0 | OHL | 0.0597 | 0.5894 | 3.5 | 805.9233 | 745.479 | 643.5297 | 745.479
COYW2T | KILS2- | 2016 | Addition | 13.37 | 0 | OHL | 0.0597 | 0.5894 | 3.5 | 805.9233 | 745.479 | 643.5297 | 745.479
DERS1Q | NECU1- | 2016 | Addition | 6.4 | 4.3 | Cable | 0.9288 | 2.6593 | 1.4302 | 132.6 | 122.655 | 105.8811 | 122.655
DUNH1Q | DUNH1S | 2016 | Addition | 0 | 0.1 | Cable | 0.005 | 0.011 | 0.0821 | 133 | 123.025 | 106.2005 | 123.025
DUNH1Q | NECU1- | 2016 | Addition | 13.65 | 0 | OHL | 0.344 | 2.4031 | 0.9058 | 386 | 357.05 | 308.221 | 357.05
DUNH1R | DUNH1T | 2016 | Addition | 0 | 0.1 | Cable | 0.005 | 0.011 | 0.0821 | 133 | 123.025 | 106.2005 | 123.025
DUNH1R | NECU1- | 2016 | Addition | 13.65 | 0 | OHL | 0.344 | 2.4031 | 0.9058 | 386 | 357.05 | 308.221 | 357.05
EWEH1Q | NEWF1Q | 2016 | Addition | 8.85 | 0 | OHL | 0.6509 | 1.9489 | 0.4654 | 133 | 123.025 | 106.2005 | 123.025
HUNC4- | HUNE4- | 2016 | Addition | 0 | 0.5 | Cable | 0.0011 | 0.0047 | 4.0212 | 1212.4356 | 1121.5029 | 968.1298 | 1121.5029
HUNC4- | HUNE4- | 2016 | Addition | 0 | 0.5 | Cable | 0.0011 | 0.0047 | 4.0212 | 1212.4356 | 1121.5029 | 968.1298 | 1121.5029
KAIM2- | SMEA2R | 2016 | Addition | 8.78 | 0 | OHL | 0.04 | 0.3875 | 2.296 | 955 | 883.375 | 762.5675 | 883.375
LINM02 | LINMX2 | 2016 | Addition | 0 | 0.79 | Cable | 0.5209 | 0.7518 | 0.0755 | 21.675 | 20.0494 | 17.3075 | 20.0494
LINM02 | LINMX2 | 2016 | Addition | 0 | 0.79 | Cable | 0.5209 | 0.7518 | 0.0755 | 21.675 | 20.0494 | 17.3075 | 20.0494
LINM02 | LINMX9 | 2016 | Addition | 10.63 | 0 | OHL | 8.5135 | 31.0933 | 0.0426 | 48.25 | 44.6312 | 38.5276 | 44.6312
NEIL2- | WIYH2R | 2016 | Addition | 25.434 | 2e-06 | Composite | 0.1068 | 1.1268 | 6.671 | 955 | 883.375 | 762.5675 | 883.375
SMEA4Q | WISH4Q | 2016 | Addition | 64.15 | 0 | OHL | 0.1273 | 1.3845 | 34.5373 | 2119.9997 | 1960.9997 | 1692.8198 | 1960.9997
SMEA4R | WISH4- | 2016 | Addition | 61.77 | 0 | OHL | 0.1226 | 1.3331 | 33.256 | 2119.9997 | 1960.9997 | 1692.8198 | 1960.9997
STHA4- | WISH4- | 2016 | Addition | 11.61 | 0 | OHL | 0.023 | 0.2506 | 6.2506 | 2119.9997 | 1960.9997 | 1692.8198 | 1960.9997
STHA4- | WISH4Q | 2016 | Addition | 11.61 | 0 | OHL | 0.023 | 0.2506 | 6.2506 | 2119.9997 | 1960.9997 | 1692.8198 | 1960.9997
AUCH2- | MAHI2- | 2016 | Change | 14.5 | 0 | OHL | 0.1062 | 0.824 | 2.953 | 689.9999 | 638.2499 | 550.9649 | 638.2499
COCK2- | SMEA2- | 2016 | Change | 9.51 | 0 | OHL | 0.0434 | 0.4198 | 2.4869 | 955 | 883.375 | 762.5675 | 883.375
COYL2- | COYW2S | 2016 | Change | 1.34 | 0 | OHL | 0.006 | 0.0591 | 0.3504 | 805.9232 | 745.479 | 643.5297 | 745.479
COYL2- | COYW2T | 2016 | Change | 1.32 | 0 | OHL | 0.0059 | 0.0583 | 0.3452 | 805.9232 | 745.479 | 643.5297 | 745.479
COYL2- | MAHI2- | 2016 | Change | 49.5 | 0 | OHL | 0.3627 | 2.8129 | 10.081 | 689.9999 | 638.2499 | 550.9649 | 638.2499
ECCL4- | TORN4- | 2016 | Change | 36.48 | 0 | OHL | 0.0491 | 0.6349 | 107.481 | 1890 | 1748.25 | 1509.165 | 1748.25
ECCL4- | TORN4- | 2016 | Change | 36.48 | 0 | OHL | 0.0491 | 0.6349 | 107.481 | 1890 | 1748.25 | 1509.165 | 1748.25
EWEH1Q | GRNA1- | 2016 | Change | 0 | 15.75 | Cable | 0.9174 | 3.5872 | 1.2067 | 168.9992 | 156.3243 | 134.9459 | 156.3243
HUNE4- | NEIL4Q | 2016 | Change | 35.782 | 2e-06 | Composite | 0.0707 | 0.7505 | 19.8193 | 1349.9999 | 1248.7499 | 1077.9749 | 1248.7499
KAIM2- | SMEA2- | 2016 | Change | 8.64 | 0 | OHL | 0.0394 | 0.3814 | 2.2594 | 955 | 883.375 | 762.5675 | 883.375
MEAD1- | MEAD1B | 2016 | Change | 0 | 1 | Cable | 0 | 0.011 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
COCK2- | KAIM2- | 2016 | Removed | 18.29 | 0 | OHL | 0.092 | 0.756 | 5.119 | 1090.0017 | 1008.2515 | 870.3663 | 1008.2515
COYW2S | KILS2- | 2016 | Removed | 13.37 | 0 | OHL | 0.068 | 0.561 | 3.8 | 955 | 883.375 | 762.5675 | 883.375
COYW2T | KILS2- | 2016 | Removed | 13.37 | 0 | OHL | 0.068 | 0.561 | 3.8 | 955 | 883.375 | 762.5675 | 883.375
NEIL2- | WIYH2R | 2016 | Removed | 25.434 | 2e-06 | Composite | 0.1068 | 1.1268 | 6.671 | 955 | 883.375 | 762.5675 | 883.375
SMEA2- | WISH2- | 2016 | Removed | 61.77 | 0 | OHL | 0.312 | 2.556 | 17.328 | 949.9987 | 878.7488 | 758.574 | 878.7488
SMEA4Q | STHA4- | 2016 | Removed | 75.76 | 0 | OHL | 0.176 | 1.446 | 43.893 | 1389.9985 | 1285.7486 | 1109.9138 | 1285.7486
STHA2A | WISH2- | 2016 | Removed | 11.61 | 0 | OHL | 0.062 | 0.504 | 3.418 | 1050.0008 | 971.2507 | 838.4256 | 971.2507
BLCW1- | MARG1- | 2017 | Addition | 1.8 | 0 | OHL | 0.1324 | 0.3964 | 0.0947 | 133 | 123.025 | 106.2005 | 123.025
DENN2- | LAMB2T | 2017 | Addition | 32.18 | 0 | OHL | 0.1468 | 1.4204 | 8.4153 | 955 | 883.375 | 762.5675 | 883.375
DENN2- | LOAN2- | 2017 | Addition | 21.35 | 0 | OHL | 0.049 | 0.8363 | 6.3429 | 1910 | 1766.75 | 1525.135 | 1766.75
KEON1- | KEOO1Q | 2017 | Addition | 2.4 | 0 | OHL | 0.0605 | 0.4225 | 0.1593 | 386 | 357.05 | 308.221 | 357.05
KEON1- | NECU1Q | 2017 | Addition | 23 | 0 | OHL | 0.5797 | 4.0492 | 1.5263 | 386 | 357.05 | 308.221 | 357.05
KEON1R | KEOO1R | 2017 | Addition | 2.4 | 0 | OHL | 0.0605 | 0.4225 | 0.1593 | 386 | 357.05 | 308.221 | 357.05
KEON1R | NECU1R | 2017 | Addition | 23 | 0 | OHL | 0.5797 | 4.0492 | 1.5263 | 386 | 357.05 | 308.221 | 357.05
KEOO1- | KEOO1R | 2017 | Addition | 0 | 2.5 | Cable | 0.2525 | 0.5625 | 0.1275 | 123 | 113.775 | 98.2155 | 113.775
KEOO1Q | MARG1- | 2017 | Addition | 0 | 10.9 | Cable | 0.5476 | 2.2264 | 0.167 | 201 | 185.925 | 160.4985 | 185.925
DENN2R | LAMB2T | 2017 | Removed | 32.18 | 0 | OHL | 0.1468 | 1.4204 | 8.4153 | 955 | 883.375 | 762.5675 | 883.375
DENN2R | LOAN2- | 2017 | Removed | 21.35 | 0 | OHL | 0.049 | 0.8363 | 6.3429 | 1910 | 1766.75 | 1525.135 | 1766.75
AIKE1- | WDOD1- | 2018 | Addition | 0 | 3.7 | Cable | 0.0704 | 0.2402 | 4.6583 | 126 | 116.55 | 100.611 | 116.55
BRAE1G | BRAP1Q | 2018 | Addition | 7.02 | 0 | OHL | 0.0955 | 0.7188 | 10.9765 | 250.0008 | 231.2508 | 199.6257 | 231.2508
BRAP1Q | ERSK1Q | 2018 | Addition | 9.81 | 0 | OHL | 0.6954 | 1.4576 | 14.752 | 121.0001 | 111.9251 | 96.6185 | 111.9251
DEVM1- | ERSK1R | 2018 | Addition | 17.5 | 0 | OHL | 1.5897 | 4.2184 | 0.8375 | 131.9999 | 122.0999 | 105.402 | 122.0999
DUNE1- | ROWA1- | 2018 | Addition | 0 | 7.5 | Cable | 0.4432 | 1.7494 | 0.3715 | 164 | 151.7 | 130.954 | 151.7
EHAU1- | MOFF1- | 2018 | Addition | 0 | 14.45 | Cable | 0.6502 | 2.5618 | 0.0778 | 201 | 185.925 | 160.4985 | 185.925
GALA1- | ROWA1- | 2018 | Addition | 0 | 16.14 | Cable | 0.9538 | 3.7646 | 0.7995 | 164 | 151.7 | 130.954 | 151.7
KILS1- | MEAD1- | 2018 | Addition | 0 | 12.57 | Cable | 0.874 | 2.581 | 2.166 | 161.9999 | 149.8499 | 129.357 | 149.8499
BONB2J | DENN2- | 2018 | Change | 20.2 | 0.275 | Composite | 0.0559 | 0.864 | 7.904 | 1031.2483 | 953.9047 | 823.4518 | 953.9047
BONB4- | DENN4- | 2018 | Change | 20.2 | 0 | OHL | 0.0262 | 0.4052 | 11.7832 | 2520.0002 | 2331.0002 | 2012.2202 | 2331.0002
DEVM1- | ERSK1Q | 2018 | Change | 17.5 | 0 | OHL | 1.5897 | 4.2184 | 0.8375 | 131.9999 | 122.0999 | 105.402 | 122.0999
KEOO1- | KEOO1R | 2018 | Change | 0 | 2.5 | Cable | 0.252 | 0.563 | 0.1275 | 131.9999 | 122.0999 | 105.402 | 122.0999
KEOO1Q | MARG1- | 2018 | Change | 0 | 10.9 | Cable | 0.548 | 2.226 | 1.664 | 201 | 185.925 | 160.4985 | 185.925
BRAE1G | BRAP1- | 2018 | Removed | 2.5 | 0 | OHL | 0.034 | 0.256 | 3.909 | 250.0008 | 231.2508 | 199.6257 | 231.2508
BRAP1- | ERSK1Q | 2018 | Removed | 9.55 | 0 | OHL | 0.677 | 1.419 | 14.361 | 121.0001 | 111.9251 | 96.6185 | 111.9251
DUNE1- | GALA1- | 2018 | Removed | 0 | 23.64 | Cable | 1.397 | 5.514 | 1.171 | 152.0001 | 140.6001 | 121.3721 | 140.6001
KILS1- | MEAD1B | 2018 | Removed | 0 | 12.57 | Cable | 0.874 | 2.581 | 2.166 | 161.9999 | 149.8499 | 129.357 | 149.8499
MEAD1- | MEAD1B | 2018 | Removed | 0 | 1 | Cable | 0 | 0.011 | 0 | 100.0001 | 92.5001 | 79.8501 | 92.5001
AREC1- | GLLR1- | 2020 | Addition | 0 | 15 | Cable | 1.1286 | 3.3032 | 0.7889 | 140 | 129.5 | 111.79 | 129.5
COAL1- | GAWH1Q | 2020 | Addition | 0 | 10 | Cable | 0.7472 | 2.1683 | 0.535 | 140 | 129.5 | 111.79 | 129.5
HUER4- | KILS4T | 2020 | Addition | 59.125 | 2e-06 | Composite | 0.0836 | 1.1482 | 35.509 | 1999.9999 | 1849.9999 | 1596.9999 | 1849.9999
KEON1- | LURR1- | 2020 | Addition | 20 | 0 | OHL | 1.4709 | 4.4043 | 1.0518 | 133 | 123.025 | 106.2005 | 123.025
KILG2- | MAHI2- | 2020 | Addition | 10 | 0 | OHL | 0.1062 | 0.4578 | 2.5133 | 552.0831 | 510.6769 | 440.8384 | 510.6769
KILS4T | STHA4- | 2020 | Addition | 34.988 | 2e-06 | Composite | 0.0695 | 0.7354 | 19.312 | 1999.9999 | 1849.9999 | 1596.9999 | 1849.9999
KINB4J | KINB4V | 2020 | Addition | 10.15 | 0 | OHL | 0.0219 | 0.2118 | 5.6235 | 1389.9999 | 1285.7499 | 1109.9149 | 1285.7499
KINB4K | KINC4A | 2020 | Addition | 10.5 | 0 | OHL | 0.0226 | 0.2191 | 5.8174 | 1389.9999 | 1285.7499 | 1109.9149 | 1285.7499
KINB4V | KINC4B | 2020 | Addition | 0 | 0.35 | Cable | 0.0002 | 0.0043 | 7.2659 | 1250.0003 | 1156.2503 | 998.1252 | 1156.2503
HUER4- | STHA4- | 2020 | Removed | 94.113 | 2e-06 | Composite | 0.153 | 1.8835 | 54.821 | 1999.9999 | 1849.9999 | 1596.9999 | 1849.9999
KINB2J | KINC2- | 2020 | Removed | 10.57 | 0 | OHL | 0.05 | 0.43 | 7.18 | 760.0018 | 703.0017 | 606.8614 | 703.0017
KINB2K | KINC2- | 2020 | Removed | 10.59 | 0 | OHL | 0.05 | 0.43 | 2.93 | 909.9978 | 841.748 | 726.6333 | 841.748
AUCH2- | NETS2- | 2023 | Addition | 40 | 0 | OHL | 0.1443 | 1.7282 | 10.6696 | 1540.0183 | 1424.517 | 1229.7046 | 1424.517
AUCH2- | NETS2- | 2023 | Addition | 40 | 0 | OHL | 0.1443 | 1.7282 | 10.6696 | 1540.0183 | 1424.517 | 1229.7046 | 1424.517
BONB2J | DENN2B | 2023 | Addition | 20.2 | 0.275 | Composite | 0.0559 | 0.8594 | 7.9258 | 1031.2483 | 953.9047 | 823.4518 | 953.9047
BONN2- | DENN2B | 2023 | Addition | 4 | 0 | OHL | 0.0168 | 0.1826 | 1.0179 | 1457.4998 | 1348.1873 | 1163.8136 | 1348.1873
BONN2- | NEAR2T | 2023 | Addition | 17 | 0 | OHL | 0.0714 | 0.7762 | 4.326 | 1457.4998 | 1348.1873 | 1163.8136 | 1348.1873
BONN4- | DENN4- | 2023 | Addition | 4 | 0 | OHL | 0.0079 | 0.0863 | 2.1535 | 2119.9997 | 1960.9997 | 1692.8198 | 1960.9997
BONN4- | WISH4- | 2023 | Addition | 40.36 | 0 | OHL | 0.0801 | 0.8561 | 22.0883 | 2119.9998 | 1960.9998 | 1692.8198 | 1960.9998
BRNX4- | ECCL4- | 2023 | Addition | 34.28 | 0 | OHL | 0.0444 | 0.6876 | 19.9964 | 2520.0002 | 2331.0002 | 2012.2202 | 2331.0002
BRNX4- | ECCL4- | 2023 | Addition | 34.28 | 0 | OHL | 0.0444 | 0.6876 | 19.9964 | 2520.0002 | 2331.0002 | 2012.2202 | 2331.0002
BRNX4- | TORN4- | 2023 | Addition | 0 | 2.2 | Cable | 0.001 | 0.018 | 86.24 | 1890 | 1748.25 | 1509.165 | 1748.25
BRNX4- | TORN4- | 2023 | Addition | 0 | 2.2 | Cable | 0.001 | 0.018 | 86.24 | 1890 | 1748.25 | 1509.165 | 1748.25
COAL1- | KENN1- | 2023 | Addition | 17 | 0 | OHL | 1.2502 | 3.7436 | 0.8941 | 166.0088 | 153.5581 | 132.558 | 153.5581
COAL1- | KYPE1- | 2023 | Addition | 11 | 0 | OHL | 0.809 | 2.4224 | 0.5785 | 166.0088 | 153.5581 | 132.558 | 153.5581
COAT2Q | NEAR2- | 2023 | Addition | 8.3 | 0 | OHL | 0.047 | 0.26 | 16.299 | 175.9999 | 162.7999 | 140.5359 | 162.7999
COAT2R | NEAR2- | 2023 | Addition | 8.3 | 0 | OHL | 0.047 | 0.26 | 16.299 | 175.9999 | 162.7999 | 140.5359 | 162.7999
DENN2A | LAMB2- | 2023 | Addition | 32.18 | 0 | OHL | 0.1468 | 1.4204 | 8.4153 | 955 | 883.375 | 762.5675 | 883.375
DENN2A | LOAN2- | 2023 | Addition | 21.35 | 0 | OHL | 0.049 | 0.8363 | 6.3429 | 1910 | 1766.75 | 1525.135 | 1766.75
DENN2B | LAMB2T | 2023 | Addition | 32.18 | 0 | OHL | 0.1468 | 1.4204 | 8.4153 | 955 | 883.375 | 762.5675 | 883.375
DENN2B | LOAN2- | 2023 | Addition | 21.35 | 0 | OHL | 0.049 | 0.8363 | 6.3429 | 1910 | 1766.75 | 1525.135 | 1766.75
DUMF4- | HAKB4R | 2023 | Addition | 40.14 | 0 | OHL | 0.0682 | 0.8111 | 23.1305 | 2009.9999 | 1859.2499 | 1604.9849 | 1859.2499
EERH2- | NEAR2T | 2023 | Addition | 7.74 | 0 | OHL | 0.0326 | 0.3428 | 2.024 | 1457.4998 | 1348.1873 | 1163.8136 | 1348.1873
GLLE1- | TONG1- | 2023 | Addition | 33.1 | 0 | OHL | 2.4416 | 7.7756 | 1.6326 | 166.0088 | 153.5581 | 132.558 | 153.5581
GLLE2- | DUMF2- | 2023 | Addition | 46 | 0 | OHL | 0.1659 | 1.9874 | 12.27 | 1540.0183 | 1424.517 | 1229.7046 | 1424.517
GLLE2- | DUMF2- | 2023 | Addition | 46 | 0 | OHL | 0.1659 | 1.9874 | 12.27 | 1540.0183 | 1424.517 | 1229.7046 | 1424.517
GLLE2- | NETS2- | 2023 | Addition | 34 | 0 | OHL | 0.1227 | 1.469 | 9.0692 | 1540.0183 | 1424.517 | 1229.7046 | 1424.517
GLLE2- | NETS2- | 2023 | Addition | 34 | 0 | OHL | 0.1227 | 1.469 | 9.0692 | 1540.0183 | 1424.517 | 1229.7046 | 1424.517
GLMT1- | NECU1- | 2023 | Addition | 13 | 0 | OHL | 0.9561 | 2.8628 | 0.6837 | 166.0088 | 153.5581 | 132.558 | 153.5581
HAKB4Q | DUMF4- | 2023 | Addition | 40.14 | 0 | OHL | 0.0682 | 0.8111 | 23.1305 | 2009.9999 | 1859.2499 | 1604.9849 | 1859.2499
KEON1- | KEOO1R | 2023 | Addition | 2.4 | 0 | OHL | 0.0605 | 0.4225 | 0.1593 | 386 | 357.05 | 308.221 | 357.05
KEON1- | NECU1R | 2023 | Addition | 23 | 0 | OHL | 0.5797 | 4.0492 | 1.5263 | 386 | 357.05 | 308.221 | 357.05
KEOO1- | GLLE1- | 2023 | Addition | 7.68 | 0 | OHL | 0.1897 | 1.2686 | 0.5368 | 481.9993 | 445.8493 | 384.8764 | 445.8493
KEOO1Q | KEOO1- | 2023 | Addition | 2.5 | 0 | OHL | 0.0618 | 0.4129 | 0.1747 | 481.9993 | 445.8493 | 384.8764 | 445.8493
NEAR2- | NEAR2T | 2023 | Addition | 7.6 | 0 | OHL | 0.0319 | 0.3368 | 1.9892 | 1457.4998 | 1348.1873 | 1163.8136 | 1348.1873
NEAR2- | WISH2- | 2023 | Addition | 15.76 | 0 | OHL | 0.0662 | 0.6983 | 4.125 | 1457.4998 | 1348.1873 | 1163.8136 | 1348.1873
BONB4- | DENN4- | 2023 | Change | 20.2 | 0 | OHL | 0.0262 | 0.403 | 11.8293 | 2520.0002 | 2331.0002 | 2012.2202 | 2331.0002
CAFA1Q | KEOO1- | 2023 | Change | 0 | 2.58 | Cable | 0.258 | 0.584 | 0.126 | 131.9999 | 122.0999 | 105.402 | 122.0999
EAST1Q | GLLE1- | 2023 | Change | 0 | 1.69 | Cable | 0.172 | 0.39 | 0.084 | 131.9999 | 122.0999 | 105.402 | 122.0999
GLLE1- | KEOO1- | 2023 | Change | 7.68 | 0 | OHL | 0.1897 | 1.2686 | 0.5368 | 481.9993 | 445.8493 | 384.8764 | 445.8493
GLLE1- | TONG1- | 2023 | Change | 33.1 | 0 | OHL | 2.4416 | 7.7756 | 1.6326 | 166.0088 | 153.5581 | 132.558 | 153.5581
KEOO1- | KEOO1R | 2023 | Change | 2.5 | 0 | OHL | 0.0618 | 0.4129 | 0.1747 | 481.9993 | 445.8493 | 384.8764 | 445.8493
BONB2J | DENN2- | 2023 | Removed | 20.2 | 0.275 | Composite | 0.0559 | 0.864 | 7.904 | 1031.2483 | 953.9047 | 823.4518 | 953.9047
BONN2A | DENN2- | 2023 | Removed | 4 | 0 | OHL | 0.0182 | 0.182 | 1.018 | 955 | 883.375 | 762.5675 | 883.375
BONN2B | DENN2- | 2023 | Removed | 4 | 0 | OHL | 0.0182 | 0.182 | 1.018 | 955 | 883.375 | 762.5675 | 883.375
COAT2Q | NEAR2Q | 2023 | Removed | 8.3 | 0 | OHL | 0.047 | 0.26 | 16.299 | 175.9999 | 162.7999 | 140.5359 | 162.7999
COAT2R | NEAR2R | 2023 | Removed | 8.3 | 0 | OHL | 0.047 | 0.26 | 16.299 | 175.9999 | 162.7999 | 140.5359 | 162.7999
DENN2- | LAMB2- | 2023 | Removed | 32.18 | 0 | OHL | 0.1468 | 1.4204 | 8.4153 | 955 | 883.375 | 762.5675 | 883.375
DENN2- | LAMB2T | 2023 | Removed | 32.18 | 0 | OHL | 0.1468 | 1.4204 | 8.4153 | 955 | 883.375 | 762.5675 | 883.375
DENN2- | LOAN2- | 2023 | Removed | 21.35 | 0 | OHL | 0.049 | 0.8363 | 6.3429 | 1910 | 1766.75 | 1525.135 | 1766.75
DENN2- | LOAN2- | 2023 | Removed | 21.35 | 0 | OHL | 0.049 | 0.8363 | 6.3429 | 1910 | 1766.75 | 1525.135 | 1766.75
ECCL4- | TORN4- | 2023 | Removed | 36.48 | 0 | OHL | 0.0491 | 0.6349 | 107.481 | 1890 | 1748.25 | 1509.165 | 1748.25
ECCL4- | TORN4- | 2023 | Removed | 36.48 | 0 | OHL | 0.0491 | 0.6349 | 107.481 | 1890 | 1748.25 | 1509.165 | 1748.25
EERH2- | NEAR2Q | 2023 | Removed | 0 | 15.34 | Cable | 0.077 | 0.632 | 4.283 | 949.9987 | 878.7488 | 758.574 | 878.7488
GLLE1- | NETS1- | 2023 | Removed | 30.04 | 0 | OHL | 3.035 | 6.767 | 1.759 | 125 | 115.625 | 99.8125 | 115.625
GLLE1- | NETS1- | 2023 | Removed | 30.04 | 0 | OHL | 3.034 | 6.759 | 1.532 | 125 | 115.625 | 99.8125 | 115.625
KEON1R | KEOO1R | 2023 | Removed | 2.4 | 0 | OHL | 0.0605 | 0.4225 | 0.1593 | 386 | 357.05 | 308.221 | 357.05
KEON1R | NECU1R | 2023 | Removed | 23 | 0 | OHL | 0.5797 | 4.0492 | 1.5263 | 386 | 357.05 | 308.221 | 357.05
NEAR2Q | WISH2- | 2023 | Removed | 16.1 | 0 | OHL | 0.079 | 0.646 | 4.38 | 955 | 883.375 | 762.5675 | 883.375
NEAR2R | WISH2- | 2023 | Removed | 16.1 | 0 | OHL | 0.079 | 0.646 | 4.38 | 285.0001 | 263.6251 | 227.5726 | 263.6251

## B-2-2c
Table B.2.2c - NGET Circuit Changes 2015/16 to 2022/13 | [13 empty] | Back To Menu
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
ABTH22 | UPPB21 | 2015 | Change | 27.035 | 1.094 | parallel Composite | 0.124 | 1.1519 | 19.226 | 770 | 712.25 | 614.845 | 712.25
BUST2* | DRAK41 | 2015 | Addition | 34.592 | 0 | OHL | 0.0375 | 0.6017 | 22.8035 | 2780 | 2571.5 | 2219.83 | 2571.5
BUST21 | DRAK21 | 2015 | Change | 34.537 | 0 | OHL | 0.0793 | 1.2709 | 10.7606 | 1200 | 1110 | 958.2 | 1110
CONQ41 | CAPE41 | 2015 | Addition | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3580 | 3311.5 | 2858.63 | 3311.5
CONQ41 | CAPE42 | 2015 | Addition | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3580 | 3311.5 | 2858.63 | 3311.5
DAIN4* | SMAN21 | 2015 | Addition | 11.393 | 0.61 | Composite | 0.05 | 0.5093 | 6.1691 | 1380 | 1276.5 | 1101.93 | 1276.5
DAIN4* | SMAN21 | 2015 | Addition | 8.418 | 0.23 | Composite | 0.0384 | 0.3775 | 3.375 | 835 | 772.375 | 666.7475 | 772.375
DAIN41 | MACC41 | 2015 | Change | 33.593 | 2.83 | parallel Composite | 0.054 | 0.656 | 75.0798 | 2400 | 2220 | 1916.4 | 2220
DRAX42 | THOM41 | 2015 | Change | 21.73 | 0.916 | parallel Composite | 0.0312 | 0.4019 | 23.6427 | 2980 | 2756.5 | 2379.53 | 2756.5
EGGB41 | THOM41 | 2015 | Change | 28.323 | 0.197 | Composite | 0.0295 | 0.494 | 22.0219 | 2220 | 2053.5 | 1772.67 | 2053.5
HACK41 | SJOW41 | 2015 | Addition | 0 | 15 | Cable | 0.0105 | 0.165 | 300 | 1600 | 1480 | 1277.6 | 1480
HEYS41 | MIDL41 | 2015 | Addition | 0.9 | 0 | OHL | 0.0008 | 0.0155 | 0.6039 | 3820 | 3533.5 | 3050.27 | 3533.5
HEYS41 | QUER4B | 2015 | Change | 9.604 | 0 | OHL | 0.0085 | 0.165 | 6.4316 | 3330 | 3080.25 | 2659.005 | 3080.25
IRON41 | OSWE * | 2015 | Addition | 27.261 | 0 | OHL | 0.0436 | 0.5243 | 16.3927 | 2400 | 2220 | 1916.4 | 2220
LEGA41 | OSWE * | 2015 | Addition | 34.812 | 0 | OHL | 0.0556 | 0.6695 | 20.9333 | 2400 | 2220 | 1916.4 | 2220
LEGA41 | OSWE * | 2015 | Addition | 34.812 | 0 | OHL | 0.0556 | 0.6695 | 20.9333 | 2400 | 2220 | 1916.4 | 2220
MIDL41 | QUER4A | 2015 | Addition | 9.204 | 0 | OHL | 0.0082 | 0.1581 | 6.165 | 3820 | 3533.5 | 3050.27 | 3533.5
NEWX21 | NEWX21 | 2015 | Addition | 0 | 0.15 | Cable | 0.0003 | 0.0034 | 1.5195 | 99999 | 92499.075 | 79849.2015 | 92499.075
SHRE4A | OSWE * | 2015 | Addition | 12.132 | 0 | OHL | 0.0194 | 0.2333 | 7.2953 | 2400 | 2220 | 1916.4 | 2220
STAL42 | THOM41 | 2015 | Change | 71.498 | 4.978 | Composite | 0.0793 | 1.2984 | 122.5823 | 1330 | 1230.25 | 1062.005 | 1230.25
THOM4* | WMEL21 | 2015 | Change | 24.411 | 0.8 | Composite | 0.1126 | 1.0793 | 10.5875 | 765 | 707.625 | 610.8525 | 707.625
THOM4* | WMEL21 | 2015 | Change | 24.413 | 0.8 | Composite | 0.1126 | 1.0794 | 10.588 | 765 | 707.625 | 610.8525 | 707.625
TREU4B | CONQ41 | 2015 | Addition | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2210 | 2044.25 | 1764.685 | 2044.25
CAPE41 | DEES42 | 2015 | Removed | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3580 | 3311.5 | 2858.63 | 3311.5
SJOW21 | TOTT24 | 2015 | Removed | 0 | 16.508 | Cable | 0.0297 | 0.3632 | 179.4419 | 870 | 804.75 | 694.695 | 804.75
LEGA41 | SHRE4A | 2015 | Removed | 46.944 | 0 | OHL | 0.075 | 0.9028 | 28.2286 | 2000 | 1850 | 1597 | 1850
IRON41 | LEGA41 | 2015 | Removed | 62.073 | 0 | OHL | 0.0992 | 1.1938 | 37.326 | 2000 | 1850 | 1597 | 1850
CARR21 | SMAN21 | 2015 | Removed | 10.747 | 0.23 | Composite | 0.0475 | 0.476 | 5.3274 | 835 | 772.375 | 666.7475 | 772.375
CARR21 | SMAN21 | 2015 | Removed | 9.294 | 0.133 | Composite | 0.0414 | 0.4101 | 3.8882 | 835 | 772.375 | 666.7475 | 772.375
DEES42 | TREU4B | 2015 | Removed | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2210 | 2044.25 | 1764.685 | 2044.25
SJOW21 | TOTT23 | 2015 | Removed | 0 | 16.368 | Cable | 0.0295 | 0.3601 | 177.9201 | 870 | 804.75 | 694.695 | 804.75
HEYS41 | QUER4A | 2015 | Removed | 9.604 | 0 | OHL | 0.0085 | 0.165 | 6.4553 | 3330 | 3080.25 | 2659.005 | 3080.25
CAPE42 | DEES41 | 2015 | Removed | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3580 | 3311.5 | 2858.63 | 3311.5
BUST21 | DRAK21 | 2015 | Removed | 34.592 | 0 | OHL | 0.0793 | 1.2733 | 10.7739 | 1200 | 1110 | 958.2 | 1110
SHRE4B | SHRE4A | 2015 | Removed | 0.054 | 0 | OHL | 0.0001 | 0.001 | 0.0324 | 9999 | 9249.075 | 7984.2015 | 9249.075
BEDD21 | WIMB21 | 2016 | Change | 8.5 | 0.968 | Composite | 0.0412 | 0.3922 | 10.7954 | 860 | 795.5 | 686.71 | 795.5
BRFO41 | LEIS4A | 2016 | Addition | 42.436 | 0 | OHL | 0.046 | 0.7381 | 27.9744 | 2780 | 2571.5 | 2219.83 | 2571.5
BRFO41 | LEIS4B | 2016 | Addition | 42.436 | 0 | OHL | 0.046 | 0.7381 | 27.9744 | 2780 | 2571.5 | 2219.83 | 2571.5
BRFO41 | SIZE41 | 2016 | Change | 43.331 | 0 | OHL | 0.047 | 0.7537 | 28.5643 | 2780 | 2571.5 | 2219.83 | 2571.5
BRFO41 | SIZE41 | 2016 | Change | 43.331 | 0 | OHL | 0.047 | 0.7537 | 28.5643 | 2780 | 2571.5 | 2219.83 | 2571.5
BUST2* | DRAK41 | 2016 | Addition | 34.537 | 0 | OHL | 0.0375 | 0.6007 | 22.7672 | 2780 | 2571.5 | 2219.83 | 2571.5
CANT41 | SELL-T* | 2016 | Addition | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 1930 | 1785.25 | 1541.105 | 1785.25
CANT41 | SELL-T* | 2016 | Addition | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 1930 | 1785.25 | 1541.105 | 1785.25
CONQ41 | FLIB * | 2016 | Addition | 0 | 3.388 | Cable | 0.0022 | 0.0485 | 42.5749 | 2500 | 2312.5 | 1996.25 | 2312.5
CONQ41 | FLIB * | 2016 | Addition | 0 | 3.495 | Cable | 0.0022 | 0.05 | 43.9195 | 2500 | 2312.5 | 1996.25 | 2312.5
CONQ41 | TREU4A | 2016 | Addition | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2400 | 2220 | 1916.4 | 2220
DUNG41 | SELL41 | 2016 | Change | 25.387 | 0.415 | Composite | 0.0463 | 0.5071 | 29.6588 | 1850 | 1711.25 | 1477.225 | 1711.25
DUNG41 | SELW41 | 2016 | Change | 25.403 | 0.415 | Composite | 0.0463 | 0.5074 | 29.6683 | 1850 | 1711.25 | 1477.225 | 1711.25
KENG41 | SJOW41 | 2016 | Addition | 0 | 6.5 | Cable | 0.0026 | 0.0575 | 49.1184 | 2000 | 1850 | 1597 | 1850
KENG42 | SJOW41 | 2016 | Addition | 0 | 6.5 | Cable | 0.0026 | 0.0575 | 49.1184 | 2000 | 1850 | 1597 | 1850
KNAR21 | MONF21 | 2016 | Addition | 56.475 | 0.141 | Composite | 0.4582 | 2.6376 | 15.3212 | 800 | 740 | 638.8 | 740
KNAR21 | POPP21 | 2016 | Addition | 35.234 | 0 | OHL | 0.1957 | 1.8269 | 7.9098 | 800 | 740 | 638.8 | 740
LEIS4A | LEIS4* | 2016 | Addition | 0 | 0.33 | Cable | 0.0002 | 0.0039 | 3.602 | 240 | 222 | 191.64 | 222
LEIS4B | LEIS4* | 2016 | Addition | 0 | 0.481 | Cable | 0.0003 | 0.0057 | 5.2502 | 240 | 222 | 191.64 | 222
LEIS4A | SIZE41 | 2016 | Addition | 0.895 | 0 | OHL | 0.001 | 0.0156 | 0.59 | 2780 | 2571.5 | 2219.83 | 2571.5
LEIS4B | SIZE41 | 2016 | Addition | 0.895 | 0 | OHL | 0.001 | 0.0156 | 0.59 | 2780 | 2571.5 | 2219.83 | 2571.5
SELL-T* | SELL41 | 2016 | Addition | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 1930 | 1785.25 | 1541.105 | 1785.25
SELL41 | SELL-T* | 2016 | Addition | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 1930 | 1785.25 | 1541.105 | 1785.25
SELW41 | SELL-T* | 2016 | Addition | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 1930 | 1785.25 | 1541.105 | 1785.25
SELW41 | SELL-T* | 2016 | Addition | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 1930 | 1785.25 | 1541.105 | 1785.25
SELW41 | SELL41 | 2016 | Addition | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 3000 | 2775 | 2395.5 | 2775
SHRE4A | OSWE * | 2016 | Change | 12.132 | 0 | OHL | 0.0194 | 0.2333 | 7.2953 | 2000 | 1850 | 1597 | 1850
SJOW41 | HACK41 | 2016 | Addition | 0 | 15 | Cable | 0.0105 | 0.165 | 300 | 2499.9998 | 2312.4998 | 1996.2498 | 2312.4998
CANT41 | SELL41 | 2016 | Removed | 26.711 | 0.257 | Composite | 0.0417 | 0.5138 | 26.0013 | 2370 | 2192.25 | 1892.445 | 2192.25
SELL41 | SELL41 | 2016 | Removed | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 1860 | 1720.5 | 1485.21 | 1720.5
CANT41 | SELL41 | 2016 | Removed | 26.711 | 0.257 | Composite | 0.0417 | 0.5138 | 26.0013 | 2370 | 2192.25 | 1892.445 | 2192.25
BRFO41 | SIZE41 | 2016 | Removed | 43.331 | 0 | OHL | 0.047 | 0.7537 | 28.5643 | 2780 | 2571.5 | 2219.83 | 2571.5
BRFO41 | BRFO41 | 2016 | Removed | 0 | 0.2 | Cable | 0 | 0 | 0 | 3340 | 3089.5 | 2666.99 | 3089.5
MONF21 | POPP21 | 2016 | Removed | 37.709 | 0.141 | Composite | 0.357 | 1.6584 | 11.1383 | 460 | 425.5 | 367.31 | 425.5
BRFO41 | SIZE41 | 2016 | Removed | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2780 | 2571.5 | 2219.83 | 2571.5
BUST21 | DRAK21 | 2016 | Removed | 34.537 | 0 | OHL | 0.0793 | 1.2709 | 10.7606 | 1200 | 1110 | 958.2 | 1110
DEES41 | TREU4A | 2016 | Removed | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2400 | 2220 | 1916.4 | 2220
BEDD23 | WIMB21 | 2017 | Change | 8.5 | 0.582 | Composite | 0.0398 | 0.3821 | 8.4754 | 1100 | 1017.5 | 878.35 | 1017.5
CILF41 | RHIG41 | 2017 | Addition | 25.011 | 0 | OHL | 0.0271 | 0.435 | 16.4876 | 2780 | 2571.5 | 2219.83 | 2571.5
CONQ41 | GWYN4* | 2017 | Addition | 30.217 | 0 | OHL | 0.065 | 0.6323 | 16.5753 | 1710 | 1581.75 | 1365.435 | 1581.75
CONQ41 | GWYN4* | 2017 | Addition | 30.217 | 0 | OHL | 0.065 | 0.6323 | 16.5753 | 1710 | 1581.75 | 1365.435 | 1581.75
CANW4* | OSWE * | 2017 | Addition | 34.812 | 0 | OHL | 0.0556 | 0.6695 | 20.9333 | 2000 | 1850 | 1597 | 1850
HACK41 | HIBU41 | 2017 | Addition | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 2500 | 2312.5 | 1996.25 | 2312.5
HIBU41 | HACK41 | 2017 | Addition | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 2780 | 2571.5 | 2219.83 | 2571.5
NORM41 | NECT4B | 2017 | Addition | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 3820 | 3533.5 | 3050.27 | 3533.5
NECT4A | NECT41 | 2017 | Addition | 0 | 0.198 | parallel Cable | 0 | 0.0006 | 2.1612 | 2520 | 2331 | 2012.22 | 2331
NECT4B | NECT41 | 2017 | Addition | 0 | 0.198 | parallel Cable | 0 | 0.0006 | 2.1612 | 2520 | 2331 | 2012.22 | 2331
NECT4A | NORM41 | 2017 | Addition | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 2520 | 2331 | 2012.22 | 2331
NECT4B | WALP41 | 2017 | Addition | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3820 | 3533.5 | 3050.27 | 3533.5
NECT4A | WALP41 | 2017 | Addition | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3820 | 3533.5 | 3050.27 | 3533.5
PEMB41 | WALH41 | 2017 | Change | 217.427 | 5.468 | parallel Composite | 0.2368 | 3.8011 | 207.2181 | 2780 | 2571.5 | 2219.83 | 2571.5
SHRE4A | OSWE * | 2017 | Change | 12.132 | 0 | OHL | 0.0194 | 0.2333 | 7.2953 | 2400 | 2220 | 1916.4 | 2220
SJOW41 | HIBU41 | 2017 | Addition | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 2500 | 2312.5 | 1996.25 | 2312.5
SJOW41 | HIBU41 | 2017 | Addition | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 2500 | 2312.5 | 1996.25 | 2312.5
SWAN41 | RHIG41 | 2017 | Addition | 34.34 | 0 | OHL | 0.0373 | 0.5973 | 22.6374 | 2780 | 2571.5 | 2219.83 | 2571.5
CILF41 | SWAN41 | 2017 | Removed | 60 | 0 | OHL | 0.0651 | 1.0436 | 39.5528 | 2780 | 2571.5 | 2219.83 | 2571.5
SJOW41 | HACK41 | 2017 | Removed | 0 | 15 | Cable | 0.0105 | 0.165 | 300 | 2499.9998 | 2312.4998 | 1996.2498 | 2312.4998
DEES41 | GWYN4* | 2017 | Removed | 30.217 | 0 | OHL | 0.0328 | 0.5256 | 19.9194 | 2780 | 2571.5 | 2219.83 | 2571.5
NEWX21 | NEWX21 | 2017 | Removed | 0 | 0.15 | Cable | 0.0003 | 0.0034 | 1.5195 | 1140 | 1054.5 | 910.29 | 1054.5
NORM41 | WALP41 | 2017 | Removed | 79.138 | 0 | OHL | 0.0702 | 1.3593 | 53.1914 | 3510 | 3246.75 | 2802.735 | 3246.75
DEES42 | GWYN4* | 2017 | Removed | 30.217 | 0 | OHL | 0.0328 | 0.5256 | 19.9194 | 2780 | 2571.5 | 2219.83 | 2571.5
HACK41 | SJOW41 | 2017 | Removed | 0 | 15 | Cable | 0.0105 | 0.165 | 300 | 1600 | 1480 | 1277.6 | 1480
NEWX21 | NEWX21 | 2017 | Removed | 0 | 0.15 | Cable | 0.0003 | 0.0034 | 1.5195 | 99999 | 92499.075 | 79849.2015 | 92499.075
NORM41 | WALP41 | 2017 | Removed | 79.046 | 0 | OHL | 0.0701 | 1.3577 | 53.1298 | 3100 | 2867.5 | 2475.35 | 2867.5
BAGB21 | BRITT* | 2018 | Addition | 1.065 | 1.439 | parallel Composite | 0.0044 | 0.0516 | 14.2608 | 1100 | 1017.5 | 878.35 | 1017.5
BAGB21 | BRITT* | 2018 | Addition | 1.065 | 1.439 | parallel Composite | 0.0044 | 0.0516 | 14.2608 | 1650 | 1526.25 | 1317.525 | 1526.25
BRITT* | MAGA21 | 2018 | Addition | 11.564 | 0 | OHL | 0.0392 | 0.4703 | 3.2751 | 1650 | 1526.25 | 1317.525 | 1526.25
BRITT* | SWAN4* | 2018 | Addition | 17.145 | 0 | OHL | 0.0572 | 0.7166 | 4.7315 | 1650 | 1526.25 | 1317.525 | 1526.25
CANW4* | OSWE * | 2018 | Addition | 34.812 | 0 | OHL | 0.0556 | 0.6695 | 20.9333 | 2000 | 1850 | 1597 | 1850
KENG41 | SJOW41 | 2018 | Change | 0 | 6 | Cable | 0.0027 | 0.0477 | 43.6608 | 2000 | 1850 | 1597 | 1850
KENG41 | WIMB41 | 2018 | Addition | 0 | 13 | Cable | 0.0075 | 0.1304 | 120.0672 | 2000 | 1850 | 1597 | 1850
KENG41 | WISD4* | 2018 | Addition | 0 | 5 | Cable | 0.002 | 0.0359 | 32.7456 | 2000 | 1850 | 1597 | 1850
KENG42 | SJOW41 | 2018 | Change | 0 | 6 | Cable | 0.0027 | 0.0477 | 43.6608 | 2000 | 1850 | 1597 | 1850
KENG42 | WIMB41 | 2018 | Addition | 0 | 13 | Cable | 0.0075 | 0.1304 | 120.0672 | 2000 | 1850 | 1597 | 1850
KENG42 | WISD4* | 2018 | Addition | 0 | 5 | Cable | 0.002 | 0.0359 | 32.7456 | 2000 | 1850 | 1597 | 1850
PELH41 | WYMO41 | 2018 | Change | 26.856 | 0 | OHL | 0.0291 | 0.4667 | 17.7225 | 2770 | 2562.25 | 2211.845 | 2562.25
PELH41 | WYMO41 | 2018 | Addition | 26.891 | 0 | OHL | 0.0292 | 0.4677 | 17.7269 | 3180 | 2941.5 | 2539.23 | 2941.5
SUND41 | WYMO41 | 2018 | Change | 18.156 | 0 | OHL | 0.0197 | 0.3152 | 11.9934 | 3050 | 2821.25 | 2435.425 | 2821.25
SUND42 | WYMO41 | 2018 | Addition | 17.986 | 0 | OHL | 0.0195 | 0.3128 | 11.8566 | 3180 | 2941.5 | 2539.23 | 2941.5
SWAN4* | BRITT* | 2018 | Addition | 17.145 | 0 | OHL | 0.0572 | 0.7166 | 4.7315 | 1900 | 1757.5 | 1517.15 | 1757.5
WISD2B | EALI21 | 2018 | Addition | 0 | 8.075 | Cable | 0.002 | 0.0229 | 10.13 | 665 | 615.125 | 531.0025 | 615.125
SJOW2A | WISD21 | 2018 | Removed | 0 | 7.399 | Cable | 0.0133 | 0.1628 | 80.4271 | 750 | 693.75 | 598.875 | 693.75
BAGB21 | SWAN4* | 2018 | Removed | 18.21 | 1.439 | Composite | 0.0625 | 0.7488 | 19.1165 | 1100 | 1017.5 | 878.35 | 1017.5
PELH41 | SUND42 | 2018 | Removed | 45.13 | 0 | OHL | 0.0487 | 0.752 | 31.2185 | 3180 | 2941.5 | 2539.23 | 2941.5
SJOW2B | WISD22 | 2018 | Removed | 0 | 7.399 | Cable | 0.0133 | 0.1628 | 80.4271 | 750 | 693.75 | 598.875 | 693.75
TILB4A | TILB41 | 2018 | Removed | 0.05808 | 0 | OHL | 0.0001 | 0.0012 | 0.033 | 3100 | 2867.5 | 2475.35 | 2867.5
TILB41 | TILB4B | 2018 | Removed | 0.0589 | 0 | OHL | 0.0001 | 0.0011 | 0.0353 | 3100 | 2867.5 | 2475.35 | 2867.5
WIMB21 | WISD2B | 2018 | Removed | 0 | 20.669 | Cable | 0.0413 | 0.4733 | 209.377 | 740 | 684.5 | 590.89 | 684.5
BAGB21 | MAGA21 | 2018 | Removed | 12.629 | 1.389 | Composite | 0.0435 | 0.5216 | 17.0509 | 1200 | 1110 | 958.2 | 1110
BICF41 | WMAR4* | 2020 | Addition | 14.35 | 0 | OHL | 0.0127 | 0.2465 | 9.6453 | 3190 | 2950.75 | 2547.215 | 2950.75
BICF42 | WMAR4* | 2020 | Addition | 14.35 | 0 | OHL | 0.0127 | 0.2465 | 9.6453 | 3160 | 2923 | 2523.26 | 2923
CANT42* | RICH4* | 2020 | Addition | 25 | 0 | OHL | 0.0399 | 0.4808 | 15.0331 | 1690 | 1563.25 | 1349.465 | 1563.25
DUNG41 | SELL41 | 2020 | Change | 25.387 | 0.415 | Composite | 0.0398 | 0.4893 | 30.1747 | 3100 | 2867.5 | 2475.35 | 2867.5
DUNG41 | SELW41 | 2020 | Change | 25.403 | 0.415 | Composite | 0.0398 | 0.4896 | 30.1843 | 3100 | 2867.5 | 2475.35 | 2867.5
HATL21 | TODP21 | 2020 | Change | 18.433 | 0 | OHL | 0.0713 | 0.7756 | 5.0477 | 1150 | 1063.75 | 918.275 | 1063.75
HIKP41 | HIKP41 | 2020 | Addition | 0 | 0 | Series Reactor | 0 | 2 | 0 | 2000 | 1850 | 1597 | 1850
KIBY41 | WASF41 | 2020 | Addition | 10.945 | 2 | Composite | 0.0199 | 0.2182 | 6.3427 | 2210 | 2044.25 | 1764.685 | 2044.25
KILL4* | KILL41 | 2020 | Addition | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 2000 | 1850 | 1597 | 1850
KINO41 | NFLE41 | 2020 | Change | 23.626 | 0 | OHL | 0.0249 | 0.4177 | 15.452 | 3100 | 2867.5 | 2475.35 | 2867.5
LACK41 | NORT41 | 2020 | Change | 22.443 | 0.25 | Composite | 0.038 | 0.4465 | 17.5688 | 3100 | 2867.5 | 2475.35 | 2867.5
NORT22 | SALH21 | 2020 | Change | 12.178 | 0 | OHL | 0.0431 | 0.5178 | 3.2966 | 1370 | 1267.25 | 1093.945 | 1267.25
NORT41 | OSBA41 | 2020 | Change | 83.839 | 0 | OHL | 0.1097 | 1.5842 | 51.2941 | 2810 | 2599.25 | 2243.785 | 2599.25
NORT41 | OSBA42 | 2020 | Change | 83.839 | 0 | OHL | 0.1097 | 1.5842 | 51.2941 | 2810 | 2599.25 | 2243.785 | 2599.25
PENT41 | TRAW41 | 2020 | Change | 45.1 | 6.308 | Composite | 0.0634 | 0.9563 | 131.5927 | 1130 | 1045.25 | 902.305 | 1045.25
PENT41 | TRAW41 | 2020 | Addition | 45.1 | 6.308 | Composite | 0.0634 | 0.956 | 174.1811 | 1600 | 1480 | 1277.6 | 1480
PEWO41 | WASF41 | 2020 | Addition | 8 | 2 | Composite | 0.0146 | 0.1596 | 4.6347 | 2210 | 2044.25 | 1764.685 | 2044.25
RICH4* | CANT42* | 2020 | Addition | 25 | 0 | OHL | 0.0399 | 0.4808 | 15.0331 | 1690 | 1563.25 | 1349.465 | 1563.25
SING41 | KINO41 | 2020 | Change | 17.685 | 0 | OHL | 0.0157 | 0.3038 | 11.8869 | 3820 | 3533.5 | 3050.27 | 3533.5
SPLN41 | WMAR4* | 2020 | Addition | 5.759 | 0 | OHL | 0.0064 | 0.1085 | 3.5417 | 3190 | 2950.75 | 2547.215 | 2950.75
WASF42 | KIBY42 | 2020 | Addition | 11.707 | 0 | OHL | 0.0213 | 0.2329 | 6.783 | 2210 | 2044.25 | 1764.685 | 2044.25
WASF42 | PEWO41 | 2020 | Addition | 8 | 0 | OHL | 0.0149 | 0.1593 | 4.6296 | 2210 | 2044.25 | 1764.685 | 2044.25
WMAR4* | SPLN41 | 2020 | Addition | 5.759 | 0 | OHL | 0.0064 | 0.1085 | 3.5417 | 3160 | 2923 | 2523.26 | 2923
WMAR4* | WALP41 | 2020 | Addition | 23.475 | 0 | OHL | 0.0208 | 0.4032 | 15.7777 | 3190 | 2950.75 | 2547.215 | 2950.75
WMAR4* | WALP41 | 2020 | Addition | 23.425 | 0 | OHL | 0.0208 | 0.4023 | 15.7443 | 3190 | 2950.75 | 2547.215 | 2950.75
KIBY21 | WASF22 | 2020 | Removed | 10.978 | 0 | OHL | 0.0415 | 0.4491 | 3.0984 | 1520 | 1406 | 1213.72 | 1406
CARR43 | DAIN41 | 2020 | Removed | 2.063 | 0 | OHL | 0.0032 | 0.0397 | 1.2352 | 750 | 693.75 | 598.875 | 693.75
BICF41 | WALP41 | 2020 | Removed | 37.775 | 0 | OHL | 0.0335 | 0.6488 | 25.3895 | 3190 | 2950.75 | 2547.215 | 2950.75
PEWO22 | WASF22 | 2020 | Removed | 23.521 | 0 | OHL | 0.0889 | 0.9623 | 6.6386 | 1520 | 1406 | 1213.72 | 1406
CARR42 | DAIN41 | 2020 | Removed | 2.036 | 0 | OHL | 0.0037 | 0.0405 | 1.1791 | 750 | 693.75 | 598.875 | 693.75
SPLN41 | WALP41 | 2020 | Removed | 29.234 | 0 | OHL | 0.0272 | 0.5117 | 19.3195 | 3190 | 2950.75 | 2547.215 | 2950.75
KIBY22 | WASF21 | 2020 | Removed | 10.945 | 0 | OHL | 0.0414 | 0.4478 | 3.0891 | 1520 | 1406 | 1213.72 | 1406
LISD21 | LISD2* | 2020 | Removed | 0 | 0 | Series Reactor | 0.0173 | 1.387 | 0 | 750 | 693.75 | 598.875 | 693.75
PEWO21 | WASF21 | 2020 | Removed | 23.481 | 0 | OHL | 0.0887 | 0.9606 | 6.6274 | 1520 | 1406 | 1213.72 | 1406
BICF42 | SPLN41 | 2020 | Removed | 20.109 | 0 | OHL | 0.0191 | 0.355 | 13.187 | 3160 | 2923 | 2523.26 | 2923
BRAI4A | BRFO41 | 2023 | Change | 48.267 | 0 | OHL | 0.0428 | 0.829 | 32.4419 | 3820 | 3533.5 | 3050.27 | 3533.5
BRAI4A | RAYL41 | 2023 | Change | 32.993 | 0 | OHL | 0.0292 | 0.5667 | 22.176 | 3820 | 3533.5 | 3050.27 | 3533.5
BRAI4B | RAYL41 | 2023 | Change | 33.032 | 0 | OHL | 0.0293 | 0.5674 | 22.2022 | 3820 | 3533.5 | 3050.27 | 3533.5
BRED21 | SMAN21 | 2023 | Change | 10.004 | 6.234 | parallel Composite | 0.048 | 0.4624 | 34.8686 | 1500 | 1387.5 | 1197.75 | 1387.5
BRFO41 | BRAI4B | 2023 | Addition | 48.267 | 0 | OHL | 0.0428 | 0.829 | 32.4419 | 3820 | 3533.5 | 3050.27 | 3533.5
BRFO41 | NORM41 | 2023 | Change | 61.576 | 0.1 | Composite | 0.0547 | 1.0587 | 43.3879 | 3820 | 3533.5 | 3050.27 | 3533.5
BRFO41 | NORM41 | 2023 | Change | 61.576 | 0.1 | Composite | 0.0547 | 1.0587 | 43.3879 | 3820 | 3533.5 | 3050.27 | 3533.5
BRFO41 | PELH41 | 2023 | Addition | 69.301 | 0 | OHL | 0.0701 | 1.1997 | 46.0176 | 3820 | 3533.5 | 3050.27 | 3533.5
BRFO42 | PELH41 | 2023 | Change | 69.301 | 0 | OHL | 0.0701 | 1.1997 | 46.0176 | 2780 | 2571.5 | 2219.83 | 2571.5
BRIM4C | HACK41 | 2023 | Addition | 13.209 | 0.527 | Composite | 0.0209 | 0.2597 | 13.6792 | 1385 | 1281.125 | 1105.9225 | 1281.125
BRIM4C | WALX41 | 2023 | Addition | 5.97 | 0 | OHL | 0.0093 | 0.1145 | 3.5827 | 1590 | 1470.75 | 1269.615 | 1470.75
BRIM4D | HACK41 | 2023 | Addition | 13.209 | 0.676 | Composite | 0.021 | 0.2614 | 15.3056 | 1385 | 1281.125 | 1105.9225 | 1281.125
BRIM4D | WALX41 | 2023 | Addition | 5.97 | 0 | OHL | 0.0093 | 0.1145 | 3.5827 | 1590 | 1470.75 | 1269.615 | 1470.75
CARR41 | DAINT* | 2023 | Addition | 3.352 | 0 | OHL | 0.0059 | 0.0653 | 1.9782 | 3100 | 2867.5 | 2475.35 | 2867.5
CELL41 | DAINT* | 2023 | Addition | 53.412 | 2.31 | parallel Composite | 0.0843 | 1.0314 | 76.88 | 2510 | 2321.75 | 2004.235 | 2321.75
CELL41 | DRAK41 | 2023 | Change | 45.012 | 0 | OHL | 0.0703 | 0.8668 | 26.8964 | 2180 | 2016.5 | 1740.73 | 2016.5
CELL41 | DRAK41 | 2023 | Change | 45.704 | 0 | OHL | 0.0714 | 0.8801 | 27.3086 | 2180 | 2016.5 | 1740.73 | 2016.5
CONQ41 | DAINT* | 2023 | Addition | 60.331 | 0 | OHL | 0.094 | 1.1575 | 36.2038 | 2890 | 2673.25 | 2307.665 | 2673.25
CONQ41 | GWYN4* | 2023 | Change | 30.217 | 0 | OHL | 0.0268 | 0.519 | 20.3102 | 3210 | 2969.25 | 2563.185 | 2969.25
CONQ41 | GWYN4* | 2023 | Change | 30.217 | 0 | OHL | 0.0268 | 0.519 | 20.3102 | 3210 | 2969.25 | 2563.185 | 2969.25
COR2 1 | COSO41 | 2023 | Addition | 0 | 1.2 | Cable | 0.0008 | 0.0132 | 24 | 1500 | 1387.5 | 1197.75 | 1387.5
COR2 1 | COSO41 | 2023 | Addition | 0 | 1.2 | Cable | 0.0008 | 0.0132 | 24 | 1500 | 1387.5 | 1197.75 | 1387.5
DAINT* | CARR41 | 2023 | Addition | 2.545 | 0 | OHL | 0.004 | 0.0488 | 1.5263 | 2170 | 2007.25 | 1732.745 | 2007.25
DAINT* | CONQ41 | 2023 | Addition | 60.294 | 0 | OHL | 0.0938 | 1.1562 | 36.2009 | 2890 | 2673.25 | 2307.665 | 2673.25
DAINT* | MACC41 | 2023 | Addition | 33.593 | 2.83 | parallel Composite | 0.054 | 0.656 | 75.0798 | 2400 | 2220 | 1916.4 | 2220
DUNG41 | LYDD41 | 2023 | Addition | 5.249 | 0 | OHL | 0.0095 | 0.1044 | 3.042 | 2010 | 1859.25 | 1604.985 | 1859.25
DUNG41 | LYDD41 | 2023 | Addition | 5.598 | 0 | OHL | 0.0102 | 0.1114 | 3.2443 | 2010 | 1859.25 | 1604.985 | 1859.25
GWYN4* | PENT41 | 2023 | Change | 49.211 | 0 | OHL | 0.0436 | 0.8452 | 33.0768 | 2780 | 2571.5 | 2219.83 | 2571.5
GWYN4* | PENT41 | 2023 | Change | 49.211 | 0 | OHL | 0.0436 | 0.8452 | 33.0768 | 3210 | 2969.25 | 2563.185 | 2969.25
HATL21 | HARM21 | 2023 | Change | 13.983 | 0 | OHL | 0.0476 | 0.5708 | 3.9608 | 1090 | 1008.25 | 870.365 | 1008.25
HAWP21 | HATL21 | 2023 | Addition | 31.443 | 0 | OHL | 0.1066 | 1.2811 | 8.9228 | 476.314 | 440.5904 | 380.3367 | 440.5904
HAWP21 | OFFE21 | 2023 | Change | 9.514 | 0 | OHL | 0.0379 | 0.3948 | 2.6412 | 1090 | 1008.25 | 870.365 | 1008.25
HAWP41 | NORT41 | 2023 | Change | 30.157 | 0 | OHL | 0.0327 | 0.5245 | 19.8799 | 1000 | 925 | 798.5 | 925
HIKP41 | PURI4* | 2023 | Addition | 15 | 0 | OHL | 0.0234 | 0.2878 | 9.0015 | 3100 | 2867.5 | 2475.35 | 2867.5
HIKP41 | PURI4* | 2023 | Addition | 15 | 0 | OHL | 0.0234 | 0.2878 | 9.0015 | 3100 | 2867.5 | 2475.35 | 2867.5
HIKP41 | TAUN41 | 2023 | Addition | 27.644 | 0 | OHL | 0.0503 | 0.55 | 16.0209 | 2210 | 2044.25 | 1764.685 | 2044.25
HIKP41 | TAUN42 | 2023 | Addition | 27.657 | 0 | OHL | 0.0503 | 0.5503 | 16.0284 | 2210 | 2044.25 | 1764.685 | 2044.25
HINP41 | HIKP41 | 2023 | Addition | 1 | 0 | OHL | 0.0018 | 0.0199 | 0.5795 | 2210 | 2044.25 | 1764.685 | 2044.25
HINP41 | HIKP41 | 2023 | Addition | 1 | 0 | OHL | 0.0018 | 0.0199 | 0.5795 | 2210 | 2044.25 | 1764.685 | 2044.25
HINP41 | SAFO41 | 2023 | Addition | 24.54 | 8.15 | Composite | 0.0376 | 0.5627 | 203.1782 | 3070 | 2839.75 | 2451.395 | 2839.75
HINP41 | SEAB41 | 2023 | Addition | 53.385 | 8.15 | Composite | 0.0697 | 1.1063 | 220.9169 | 3100 | 2867.5 | 2475.35 | 2867.5
INDQ41 | LAND41 | 2023 | Change | 49.565 | 0 | OHL | 0.0946 | 0.9615 | 29.5135 | 1930 | 1785.25 | 1541.105 | 1785.25
INDQ41 | LAND42 | 2023 | Change | 49.565 | 0 | OHL | 0.0946 | 0.9615 | 29.5135 | 1930 | 1785.25 | 1541.105 | 1785.25
KEMS41 | LOFI4A | 2023 | Change | 38.035 | 0 | OHL | 0.0589 | 0.7286 | 22.8653 | 1930 | 1785.25 | 1541.105 | 1785.25
KEMS41 | LOFI4B | 2023 | Change | 37.572 | 0 | OHL | 0.0585 | 0.7207 | 22.5541 | 1930 | 1785.25 | 1541.105 | 1785.25
LITT41 | LOFI4A | 2023 | Change | 8.152 | 0 | OHL | 0.0072 | 0.1378 | 5.5754 | 1390 | 1285.75 | 1109.915 | 1285.75
LITT41 | LOFI4B | 2023 | Change | 8.152 | 0 | OHL | 0.0072 | 0.1378 | 5.5754 | 1390 | 1285.75 | 1109.915 | 1285.75
LITT41 | WTHU4E | 2023 | Change | 1.801 | 1.853 | Composite | 0.0041 | 0.0566 | 21.302 | 1940 | 1794.5 | 1549.09 | 1794.5
LOFI4A | ROWD41 | 2023 | Change | 26.714 | 0 | OHL | 0.0416 | 0.5125 | 16.031 | 1590 | 1470.75 | 1269.615 | 1470.75
LOFI4B | ROWD41 | 2023 | Change | 26.714 | 0 | OHL | 0.0416 | 0.5125 | 16.031 | 1590 | 1470.75 | 1269.615 | 1470.75
LYDD41 | DUNG41 | 2023 | Addition | 5.598 | 0 | OHL | 0.0102 | 0.1114 | 3.2443 | 2010 | 1859.25 | 1604.985 | 1859.25
LYDD41 | DUNG41 | 2023 | Addition | 5.249 | 0 | OHL | 0.0095 | 0.1044 | 3.042 | 2010 | 1859.25 | 1604.985 | 1859.25
LYDD41 | NINF41 | 2023 | Addition | 35.55 | 0 | OHL | 0.0315 | 0.6106 | 23.8947 | 3820 | 3533.5 | 3050.27 | 3533.5
LYDD41 | NINF41 | 2023 | Addition | 35.55 | 0 | OHL | 0.0315 | 0.6106 | 23.8947 | 3820 | 3533.5 | 3050.27 | 3533.5
LYDD41 | ROWD41 | 2023 | Addition | 90 | 5 | Composite | 0.1012 | 1.6204 | 159.3291 | 2600 | 2405 | 2076.1 | 2405
MELK41 | PURI4* | 2023 | Addition | 78.5 | 0 | OHL | 0.1223 | 1.5103 | 46.977 | 3100 | 2867.5 | 2475.35 | 2867.5
MELK41 | PURI4* | 2023 | Addition | 78.5 | 0 | OHL | 0.1223 | 1.5103 | 46.977 | 3100 | 2867.5 | 2475.35 | 2867.5
NORT41 | HAWP41 | 2023 | Addition | 30.157 | 0 | OHL | 0.0327 | 0.5245 | 19.8799 | 645.0157 | 596.6396 | 515.0451 | 596.6396
NECT4A | KINL41 | 2023 | Addition | 30.347 | 0 | OHL | 0.0269 | 0.5209 | 20.404 | 2520 | 2331 | 2012.22 | 2331
OFFE21 | WBOL21 | 2023 | Change | 8.207 | 0 | OHL | 0.0327 | 0.3406 | 2.2784 | 1090 | 1008.25 | 870.365 | 1008.25
PELH41 | RYEH4A | 2023 | Change | 23.015 | 0 | OHL | 0.0359 | 0.4657 | 13.0582 | 3100 | 2867.5 | 2475.35 | 2867.5
PELH41 | RYEH4B | 2023 | Change | 23.439 | 0 | OHL | 0.0366 | 0.4743 | 13.2981 | 3100 | 2867.5 | 2475.35 | 2867.5
PENT41 | TRAW41 | 2023 | Change | 45.1 | 12.616 | parallel Composite | 0.0429 | 0.8075 | 325.4248 | 3210 | 2969.25 | 2563.185 | 2969.25
PENT41 | TRAW41 | 2023 | Change | 45.1 | 12.616 | parallel Composite | 0.0439 | 0.823 | 324.8448 | 3210 | 2969.25 | 2563.185 | 2969.25
PURI4* | BRWA4* | 2023 | Addition | 4 | 0 | OHL | 0.0062 | 0.0767 | 2.4004 | 3100 | 2867.5 | 2475.35 | 2867.5
PURI4* | BRWA4* | 2023 | Addition | 4 | 0 | OHL | 0.0062 | 0.0767 | 2.4004 | 3100 | 2867.5 | 2475.35 | 2867.5
ROWD41 | LYDD41 | 2023 | Addition | 90 | 5 | Composite | 0.1012 | 1.6204 | 159.3291 | 2600 | 2405 | 2076.1 | 2405
RYEH41 | RYEH4B | 2023 | Change | 0.137 | 0 | OHL | 0.0002 | 0.0028 | 0.0777 | 3100 | 2867.5 | 2475.35 | 2867.5
RYEH41 | WALX41 | 2023 | Change | 5.324 | 0 | OHL | 0.0083 | 0.1077 | 3.0209 | 3100 | 2867.5 | 2475.35 | 2867.5
RYEH4A | WALX41 | 2023 | Change | 5.461 | 0 | OHL | 0.0085 | 0.1105 | 3.0987 | 3100 | 2867.5 | 2475.35 | 2867.5
SAFO41 | SEAB41 | 2023 | Addition | 28.845 | 0 | OHL | 0.0322 | 0.5436 | 17.7387 | 3070 | 2839.75 | 2451.395 | 2839.75
SELL41 | LYDD41 | 2023 | Addition | 19.805 | 0 | OHL | 0.0308 | 0.38 | 11.8853 | 2200 | 2035 | 1756.7 | 2035
SELL41 | LYDD41 | 2023 | Addition | 19.805 | 0 | OHL | 0.0308 | 0.38 | 11.8853 | 2200 | 2035 | 1756.7 | 2035
SSHI21 | WBOL21 | 2023 | Addition | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 1090 | 1008.25 | 870.365 | 1008.25
TYNE21 | SSHI21 | 2023 | Addition | 6.863 | 0 | OHL | 0.0303 | 0.2915 | 1.8625 | 1090 | 1008.25 | 870.365 | 1008.25
WALP41 | KINL41 | 2023 | Addition | 44.319 | 0 | OHL | 0.0393 | 0.7609 | 29.7952 | 2520 | 2331 | 2012.22 | 2331
WBOL21 | HAWP21 | 2023 | Addition | 17.721 | 0 | OHL | 0.0705 | 0.7355 | 4.9196 | 443.4483 | 410.1897 | 354.0935 | 410.1897
WYLF41 | PENT41 | 2023 | Addition | 33.74 | 3 | parallel Composite | 0.0446 | 0.6576 | 90.4415 | 2780 | 2571.5 | 2219.83 | 2571.5
WYLF41 | PENT41 | 2023 | Addition | 33.74 | 3 | parallel Composite | 0.0446 | 0.6576 | 90.4415 | 2780 | 2571.5 | 2219.83 | 2571.5
DUNG41 | NINF41 | 2023 | Removed | 44.056 | 0 | OHL | 0.0391 | 0.7567 | 29.6111 | 3070 | 2839.75 | 2451.395 | 2839.75
CARR41 | DAIN41 | 2023 | Removed | 3.352 | 0 | OHL | 0.0059 | 0.0653 | 1.9782 | 3100 | 2867.5 | 2475.35 | 2867.5
BRIM2C | TOTT22 | 2023 | Removed | 7.455 | 0.235 | Composite | 0.0344 | 0.3223 | 4.5788 | 1090 | 1008.25 | 870.365 | 1008.25
BRIM2D | TOTT23 | 2023 | Removed | 7.455 | 0.384 | Composite | 0.0347 | 0.3264 | 6.1984 | 1090 | 1008.25 | 870.365 | 1008.25
BRIM2C | WALX21 | 2023 | Removed | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1090 | 1008.25 | 870.365 | 1008.25
DAIN41 | MACC41 | 2023 | Removed | 33.593 | 2.83 | Composite | 0.054 | 0.656 | 75.0798 | 2400 | 2220 | 1916.4 | 2220
DUNG41 | SELL41 | 2023 | Removed | 25.387 | 0.415 | Composite | 0.0398 | 0.4893 | 30.1747 | 3100 | 2867.5 | 2475.35 | 2867.5
BRIM2D | WALX21 | 2023 | Removed | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1090 | 1008.25 | 870.365 | 1008.25
HINP41 | TAUN41 | 2023 | Removed | 26.644 | 0 | OHL | 0.0485 | 0.5301 | 15.4408 | 2210 | 2044.25 | 1764.685 | 2044.25
HINP41 | MELK41 | 2023 | Removed | 86.439 | 0 | OHL | 0.1572 | 1.7198 | 50.0946 | 2010 | 1859.25 | 1604.985 | 1859.25
TYNE21 | WBOL21 | 2023 | Removed | 11.399 | 0 | OHL | 0.051 | 0.4835 | 3.093 | 1090 | 1008.25 | 870.365 | 1008.25
HAWP21 | NORT21 | 2023 | Removed | 30.238 | 0.459 | Composite | 0.0719 | 1.1367 | 14.2369 | 910 | 841.75 | 726.635 | 841.75
HACK21 | TOTT21 | 2023 | Removed | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 955 | 883.375 | 762.5675 | 883.375
HINP41 | TAUN42 | 2023 | Removed | 26.657 | 0 | OHL | 0.0485 | 0.5304 | 15.4483 | 2210 | 2044.25 | 1764.685 | 2044.25
Necton | WALP41 | 2023 | Removed | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3820 | 3533.5 | 3050.27 | 3533.5
HACK22 | TOTT22 | 2023 | Removed | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 955 | 883.375 | 762.5675 | 883.375
DUNG41 | SELW41 | 2023 | Removed | 25.403 | 0.415 | Composite | 0.0398 | 0.4896 | 30.1843 | 3100 | 2867.5 | 2475.35 | 2867.5
DAIN41 | CARR41 | 2023 | Removed | 2.545 | 0 | OHL | 0.004 | 0.0488 | 1.5263 | 2170 | 2007.25 | 1732.745 | 2007.25
CONQ41 | DAIN41 | 2023 | Removed | 60.331 | 0 | OHL | 0.094 | 1.1575 | 36.2038 | 2890 | 2673.25 | 2307.665 | 2673.25
HINP21 | BRWA2B | 2023 | Removed | 17.867 | 0.68 | Composite | 0.0828 | 0.7752 | 12.2388 | 240 | 222 | 191.64 | 222
HINP22 | BRWA2A | 2023 | Removed | 17.867 | 0.61 | Composite | 0.0827 | 0.7732 | 11.4779 | 240 | 222 | 191.64 | 222
HINP41 | MELK41 | 2023 | Removed | 86.448 | 0 | OHL | 0.1573 | 1.72 | 50.0998 | 2010 | 1859.25 | 1604.985 | 1859.25
DUNG41 | NINF41 | 2023 | Removed | 44.081 | 0 | OHL | 0.0391 | 0.7571 | 29.6278 | 3070 | 2839.75 | 2451.395 | 2839.75
HATL21 | WBOL21 | 2023 | Removed | 49.164 | 0 | OHL | 0.1876 | 2.0311 | 13.7303 | 1090 | 1008.25 | 870.365 | 1008.25
DAIN41 | CONQ41 | 2023 | Removed | 60.294 | 0 | OHL | 0.0938 | 1.1562 | 36.2009 | 2890 | 2673.25 | 2307.665 | 2673.25
CELL41 | DAIN41 | 2023 | Removed | 53.412 | 2.31 | Composite | 0.0843 | 1.0314 | 76.88 | 2510 | 2321.75 | 2004.235 | 2321.75
BRAI4B | PELH41 | 2023 | Removed | 65.942 | 0 | OHL | 0.0716 | 1.1469 | 43.4688 | 2780 | 2571.5 | 2219.83 | 2571.5

## B-2-2d
Table B.2.2d - Offshore Transmission Circuit Changes 2015/16 to 2023/24 | [11 empty] | Back To Menu
Node 1 | Node 2 | Year | Status | Voltage (kV) | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA)
WAEN8* | WAEN8* | 2015 | Addition | 150 | 0 | 50 | Cable | 1.3333 | 2.6667 | 74.2201 | 180
WAEN8* | WAEN8* | 2015 | Addition | 150 | 0 | 50 | Cable | 1.3333 | 2.6667 | 74.2201 | 180
WAEN8* | WAEN8* | 2015 | Addition | 150 | 0 | 50 | Cable | 1.3333 | 2.6667 | 74.2201 | 180
WAEN8* | WAEN8* | 2015 | Addition | 150 | 0 | 50 | Cable | 1.3333 | 2.6667 | 74.2201 | 180
GAOF1* | GAOF1* | 2017 | Addition | 132 | 0 | 17 | Cable | 0.36 | 1.07 | 0.6224 | 300
GAON1* | GAOF1* | 2017 | Addition | 132 | 0 | 45 | Cable | 1.02 | 3.0599 | 1.776 | 300
GAON1* | GAOF1* | 2017 | Addition | 132 | 0 | 45 | Cable | 1.02 | 3.0599 | 1.776 | 300
GAON1* | GAOF1* | 2017 | Addition | 132 | 0 | 45 | Cable | 0 | 0 | 0 | 300
BUBW8* | BUBW8* | 2018 | Addition | 220 | 0 | 10.6 | Cable | 0.0701 | 0.311 | 25.9726 | 246
BUBW8* | BUBW8* | 2018 | Addition | 220 | 0 | 21.5 | Cable | 0.2265 | 0.5331 | 62.1134 | 246
WALP1* | DOCS1* | 2020 | Addition | 132 | 0 | 60 | Cable | 0.546 | 6.018 | 134.094 | 1000
WALP1* | DOCS1* | 2020 | Addition | 132 | 0 | 60 | Cable | 0.546 | 6.018 | 134.094 | 1000
WALP1* | RACB1* | 2020 | Addition | 132 | 0 | 60 | Cable | 0.546 | 6.018 | 134.094 | 1000
WALP1* | RACB1* | 2020 | Addition | 132 | 0 | 60 | Cable | 0.546 | 6.018 | 134.094 | 1000
HORN4* | KILL41 | 2020 | Addition | 220 | 0 | 100 | HVDC | 0 | 0.0002 | 0 | 2500
DOGG4* | CREB41 | 2023 | Addition | 220 | 0 | 100 | HVDC | 0 | 0.0001 | 0 | 2500
HORN4* | KILL41 | 2023 | Addition | 220 | 0 | 100 | HVDC | 0 | 0.0002 | 0 | 2500

## B-3-1a
Table B.3.1a - SHE Transmission Transformers 2014/15 | [5 empty] | Back To Menu
Node 1 | Node 2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
ABNE1Q | ABNE3- | 1.05 | 27.98 | 0 | 60
ABNE1R | ABNE3- | 1.05 | 28.5 | 0 | 60
ALNE1Q | ALNE3J | 0.365 | 26 | 0 | 120
ALNE1R | ALNE3J | 0.365 | 26 | 0 | 120
ANSU1- | ANSU3- | 0.817 | 27.121 | 0 | 45
ARBR1Q | ARBR3- | 0.7 | 28.29 | 0 | 45
ARBR1R | ARBR3- | 0.7 | 28.29 | 0 | 45
ARDK1- | ARDK3K | 0.807 | 24.876 | 0 | 45
ARMO1J | ARMO3- | 0.7 | 21 | 0 | 60
BEAU1J | BEAU1P | 0.177 | 3.6 | 0 | 150
BEAU1J | BEAU3- | 1.04 | 27.7301 | 0 | 45
BEAU1K | BEAU1Q | 0.177 | 3.6 | 0 | 150
BEAU1K | BEAU3- | 1.04 | 27.7301 | 0 | 45
BEAU2J | BEAU1J | 0.6786 | 12.2312 | -0.0009 | 120
BEAU2J | BEAU1J | 0.6786 | 12.1644 | -0.0009 | 120
BEAU2K | BEAU1K | 0.6786 | 12.1895 | -0.0009 | 120
BEAU4- | BEAU2J | 0.018 | 1.576 | -0.09 | 1200
BEAU4- | BEAU2K | 0.018 | 1.576 | -0.09 | 1200
BERB2Q | BERB3- | 0.42 | 20 | 0 | 120
BOAG1Q | BOAG3- | 0.611 | 24.993 | 0 | 60
BOAG1R | BOAG3- | 0.605 | 24.826 | 0 | 60
BRAC1Q | BRAC3- | 0.9 | 27.85 | 0 | 60
BRAC1R | BRAC3- | 0.9 | 27.6 | 0 | 60
BRID1Q | BRID3- | 0.633 | 28.76 | 0 | 60
BRID1R | BRID3- | 0.637 | 28.943 | 0 | 60
BROA1Q | BROA3- | 1.19 | 38.9998 | 0 | 30
BROR1- | BROR3- | 1.82 | 67.13 | 0 | 15
BUMU1Q | BUMU3- | 0.407 | 26.975 | 0 | 90
BUMU1R | BUMU3- | 0.407 | 26.975 | 0 | 90
CAAD1Q | CAAD3- | 1.04 | 27.65 | 0 | 60
CAAD1Q | CAAD3J | 0.5 | 25 | 0 | 90
CAAD1R | CAAD3- | 1.04 | 27.65 | 0 | 60
CAAD1R | CAAD3J | 0.5 | 25 | 0 | 90
CASS1Q | CASS3- | 1.518 | 39.8711 | 0 | 30
CHAR1- | CHAR3- | 0.407 | 26.975 | 0 | 90
CHAR1R | CHAR3- | 0.407 | 26.975 | 0 | 90
CLAY1Q | CLAY3- | 0.87 | 24.92 | 0 | 60
CLAY1R | CLAY3- | 0.87 | 24.92 | 0 | 60
CORI1J | CORI3- | 0.5 | 25 | 0 | 90
COUA1Q | COUA3- | 1.05 | 27.89 | 0 | 45
COUA1R | COUA3- | 1.05 | 27.89 | 0 | 45
CRAI1- | CRAI3- | 1.78 | 29.9 | 0 | 30
CRAI1Q | CRAI3- | 1.75 | 30.27 | 0 | 30
DAAS2- | DAAS3- | 0.417 | 20 | 0 | 120
DOUN1- | DOUN3- | 0.4676 | 26.1 | 0 | 90
DOUN1- | DOUN3- | 0.434 | 25.95 | 0 | 90
DOUN2- | DOUN1- | 0.2112 | 7.7054 | -0.0006 | 240
DOUN2- | DOUN1- | 0.2237 | 7.9135 | -0.0006 | 240
DUBE1Q | DUBE3- | 1.52 | 39.4 | 0 | 30
DUDH1Q | DUDH3- | 0.78 | 24.93 | 0 | 60
DUDH1R | DUDH3- | 0.78 | 23.93 | 0 | 60
DUGR1Q | DUGR3- | 0.7 | 21 | 0 | 60
DYCE1Q | DYCE3- | 1.35 | 26.67 | 0 | 60
DYCE1R | DYCE3- | 1.36 | 26.7299 | 0 | 60
EDIN1- | EDIN3- | 0.558 | 16.991 | 0 | 60
ELGI1Q | ELGI3- | 0.63 | 27.98 | 0 | 90
ELGI1R | ELGI3- | 0.63 | 27.78 | 0 | 90
ERRO1J | ERRO1A | 0.04 | 1.942 | 0 | 240
ERRO1K | ERRO1B | 0.04 | 1.942 | 0 | 240
ERRO1T | ERRO1J | 0.068 | 3.73 | 0 | 150
FAAR1Q | FAAR3J | 0.9 | 28.34 | 0 | 90
FAAR1R | FAAR3K | 0.9 | 28.34 | 0 | 90
FASN2- | FASN3- | 0.42 | 20 | 0 | 120
FASN2- | FASN3- | 0.42 | 20 | 0 | 120
FAUG1Q | FAUG3- | 2.23 | 64.33 | 0 | 15
FAUG2- | FAUG1- | 0.2629 | 7.7038 | -0.0005 | 240
FAUG2- | FAUG1- | 0.2629 | 7.7038 | -0.0005 | 240
FAUG4- | FAUG1- | 0.2149 | 8.0138 | -0.013 | 240
FERO1- | FERO3- | 0.3697 | 10.5 | 0 | 90
FETT1- | FETT3S | 0.6 | 20 | 0 | 120
FETT2R | FETT1- | 0.2217 | 4.3026 | -0.0071 | 240
FIDD1Q | FIDD3- | 0.4567 | 26.23 | 0 | 90
FIDD1R | FIDD1B | 0.11 | 4.11 | 0 | 150
FIDD1R | FIDD3- | 0.4562 | 26.084 | 0 | 90
FRAS1Q | FRAS3- | 0.642 | 26.9039 | 0 | 45
FRAS1R | FRAS3- | 0.642 | 26.9039 | 0 | 45
FWIL1Q | FWIL3- | 0.88 | 27.33 | 0 | 60
FWIL1R | FWIL3- | 0.88 | 27.67 | 0 | 60
GLAG1Q | GLAG3J | 0.82 | 19.3299 | 0 | 60
GLAG1R | GLAG3K | 0.82 | 19.6 | 0 | 60
GLFA1- | GLFA3- | 1.111 | 28 | 0 | 90
GORW2- | GORW3- | 0.258 | 20.06 | 0 | 120
GRIF1S | GRIF36 | 0.248 | 16.298 | 0 | 120
GRIF1T | GRIF38 | 0.247 | 16.248 | 0 | 120
INNE1J | INNE3- | 0.89 | 27.87 | 0 | 60
INNE1K | INNE3- | 0.9 | 28 | 0 | 60
INNE1L | INNE3- | 0.427 | 26.774 | 0 | 90
INVB2A | INVR1- | 0.217 | 4.2737 | -0.0006 | 240
INVB2B | INVR1- | 0.2164 | 4.257 | -0.0066 | 240
KEIT1- | KEIT3- | 0.54 | 27.778 | 0 | 90
KEIT1- | KEIT3- | 0.54 | 27.778 | 0 | 90
KEIT1- | KEITH3A | 0.4281 | 25.8965 | 0 | 90
KEIT1- | KEITH3A | 0.499 | 24.995 | 0 | 90
KEIT2Q | KEIT1- | 0.2735 | 8.6123 | -0.0007 | 240
KEIT2R | KEIT1- | 0.3328 | 8.9105 | -0.0383 | 240
KIIN1- | KIIN3- | 0.772 | 24.8769 | 0 | 45
KIIN1- | KIIN3- | 0.769 | 24.5211 | 0 | 45
KILO1- | KILO3- | 0.88 | 27.7801 | 0 | 45
KINT1- | KINT3- | 1.04 | 27.65 | 0 | 60
KINT1- | KINT3- | 0.78 | 25 | 0 | 60
KINT1- | KINT3- | 0.456 | 26.107 | 0 | 90
KINT2J | KINT1- | 0.3771 | 10.1929 | -0.018 | 240
KINT2K | KINT1- | 0.3751 | 10.2314 | -0.0147 | 240
KINT2K | KINT1- | 0.6786 | 12.1477 | -0.0013 | 240
KNOC2J | KNOC1J | 0.2216 | 4.311 | -0.0076 | 240
KNOC2K | KNOC1J | 0.2205 | 4.3319 | -0.0006 | 240
LAIR1Q | LAIR3- | 0.425 | 24.674 | 0 | 90
LUNA1Q | LUNA3- | 0.435 | 25.018 | 0 | 90
LUNA1R | LUNA3- | 0.429 | 25.741 | 0 | 90
LYND1Q | LYND3- | 0.78 | 24.3 | 0 | 60
LYND1R | LYND3- | 0.78 | 24.73 | 0 | 60
MACD1Q | MACD3- | 0.83 | 18.89 | 0 | 90
MACD1R | MACD3- | 0.83 | 18.89 | 0 | 90
MILC1R | MILC3- | 0.78 | 24.8299 | 0 | 60
MILC1S | MILC3- | 0.88 | 28.1301 | 0 | 60
MILW1Q | MILW3- | 0.439 | 24.896 | 0 | 90
MYBS1Q | MYBS3J | 0.895 | 23.9169 | 0 | 60
MYBS1R | MYBS3J | 1.99 | 32.87 | 0 | 30
MYBS1R | MYBS3J | 1.636 | 33.73 | 0 | 30
MYBS1S | MYBS3K | 0.3837 | 24.98 | 0 | 120
MYBS1T | MYBS3K | 0.3837 | 24.98 | 0 | 120
NAIR1Q | NAIR3- | 1.06 | 28.6 | 0 | 60
NAIR1R | NAIR3- | 1.05 | 28.6001 | 0 | 60
NANT1Q | NANT3- | 2.857 | 45.714 | 0 | 35
ORRI1Q | ORRI3- | 0.564 | 16.824 | 0 | 60
PEHE2Q | PEHE1- | 0.4842 | 9.9549 | -0.0177 | 240
PEHE2R | PEHE1- | 0.3422 | 8.8892 | -0.0359 | 240
PEHERSV1 | PEHE1- | 0.2649 | 9.2254 | -0.0005 | 240
PEHG1Q | PEHG3- | 1.05 | 28.53 | 0 | 45
PEHG1R | PEHG3- | 1.05 | 28.3999 | 0 | 45
PERS1Q | PERS3- | 0.407 | 26.975 | 0 | 90
PERS1R | PERS3- | 0.407 | 26.975 | 0 | 90
PERS2Q | PERS1Q | 0.3363 | 8.9062 | -0.0412 | 240
PERS2R | PERS1R | 0.3342 | 8.8645 | -0.0419 | 240
PORA1Q | PORA3- | 1.803 | 29.812 | 0 | 30
PORA1R | PORA3- | 1.803 | 29.812 | 0 | 30
REDM1Q | REDM3- | 0.91 | 27 | 0 | 60
REDM1R | REDM3- | 0.9 | 27.83 | 0 | 60
SHIN1- | SHIN3- | 0.425 | 26.05 | 0 | 90
SHIN1- | SHIN3- | 0.437 | 26.22 | 0 | 90
STRB2- | STRB3W | 0.251 | 19.873 | 0 | 120
STRI1Q | STRI3- | 0.407 | 26.975 | 0 | 90
STRI1R | STRI3- | 0.407 | 26.975 | 0 | 90
TARL1Q | TARL3- | 2.42 | 41 | 0 | 30
TARL1R | TARL3- | 2.13 | 38.5298 | 0 | 30
TAYN1Q | TAYN3- | 0.315 | 28.7869 | 0 | 90
TAYN1R | TAYN3- | 0.315 | 28.7869 | 0 | 90
TEAL2J | TEAL1- | 0.5506 | 11.7649 | -0.0008 | 180
TEAL2K | TEAL1- | 0.2564 | 11.7305 | -0.0131 | 180
TEAL2K | TEAL1- | 0.5506 | 11.8761 | -0.0008 | 180
THSO1Q | THSO3- | 0.87 | 29.03 | 0 | 60
THSO1R | THSO3- | 0.733 | 23.37 | 0 | 60
TUMM2J | TUMM1J | 0.2649 | 9.2254 | -0.0005 | 240
TUMM2K | TUMM1K | 0.2649 | 9.2254 | -0.0005 | 240
WIOW1Q | WIOW3- | 0.88 | 24.5 | 0 | 60
WIOW1R | WIOW3- | 0.88 | 24.5 | 0 | 60
WOHI1Q | WOHI3- | 0.62 | 27.2399 | 0 | 90
WOHI1R | WOHI3- | 0.61 | 27.31 | 0 | 90

## B-3-1b
Table B.3.1b - SPT Transformers 2014/15 | [5 empty] | Back To Menu
Node1 | Node2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
AREC1- | AREC3A | 0.3886 | 16.84 | -0.0241 | 90
AREC1- | AREC3B | 0.3915 | 16.7288 | -0.0227 | 90
AYR-2Q | AYR-3- | 0.2752 | 25.1818 | -0.0142 | 120
AYR-2R | AYR-3- | 0.4326 | 19.1618 | 0 | 120
BAGA1Q | BAGA3- | 0.741 | 27.0343 | 0 | 90
BAGA1R | BAGA3- | 0.741 | 27.2233 | 0 | 90
BAIN1- | BAIN3- | 0.7736 | 20.7356 | -0.4528 | 60
BAIN1- | BAIN3- | 0.5545 | 26.2275 | -0.0056 | 60
BERW1Q | BERW3- | 0.9683 | 26.4656 | -0.0061 | 60
BERW1Q | MARM0J | 0.933 | 56.0122 | 0 | 10
BERW1R | BERW3- | 0.7912 | 26.5549 | -0.0061 | 60
BERW1R | MARM0K | 0.933 | 56.0122 | 0 | 10
BLKL1- | BLKL3A | 0.0943 | 18.6775 | 0 | 90
BLKL1- | BLKL3B | 0.0955 | 18.6553 | 0 | 90
BONN1- | BONN3- | 0.965 | 21.178 | 0 | 60
BONN1- | BONN3- | 0.965 | 21.178 | 0 | 60
BONN1- | BONN3- | 0.965 | 21.178 | 0 | 60
BONN2A | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240
BONN2B | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90
BROX1Q | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90
BROX1R | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90
CAFA1Q | CAFA5- | 1.0894 | 32.6818 | 0 | 30
CATY1Q | CATY0J | 2.24 | 57.9567 | -0.0633 | 10
CATY1Q | CATY3- | 1.015 | 25.8801 | -0.1318 | 60
CATY1R | CATY0K | 2.2 | 57.9583 | -0.0625 | 10
CATY1R | CATY3- | 1.0164 | 25.6132 | -0.0966 | 60
CHAP1- | CHAP3- | 0.4338 | 27.5299 | -0.0175 | 90
CHAP1- | CHAP3- | 0.4294 | 27.5633 | -0.0188 | 90
CHAS2Q | CHAS3- | 0.4875 | 18.1601 | -0.1331 | 120
CHAS2R | CHAS3- | 0.4868 | 20.6609 | -0.2478 | 120
CLYM2- | CLYM3- | 0.4917 | 19.994 | -0.1425 | 120
CLYM2- | CLYM3- | 0.4722 | 20.2028 | -0.1542 | 120
CLYN2Q | CLYN3A | 0.3432 | 13.0038 | -0.0115 | 120
CLYN2Q | CLYN3B | 0.3423 | 12.9455 | -0.0108 | 120
CLYN2Q | CLYN3C | 0.3414 | 13.0205 | -0.0094 | 120
CLYN2Q | CLYN3D | 0.3472 | 12.9954 | -0.0133 | 120
CLYS2R | CLYS3A | 0.3406 | 12.9789 | -0.0112 | 120
CLYS2R | CLYS3B | 0.3475 | 13.0037 | -0.0112 | 120
COAL4- | COAL1- | 0.1258 | 9.7909 | -0.0801 | 240
COAL4- | COAL1- | 0.1216 | 9.6242 | -0.0793 | 240
COAT2Q | COAT3- | 0.2681 | 24.3152 | -0.021 | 120
COAT2R | COAT3- | 0.2681 | 24.3152 | -0.021 | 120
COCK2- | COCK3- | 0.4809 | 18.5354 | -0.2953 | 120
COCK2- | COCK3- | 0.4792 | 18.7022 | -0.2214 | 120
COCK4Q | COCK2- | 0.0135 | 1.6479 | -0.3338 | 1000
COCK4R | COCK2- | 0.013 | 1.5999 | -0.2252 | 1000
COYL1- | COYL3- | 0.9944 | 20.8596 | -0.0881 | 60
COYL1- | COYL3- | 0.9217 | 21.6804 | 0 | 60
COYL2- | COYL1- | 0.1718 | 8.665 | -0.0204 | 120
COYL2- | COYL1- | 0.3396 | 12.8288 | -0.2375 | 120
CROO1Q | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60
CROO1Q | CROO3K | 0.9194 | 21.9808 | 0 | 60
CROO1R | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60
CROO1R | CROO3K | 0.9758 | 26.6321 | -0.0063 | 60
CRUA2Q | CRUA01 | 0.1442 | 9.4772 | -1.1608 | 270
CRUA2R | CRUA03 | 0.1947 | 9.3713 | 0 | 150
CRUA2R | CRUA04 | 0.192 | 9.358 | 0 | 150
CRYR1- | CRYR31 | 0.438 | 13.3 | 0 | 220
CRYR4- | CRYR1- | 0.1496 | 10.0489 | -0.0583 | 240
CUMB1Q | CUMB3- | 0.7407 | 29.324 | -0.129 | 90
CUMB1R | CUMB3- | 0.741 | 27.111 | 0 | 90
CUPA1Q | CUPA3- | 0.9389 | 19.8778 | 0 | 60
CUPA1R | CUPA3- | 0.9417 | 19.8777 | 0 | 60
CURR1- | CURR5- | 3.225 | 79.0009 | 0 | 30
CURR1- | CURR5- | 3.23 | 79.0007 | 0 | 30
CURR2- | CURR1- | 0.1148 | 8.4492 | -0.073 | 240
CURR2- | CURR1- | 0.1205 | 8.4741 | -0.084 | 240
DALM1- | DALM3- | 0.447 | 27.333 | 0 | 90
DALM1- | DALM3- | 0.469 | 27.333 | 0 | 90
DALM2Q | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240
DALM2R | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240
DEVM1- | DEVM0J | 1.232 | 73.8097 | 0 | 5
DEVM1- | DEVM0K | 1.232 | 73.8097 | 0 | 5
DEVM1- | DEVM3- | 1.0878 | 19.9704 | -1.7577 | 60
DEVM1- | DEVM3- | 1.0869 | 20.0038 | -1.8609 | 60
DEVM4- | DEVM1- | 0.1335 | 8.3739 | -0.1562 | 240
DEVM4- | DEVM1- | 0.1338 | 8.3739 | -0.2103 | 240
DEVO1- | DEVO3- | 0.74 | 29.6674 | 0 | 90
DEVO1- | DEVO3- | 0.728 | 29.4443 | 0 | 90
DEWP2Q | DEWP3- | 0.2936 | 21.0667 | -0.079 | 160
DEWP2R | DEWP3- | 0.4938 | 18.3267 | -0.1402 | 120
DRCR1Q | DRCR3- | 0.5273 | 27.0838 | -0.0105 | 90
DRCR1R | DRCR3- | 0.5227 | 26.8727 | -0.0109 | 90
DRUM2Q | DRUM3- | 0.3963 | 23.9134 | -0.0247 | 120
DRUM2R | DRUM3- | 0.4418 | 19.2866 | 0 | 120
DUMF1- | DUMF3- | 0.367 | 11.7276 | 0 | 90
DUMF1- | DUMF3- | 0.375 | 11.794 | 0 | 90
DUMF1- | DUMF3I | 0.766 | 20.5657 | 0 | 60
DUMF1- | DUMF5- | 5.333 | 68.3322 | 0 | 30
DUMF1- | DUMF5- | 5.333 | 79.0002 | 0 | 30
DUNB1Q | DUNB3- | 0.8069 | 21.4849 | -0.3294 | 60
DUNB1R | DUNB3- | 0.8069 | 21.4849 | -0.3294 | 60
DUNE1- | DUNE3- | 0.4271 | 19.5731 | -0.0091 | 90
DUNE1- | DUNE3- | 0.4249 | 19.3175 | -0.0084 | 90
DUNF1Q | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90
DUNF1R | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90
DUNO1Q | DUNO3- | 2 | 24.49 | 0 | 45
DUNO1R | DUNO3- | 2 | 24.5801 | 0 | 45
EAST1Q | EAST5- | 4.1511 | 74.885 | -0.1943 | 15
ECCF1J | ECCF0J | 1.4773 | 33.3006 | -0.0896 | 15
ECCF1K | ECCF0K | 0.4481 | 26.8629 | 0 | 18
ECCL1- | ECCL3- | 1.054 | 26.8827 | 0 | 60
ECCL1- | ECCL3- | 1.04 | 26.7314 | 0 | 60
ECCL4- | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240
ECCL4- | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240
EERH2- | EERH3- | 0.4868 | 18.7437 | -0.2478 | 120
EERH2- | EERH3- | 0.2569 | 25.607 | -0.0414 | 120
EKIL2S | EKIL3- | 0.303 | 17.9224 | -0.0436 | 120
EKIL2T | EKIL3- | 0.303 | 17.8441 | -0.0485 | 120
EKIS2- | EKIS3- | 0.4948 | 24.3283 | -0.2487 | 120
EKIS2- | EKIS3- | 0.4773 | 24.2453 | -0.2651 | 120
ELDE1Q | ELDE3- | 0.9136 | 19.8123 | -0.3053 | 60
ELDE1R | ELDE3- | 0.9136 | 19.9791 | -0.3053 | 60
ELVA4- | ELVA0J | 0.1612 | 10.3112 | -0.0029 | 80
ELVA4- | ELVA0K | 0.1613 | 10.3112 | -0.0101 | 80
ELVA4- | ELVA2Q | 0.0309 | 3.2879 | -0.8983 | 500
ELVA4- | ELVA2R | 0.031 | 3.2859 | -0.8082 | 500
ERSK1Q | ERSK3- | 1.7778 | 33.4528 | 0 | 30
ERSK1R | ERSK3- | 1.84 | 34.3174 | 0 | 30
FALL4- | FALL3A | 0.2564 | 16.6647 | 0 | 120
FALL4- | FALL3B | 0.2564 | 16.6647 | 0 | 120
FIFE1A | FIFE5- | 0.364 | 13.3328 | 0 | 90
FIFE1B | FIFE5B | 0.4312 | 34.0973 | -0.0668 | 70
FINN1Q | FINN3- | 0.5198 | 26.0837 | -0.0091 | 90
FINN1R | FINN3- | 0.5221 | 25.9836 | -0.0092 | 90
GALA1- | GALA3- | 1.1936 | 28.2415 | 0 | 45
GALA1- | GALA3- | 1.5733 | 28.6235 | 0 | 45
GIFF2Q | GIFF3- | 0.4958 | 18.4517 | -0.196 | 120
GIFF2R | GIFF3- | 0.4868 | 18.3352 | -0.2147 | 120
GLLE1- | GLLE5- | 2.3889 | 72.9609 | 0 | 30
GLLU1Q | GLLU3- | 0.961 | 24.5329 | 0 | 60
GLLU1R | GLLU3- | 1.069 | 25.0839 | 0 | 60
GLNI1- | GLNI3- | 0.6894 | 27.7692 | -0.1102 | 90
GLNI1- | GLNI3- | 0.6998 | 27.8134 | -0.1093 | 90
GLRO2- | GLRO3A | 0.479 | 24.4953 | 0 | 120
GLRO2- | GLRO3B | 0.4763 | 24.412 | 0 | 120
GORG1Q | GORG3- | 0.9167 | 21.8975 | 0 | 60
GORG1R | GORG3- | 0.9111 | 21.9311 | 0 | 60
GOVA1Q | GOVA3- | 0.5223 | 26.1503 | -0.0083 | 90
GOVA1R | GOVA3- | 0.5155 | 26.1727 | -0.0108 | 90
GRMO2- | BPGR3J | 0.5271 | 18.7426 | -0.222 | 120
GRMO2- | BPGR3K | 0.3093 | 18.8225 | -0.0373 | 120
GRMO2- | GRMO3C | 0.4781 | 25.1621 | -0.0871 | 120
GRMO2- | GRMO3C | 0.4985 | 25.2451 | -0.0869 | 120
GRNA1- | EWEH5- | 1.161 | 23.225 | 0 | 40
GRNA4- | GRNA1- | 0.1472 | 10.0573 | -0.0558 | 240
GRNA4- | GRNA1- | 0.1252 | 9.7909 | -0.081 | 240
HADH1- | HADH3- | 0.438 | 13.3003 | 0 | 120
HAGR1Q | HAGR3- | 0.9806 | 20.7268 | -1.3737 | 60
HAGR1R | HAGR3- | 0.5478 | 25.8775 | -0.008 | 60
HARE1- | HARE3- | 0.2834 | 16.8087 | -0.0216 | 90
HARE1- | HARE3- | 0.2866 | 16.7864 | -0.0216 | 90
HAWI1- | HAWI3- | 1.0278 | 25.6127 | -0.1152 | 60
HAWI1- | HAWI3- | 1.0136 | 25.8802 | -0.1316 | 60
HELE1- | HELE3- | 0.9544 | 20.8615 | 0 | 60
HELE1- | HELE3- | 0.6843 | 28.6252 | -0.0082 | 60
HUER4- | HUER07 | 0.0205 | 2.045 | -1.5848 | 753
HUER4- | HUER08 | 0.0235 | 2.0902 | -1.8199 | 753
HUER4- | HUER1- | 0.1122 | 9.3465 | -0.2007 | 360
HUER4- | HUER1- | 0.1134 | 9.4715 | -0.1992 | 360
HUNF1Q | HUNF3- | 0.8042 | 16.5638 | -0.06 | 60
HUNF1R | HUNF3- | 0.7893 | 16.4144 | -0.0596 | 60
INKE1Q | INKE3- | 0.6185 | 23.7697 | 0 | 90
INKE1R | INKE3- | 0.6222 | 23.7696 | 0 | 90
INWI1Q | INWI0J | 0.917 | 55.0024 | 0 | 10
INWI1R | INWI0K | 0.917 | 55.0024 | 0 | 10
JOHN1Q | JOHN3- | 0.9461 | 21.8128 | 0 | 60
JOHN1R | JOHN3- | 0.9461 | 21.8128 | 0 | 60
KAIM2- | KAIM3- | 0.4819 | 20.2443 | -0.2454 | 120
KAIM2- | KAIM3- | 0.4944 | 20.244 | -0.245 | 120
KEOO1- | KEOO5- | 2.9 | 71.608 | -0.028 | 30
KIER1Q | KIER3- | 0.7227 | 25.3341 | 0 | 90
KIER1R | KIER3- | 0.7227 | 24.8895 | 0 | 90
KILB1Q | KILB3- | 0.9214 | 23.8656 | -0.6492 | 60
KILB1Q | KILB5- | 4.3575 | 97.6528 | -0.0539 | 20
KILB1R | KILB3- | 0.8919 | 23.8333 | -0.6287 | 60
KILB1R | KILB5- | 4.3825 | 97.2012 | -0.059 | 20
KILS2- | KILS1- | 0.143 | 8.6447 | -0.1299 | 240
KILS2- | KILS3- | 0.5013 | 24.0114 | -0.1726 | 120
KILS2- | KILS3- | 0.4823 | 24.1619 | -0.2177 | 120
KILS4- | KILS2- | 0.018 | 1.6069 | -0.5085 | 1000
KILS4- | KILS2- | 0.0134 | 1.6649 | -0.5095 | 1000
KILT2Q | KILT3- | 0.4927 | 18.4934 | -0.1756 | 120
KILT2R | KILT3- | 0.4976 | 18.4933 | -0.1775 | 120
KILW1Q | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90
KILW1R | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90
LEVE1Q | LEVE3- | 0.979 | 20.6001 | 0 | 60
LEVE1R | LEVE3- | 0.944 | 20.7502 | 0 | 60
LING1Q | LING3- | 0.7346 | 29.6576 | -0.1478 | 90
LING1R | LING3- | 0.7309 | 28.7685 | -0.109 | 90
LINM1Q | LINM3- | 0.4309 | 27.7078 | -0.0186 | 90
LINM1R | LINM3- | 0.4283 | 27.73 | -0.0186 | 90
LOAN2- | LOAN01 | 0.029 | 2.9709 | 0 | 690
LOAN2- | LOAN02 | 0.029 | 2.9709 | 0 | 690
LOAN2- | LOAN03 | 0.0287 | 2.9564 | 0 | 690
LOAN2- | LOAN04 | 0.0296 | 2.9709 | 0 | 690
MAHI2- | MAHI1- | 0.1284 | 8.6824 | -0.2535 | 240
MAHI2- | MAHI3- | 0.2928 | 12.1973 | -0.0267 | 120
MAYB1- | MAYB3- | 1.84 | 33.2825 | 0 | 30
MAYB1- | MAYB3- | 1.84 | 34.3174 | 0 | 30
MEAD1Q | MEAD5- | 1.161 | 23.225 | 0 | 40
MEAD1R | MEAD5- | 1.174 | 23.475 | 0 | 40
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240
MOSH1Q | MOSH5J | 1.1896 | 19.9646 | 0 | 37.5
MOSH1R | MOSH5K | 1.1896 | 19.9646 | 0 | 37.5
MOSM1- | MOSM3Q | 1.4321 | 26.6282 | 0 | 45
MOSM1- | MOSM3R | 1.4321 | 26.6282 | 0 | 45
MOSM2Q | MOSM1- | 0.151 | 8.332 | -0.1299 | 240
MOSM2Q | MOSM1- | 0.157 | 8.7486 | -0.1299 | 240
NEAR2Q | NEAR3- | 0.4856 | 18.2435 | -0.1614 | 120
NEAR2R | NEAR3- | 0.4856 | 18.1602 | -0.1723 | 120
NEIL2- | NEIL1- | 0.1457 | 8.5196 | -0.1979 | 240
NEIL2- | NEIL1- | 0.1509 | 8.4778 | -0.1862 | 240
NEIL4Q | NEIL1C | 0.1122 | 9.3882 | -0.2007 | 360
NEIL4Q | NEIL2C | 0.0181 | 1.6169 | -0.4986 | 1000
NETS1- | NETS3- | 0.3511 | 18.3966 | -0.0097 | 60
PAIS1S | PAIS3- | 0.5609 | 26.1773 | -0.004 | 60
PAIS1T | PAIS3- | 0.7736 | 20.352 | -0.216 | 60
PART1Q | PART3- | 0.9103 | 21.2972 | 0 | 60
PART1R | PART3- | 0.93 | 21.5299 | 0 | 60
POOB2Q | POOB0J | 0.5559 | 33.3287 | 0 | 18
POOB2Q | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120
POOB2R | POOB0K | 0.5559 | 33.3287 | 0 | 18
POOB2R | POOB3- | 0.5 | 19.278 | 0 | 90
PORD2Q | PORD3- | 0.3702 | 18.3296 | -0.1621 | 120
PORD2R | PORD3- | 0.3698 | 18.3963 | -0.1357 | 120
REDH1- | REDH3- | 0.94 | 19.8995 | 0 | 60
REDH1- | REDH3- | 0.6267 | 19.9124 | 0 | 90
SACO1Q | SACO0J | 0.933 | 56.0022 | 0 | 10
SACO1Q | SACO3J | 0.9444 | 24.4484 | 0 | 60
SACO1Q | SACO3K | 0.9542 | 21.1451 | 0 | 60
SACO1R | SACO0K | 0.933 | 56.0022 | 0 | 10
SACO1R | SACO3J | 0.9444 | 24.4484 | 0 | 60
SACO1R | SACO3K | 0.9683 | 21.4114 | 0 | 60
SANX1Q | SANX0J | 0.558 | 33.4787 | 0 | 18
SANX1Q | SANX3- | 0.8844 | 21.5485 | -0.309 | 60
SANX1R | SANX0K | 0.558 | 33.4787 | 0 | 18
SANX1R | SANX3- | 0.8767 | 21.2319 | -0.3087 | 60
SHRU2Q | SHRU3- | 0.4656 | 19.9946 | -0.3204 | 120
SHRU2R | SHRU3- | 0.4926 | 19.9939 | -0.2739 | 120
SIGH2Q | SIGH3A | 0.4536 | 27.274 | 0 | 180
SIGH2R | SIGH3A | 0.4868 | 18.7437 | 0 | 120
SMEA2- | SMEA1- | 0.1271 | 8.7241 | -0.043 | 240
SMEA4R | SMEA2- | 0.0134 | 1.6639 | -0.2312 | 1000
SPAV1Q | SPAV3- | 0.728 | 26.6656 | 0 | 90
SPAV1R | SPAV3- | 0.728 | 26.6656 | 0 | 90
STHA2A | STHA3- | 0.4722 | 20.2445 | -0.1542 | 120
STHA2B | STHA3- | 0.4917 | 19.994 | -0.1424 | 120
STHA4- | STHA2A | 0.018 | 1.7059 | -0.2252 | 1000
STHA4- | STHA2B | 0.0134 | 1.6949 | -2.0384 | 1000
STIR1S | STIR3- | 0.6 | 27.5446 | 0 | 90
STIR1T | STIR3- | 0.503 | 27.1331 | 0 | 90
STLE1- | STLE0J | 0.958 | 57.502 | 0 | 10
STLE1- | STLE0K | 0.958 | 57.502 | 0 | 10
STLE1- | STLE3S | 0.8975 | 24.7838 | 0 | 60
STLE1- | STLE3S | 0.8975 | 24.9005 | 0 | 60
TELR1Q | TELR3- | 0.9575 | 20.6778 | 0 | 60
TELR1R | TELR3- | 0.6325 | 28.5763 | -0.0081 | 60
TONG1- | TONG1R | 0.0267 | 1.3331 | 0 | 90
TONG1- | TONG5- | 1.6834 | 33.9917 | -0.01 | 30
TONG1- | TONG5- | 1.6721 | 34.0924 | -0.0269 | 30
TONG1Q | TONG1R | 0.0125 | 2.5 | 0 | 90
TORN4- | TORN01 | 0.02 | 2.01 | 0 | 800
TORN4- | TORN02 | 0.02 | 2.01 | 0 | 800
TORN4- | TORN1- | 0.1674 | 8.0399 | -0.0509 | 240
TORN4- | TORN1- | 0.1688 | 8.0816 | -0.0663 | 240
WFIE1A | WFIE3- | 0.9889 | 20.4928 | 0 | 60
WFIE1B | WFIE3- | 0.9528 | 20.5613 | 0 | 60
WFIE2- | WFIE1A | 0.1408 | 8.6113 | -0.1827 | 240
WFIE2- | WFIE1B | 0.1264 | 8.7366 | -0.1602 | 240
WGEO2Q | WGEO3- | 0.4889 | 18.2518 | -0.2083 | 120
WGEO2R | WGEO3- | 0.4911 | 18.3268 | -0.2083 | 120
WHHO2Q | WHHO3- | 0.4128 | 24.9549 | -0.0345 | 120
WHHO2R | WHHO3- | 0.5236 | 20.1599 | -0.1959 | 120
WHTL1S | WHTL3- | 2 | 27.1108 | 0 | 45
WHTL1T | WHTL3- | 2 | 27.1108 | 0 | 45
WISH2- | WISH0J | 0.4979 | 29.8997 | 0 | 26
WISH2- | WISH0K | 0.4979 | 29.8997 | 0 | 26
WISH2- | WISH1- | 0.1297 | 8.8874 | -0.2192 | 215
WISH2- | WISH3- | 0.4821 | 24.1785 | -0.226 | 120
WISH2- | WISH3- | 0.4824 | 24.1285 | -0.2277 | 120
WISH2- | WISH3S | 0.4382 | 19.1617 | -0.195 | 120
WISH2- | WISH3T | 0.4889 | 18.3268 | -0.1166 | 120
WIYH2- | WIYH1- | 0.1568 | 8.4569 | -0.3494 | 240
WIYH2- | WIYH1- | 0.1517 | 8.707 | -0.1161 | 240
WIYH2- | WIYH1- | 0.1524 | 8.457 | -0.3487 | 240
WIYH4Q | WIYH2- | 0.0133 | 1.6699 | -0.3581 | 1000
WLEE2- | WLEE3A | 0.2583 | 12.2648 | -0.0357 | 120
WLEE2- | WLEE3B | 0.2592 | 12.1922 | -0.0271 | 120
WLEE2- | WLEE3C | 0.26 | 12.3048 | -0.0301 | 120
WLEX2- | WLEX3A | 0.231 | 12.258 | 0 | 120
WLEX2- | WLEX3B | 0.231 | 12.275 | 0 | 120
WLEX2- | WLEX3C | 0.232 | 12.292 | 0 | 120

## B-3-1c
Table B.3.1c - NGET Transformers 2014/15 | [5 empty] | Back To Menu
Node 1 | Node 2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
ABHA41 | ABHA12 | 0.1658 | 8.4025 | -1.5604 | 240
ABHA42 | ABHA11 | 0.1658 | 8.4025 | -1.5604 | 240
ABTH21 | ABTH11 | 0.1366 | 8.0648 | -0.0471 | 240
ABTH21 | ABTH12 | 0.0977 | 8.1994 | -1.7127 | 180
ABTH21 | ABTH13 | 0.1646 | 8.0383 | -0.1808 | 180
ALDW21 | ALDW31 | 0.7076 | 26.5771 | -0.0784 | 98
ALDW21 | ALDW31 | 0.4848 | 24.6692 | -0.018 | 105
ALDW21 | ALDW31 | 0.3543 | 25.4142 | -0.4983 | 105
ALDW21 | ALDW32 | 0.656 | 25.925 | -0.297 | 32
ALDW21 | ALDW32 | 0.656 | 25.925 | -0.297 | 32
ALVE4A | ALVE11 | 0.1118 | 8.3874 | -0.0906 | 240
ALVE4B | ALVE11 | 0.1621 | 8.0984 | -0.0747 | 240
AMEM41 | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 240
AMEM42 | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 240
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 240
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 240
BARK21 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 240
BARK21 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 240
BARK21 | BARW31 | 0.618 | 29.2635 | -0.2527 | 100
BARK21 | BARW32 | 0.618 | 29.2635 | -0.2527 | 100
BARK22 | BARK11 | 0.1646 | 8.0383 | -0.1808 | 180
BARK22 | BARK11 | 0.1221 | 8.0467 | -0.0391 | 217
BARK22 | BARW31 | 0.618 | 29.2635 | -0.2527 | 100
BARK22 | BARW32 | 0.492 | 19.4438 | -0.4018 | 100
BARK22 | BARW32 | 0.618 | 29.2635 | -0.2527 | 100
BARK41 | BARK21 | 0.0268 | 2.7989 | -0.3188 | 750
BARK41 | BARK22 | 0.0268 | 2.7989 | -0.3188 | 750
BEDD21 | BEDD2* | 0.2264 | 12.2479 | -0.6062 | 120
BEDD21 | BEGI11 | 0.167 | 7.9774 | -0.2092 | 240
BEDD21 | BEGI12 | 0.167 | 7.9774 | -0.2092 | 240
BEDD22 | BEGI12 | 0.167 | 7.9774 | -0.2092 | 240
BEDD23 | BEDD2* | 0.2264 | 12.2479 | -0.6062 | 120
BEDD23 | BEGI11 | 0.167 | 7.9774 | -0.2092 | 240
BEDD4A | BEDD2* | 0.0258 | 2.6799 | -1.2431 | 750
BEDD4A | BEDD23 | 0.0258 | 2.6799 | -1.2431 | 750
BEDD4B | BEDD21 | 0.0258 | 2.6799 | -1.2431 | 750
BEDD4B | BEDD22 | 0.0258 | 2.6805 | -1.2431 | 750
BESW21 | BESW11 | 0.1411 | 8.6331 | -0.2264 | 240
BESW21 | BESW11 | 0.1411 | 8.6331 | -0.2264 | 240
BESW21 | BESW12 | 0.1411 | 8.6331 | -0.2264 | 240
BICF41 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 240
BICF42 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 240
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 240
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 240
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 240
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 240
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 240
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 240
BISW21 | BISW11 | 0.0918 | 8.7537 | -0.0575 | 240
BLYT21 | BLYT1A | 0.1666 | 8.378 | -0.1047 | 240
BLYT21 | BLYT1B | 0.1666 | 8.378 | -0.1047 | 240
BLYT21 | BLYT61 | 0.2275 | 10.8456 | -0.0697 | 180
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 120
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 120
BLYT4* | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1100
BLYT4* | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1100
BODE41 | SASA11 | 0.1311 | 7.9055 | -0.1016 | 240
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 275
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 275
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 275
BOLN41 | BOLN12 | 0.1557 | 8.3736 | -0.4146 | 275
BOLN41 | BOLN12 | 0.1264 | 8.4534 | -0.357 | 275
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 240
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 240
BRAI4A | BRAI11 | 0.1373 | 8.1976 | -0.1719 | 240
BRAI4B | BRAI11 | 0.1307 | 7.9515 | -0.1098 | 240
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 240
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 240
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 240
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 240
BRAW4A | BRAW21 | 0.0175 | 1.5879 | -4.0069 | 1000
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 240
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 240
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 240
BRFO41 | BRFO1* | 0.1307 | 7.9515 | -0.1098 | 240
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 260
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 260
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 265
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 265
BRIM2A | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 240
BRIM2B | BRIM11 | 0.1266 | 8.6449 | -1.9406 | 240
BRIM2C | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 240
BRIM2D | BRIM1* | 0.1688 | 8.3316 | -1.1711 | 240
BRIN41 | BRIN2* | 0.0146 | 1.609 | -1.8746 | 1000
BRIN41 | BRIN22 | 0.0132 | 1.6756 | -0.4337 | 1000
BRLE41 | BRLE1* | 0.1303 | 7.8698 | -0.4285 | 240
BRLE41 | BRLE1* | 0.1303 | 7.8698 | -0.4285 | 240
BRLE41 | BRLE11 | 0.103 | 7.9231 | -0.0638 | 240
BRLE41 | BRLE12 | 0.1471 | 8.4008 | -0.1719 | 240
BRLE41 | BRLE13 | 0.1471 | 8.4008 | -0.1719 | 240
BRLE41 | BRLE14 | 0.103 | 7.9231 | -0.0638 | 240
BRWA2A | BRWA11 | 0.167 | 7.9774 | -0.2092 | 240
BRWA2B | BRWA11 | 0.167 | 7.9774 | -0.2092 | 240
BURW41 | BURW11 | 0.1675 | 8.2453 | -0.6567 | 240
BURW41 | BURW11 | 0.1675 | 8.2453 | -0.6567 | 240
BURW41 | BURW11 | 0.1812 | 8.028 | -0.1253 | 240
BUSH21 | BUSH11 | 0.1048 | 8.8443 | -0.0335 | 240
BUSH21 | BUSH11 | 0.1221 | 8.0467 | -0.0391 | 240
BUSH21 | BUSH11 | 0.1221 | 8.0467 | -0.0391 | 240
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 240
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 240
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 240
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 240
CANT41 | CANT11 | 0.1658 | 8.426 | -0.2939 | 240
CANT41 | CANT12 | 0.1509 | 8.2849 | -0.3279 | 240
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 180
CAPE21 | CAPE11 | 0.196 | 8.3446 | -0.7059 | 180
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 180
CAPE21 | CAPE1A | 0.1366 | 8.0648 | -0.0471 | 240
CAPE21 | CAPE1B | 0.171 | 8.8392 | -0.0268 | 180
CAPE41 | CAPE21 | 0.0185 | 1.614 | -0.5638 | 750
CAPE42 | CAPE21 | 0.0178 | 1.5995 | -1.2431 | 750
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 240
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 240
CARR21 | CARR1* | 0.1927 | 8.5256 | -0.5357 | 180
CARR21 | CARR11 | 0.1681 | 8.3396 | -1.4878 | 180
CARR21 | CARR11 | 0.1927 | 8.5256 | -0.5357 | 180
CARR21 | CARR12 | 0.2264 | 12.2479 | -0.6062 | 120
CARR21 | CARR12 | 0.2847 | 12.2467 | -1.4346 | 120
CARR41 | CARR11 | 0.1812 | 8.028 | -0.1253 | 240
CARR42 | CARR21 | 0.0185 | 1.614 | -0.5638 | 750
CARR43 | CARR21 | 0.0185 | 1.614 | -0.5638 | 750
CELL41 | CELL1* | 0.1658 | 8.4025 | -1.5604 | 240
CELL41 | CELL11 | 0.1658 | 8.4025 | -1.5604 | 240
CELL41 | CELL11 | 0.1307 | 7.9515 | -0.1098 | 240
CELL41 | CELL12 | 0.1658 | 8.4025 | -1.5604 | 240
CELL41 | CELL12 | 0.1373 | 8.1976 | -0.1719 | 240
CELL41 | CELL4* | 0.3995 | 7.99 | -0.1549 | 170
CELL41 | CELL4* | 0.3995 | 7.99 | -0.1549 | 170
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 240
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 240
CHSI21 | CHSI11 | 0.167 | 7.9774 | -0.2092 | 240
CHSI21 | CHSI11 | 0.1411 | 8.6331 | -0.2264 | 240
CHSI21 | CHSI1A | 0.2264 | 12.2479 | -0.6062 | 120
CHSI21 | CHSI1B | 0.2264 | 12.2479 | -0.6062 | 120
CHTE21 | CHTE11 | 0.1545 | 7.6337 | -0.562 | 240
CHTE21 | CHTE11 | 0.1594 | 8.6081 | -0.2215 | 240
CHTE21 | CHTE12 | 0.1545 | 7.6337 | -0.562 | 240
CHTE21 | CHTE12 | 0.0918 | 8.7537 | -0.0575 | 240
CILF41 | CILF21 | 0.017 | 1.6132 | -5.1203 | 750
CILF41 | CILF22 | 0.017 | 1.6132 | -5.1203 | 750
CITR41 | CITR11 | 0.1264 | 7.974 | -0.1303 | 240
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 240
CITR41 | CITR11 | 0.0997 | 8.0088 | -0.093 | 240
CITR41 | CITR12 | 0.1373 | 8.1976 | -0.1719 | 240
CITR41 | CITR12 | 0.1229 | 8.3873 | -0.1147 | 240
CITR41 | CITR12 | 0.1373 | 8.1976 | -0.1719 | 240
CONQ41 | CONQ11 | 0.103 | 7.9231 | -0.0638 | 240
CONQ41 | CONQ11 | 0.1557 | 8.3736 | -0.4146 | 240
COTT41 | COTT52 | 1.892 | 30.9 | -19.9978 | 9999
COTT42 | COTT51 | 4.952 | 31 | -19.9978 | 9999
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 240
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 240
COVE21 | COVE12 | 0.1392 | 8.4361 | -0.781 | 240
COVE21 | COVE12 | 0.1623 | 8.097 | -1.5978 | 240
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 240
COWL41 | COWL11 | 0.1307 | 7.9515 | -0.1098 | 240
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 240
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 240
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 240
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 240
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 240
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 240
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 240
CREB41 | CREB21 | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB21 | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB22 | 0.0176 | 1.5826 | -0.1148 | 1500
CREB41 | CREB22 | 0.0176 | 1.5826 | -0.1148 | 1500
CULJ41 | CULJ3* | 0.069 | 25 | 0 | 90
CULJ41 | CULJ3* | 0.069 | 25 | 0 | 90
CULJ41 | CULJ3* | 0.069 | 25 | 0 | 90
DEES41 | CONQ13 | 0.1057 | 7.9352 | -0.339 | 240
DEES41 | DEES4* | 0 | 2 | 0 | 600
DEES42 | CONQ12 | 0.1264 | 8.4534 | -0.357 | 240
DRAK21 | DRAK11 | 0.2264 | 12.2479 | -0.6062 | 120
DRAK21 | DRAK2* | 0.2756 | 9.9228 | -0.0925 | 150
DRAK41 | DRAK11 | 0.1303 | 7.8698 | -0.4285 | 240
DRAK41 | DRAK11 | 0.1303 | 7.8698 | -0.4285 | 240
DRAK41 | DRAK21 | 0.0178 | 1.5995 | -1.2431 | 750
DRAK41 | DRAK21 | 0.0175 | 1.5879 | -4.0069 | 1000
DRAK41 | Term262 | 0.017 | 1.6132 | -5.1203 | 750
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 240
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 240
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 180
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 180
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 710
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 710
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126
EASO41 | EASO1* | 0.103 | 7.9231 | -0.0638 | 240
EASO41 | EASO1* | 0.103 | 7.9231 | -0.0638 | 240
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 240
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 240
ECLA41 | ECLA12 | 0.1139 | 8.1036 | -2.059 | 240
ECLA41 | ECLA12 | 0.0997 | 8.0088 | -0.093 | 240
ECLA41 | ECLA4* | 0.2528 | 5.057 | -0.2264 | 237
EGGB41 | EGGB51 | 0 | 30.9 | -19.9978 | 9999
EGGB42 | EGGB51 | 0 | 30.52 | -19.9978 | 9999
ELLA21 | ELLA11 | 0.1221 | 8.0467 | -0.0391 | 240
ELLA21 | ELLA11 | 0.1681 | 8.3396 | -1.4878 | 180
ELLA21 | ELLA12 | 0.1722 | 8.4551 | -0.2968 | 180
ELLA21 | ELLA12 | 0.1221 | 8.0467 | -0.0391 | 240
ELST21 | ELST1* | 0.1221 | 8.0467 | -0.0391 | 240
ELST21 | ELST12 | 0.1954 | 8.0796 | -0.2295 | 180
ELST21 | ELST12 | 0.1985 | 8.1167 | -0.4624 | 180
ELST21 | ELST13 | 0.3567 | 11.136 | -0.7303 | 120
ELST22 | ELST11 | 0.1031 | 8.1045 | -0.0494 | 180
ELST22 | ELST11 | 0.1923 | 8.081 | -1.4418 | 180
ELST22 | ELST14 | 0.3567 | 11.136 | -0.7303 | 120
ELST41 | ELST11 | 0.1303 | 7.8698 | -0.4285 | 240
ELST41 | ELST22 | 0.0181 | 1.5835 | -3.6502 | 1100
ELST42 | ELST21 | 0.0176 | 1.5828 | -0.1018 | 1000
ENDE41 | ENDE1* | 0.1303 | 7.8698 | -0.4285 | 240
ENDE41 | ENDE11 | 0.1118 | 8.3874 | -0.0906 | 240
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 240
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 240
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 240
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 240
FECK21 | FECK2* | 0.2756 | 9.9228 | -0.0925 | 150
FECK21 | FECK61 | 0.3142 | 15.7855 | -1.1826 | 120
FECK41 | FECK21 | 0.0211 | 1.6463 | -14.2471 | 1000
FECK41 | FECK4* | 0.2575 | 14.031 | -0.9837 | 180
FECK41 | FECK4* | 0.1867 | 13.8218 | -0.1803 | 180
FECK41 | FECK4* | 0.1867 | 13.8218 | -0.1803 | 180
FERR22 | FERR11 | 0.1147 | 8.673 | -0.0358 | 240
FERR22 | FERR12 | 0.3732 | 11.6023 | -0.7962 | 120
FERR22 | FERR61 | 0.237 | 10.8633 | -0.263 | 180
FERR23 | FERR11 | 0.1147 | 8.673 | -0.0358 | 240
FERR23 | FERR61 | 0.237 | 10.8633 | -0.263 | 180
FERR2A | FERR11 | 0.0918 | 8.7537 | -0.0575 | 240
FERR2B | FERR12 | 0.2847 | 12.2467 | -1.4346 | 120
FERR41 | FERR21 | 0.0144 | 1.4435 | -4.4078 | 1100
FERR41 | FERR23 | 0.0186 | 1.5729 | -7.729 | 1000
FIDF21 | FIDF12 | 0.2847 | 12.2467 | -1.4346 | 120
FIDF21 | FIDF13 | 0.1594 | 8.6081 | -0.2215 | 240
FIDF22 | FIDF11 | 0.1392 | 8.4361 | -0.781 | 240
FIDF23 | FIDF1* | 0.2847 | 12.2467 | -1.4346 | 120
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 240
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 240
FLEE41 | FLEE11 | 0.1368 | 8.5406 | -0.262 | 240
FLEE41 | FLEE11 | 0.1812 | 8.028 | -0.1253 | 240
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 240
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 240
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 240
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 40
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 40
FROD21 | FROD11 | 0.1927 | 8.5256 | -0.5357 | 180
FROD22 | FROD11 | 0.1392 | 8.4361 | -0.781 | 240
FROD41 | FROD1* | 0.054 | 4.8906 | -0.1253 | 460
FROD41 | FROD21 | 0.0176 | 1.5828 | -0.1018 | 1000
FROD41 | FROD22 | 0.0132 | 1.6756 | -0.4337 | 1000
FROD41 | WEAV * | 0.3209 | 20.5475 | -0.1224 | 80
FROD41 | WEAV * | 0.3209 | 20.5475 | -0.1224 | 80
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 240
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 240
GREN41 | GREN11 | 0.1557 | 8.3736 | -0.4146 | 240
GREN41 | GREN11 | 0.1307 | 7.9515 | -0.1098 | 240
GREN41 | GREN11 | 0.1303 | 7.8698 | -0.4285 | 240
GREN41 | GREN12 | 0.1557 | 8.3736 | -0.4146 | 240
GREN41 | GREN12 | 0.1557 | 8.3736 | -0.4146 | 240
GRIW41 | GRIW11 | 0.1658 | 8.4025 | -1.5604 | 240
GRIW41 | GRIW12 | 0.1658 | 8.4025 | -1.5604 | 240
GRSA21 | GRST52 | 0.01 | 0.1 | -0.5946 | 300
GRSB21 | GRST51 | 0.01 | 0.1 | -0.5946 | 300
HACK21 | HACK61 | 0.2793 | 13.3304 | -0.6737 | 180
HACK22 | HACK61 | 0.2793 | 13.3304 | -0.6737 | 180
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 240
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 240
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 240
HACK41 | HACK21 | 0.0182 | 1.5763 | -0.0904 | 1100
HACK41 | HACK22 | 0.0182 | 1.5763 | -0.0904 | 1100
HAMH41 | HAMH2A | 0.0175 | 1.5879 | -4.0069 | 1000
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 240
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 240
HAMH41 | LEMR12 | 0.1118 | 8.3874 | -0.0906 | 240
HAMH41 | LEMR12 | 0.1118 | 8.3874 | -0.0906 | 240
HARK21 | HARK11 | 0.3328 | 11.6619 | -0.9523 | 120
HARK21 | HARK12 | 0.3328 | 11.6619 | -0.9523 | 120
HARK21 | HARK2* | 0.2756 | 9.9228 | -0.0925 | 150
HARK22 | HARK11 | 0.2264 | 12.2479 | -0.6062 | 120
HARK22 | HARK12 | 0.3328 | 11.6619 | -0.9523 | 120
HARK22 | HARK13 | 0.1147 | 8.673 | -0.0358 | 222
HARK22 | HARK2* | 0.2756 | 9.9228 | -0.0925 | 150
HARK4* | HARK22 | 0.0292 | 2.402 | -0.2732 | 500
HARK41 | HARK21 | 0.0321 | 2.4344 | -0.0528 | 500
HARK41 | HARK21 | 0.0376 | 2.3797 | -3.9009 | 500
HARK41 | HARK22 | 0.0376 | 2.3797 | -3.9009 | 500
HARM21 | HARM61 | 0.3726 | 16.7215 | -0.6945 | 120
HARM21 | HARM61 | 0.3726 | 16.7215 | -0.6945 | 120
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 180
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 180
HAWP4A | HAWP21 | 0.0132 | 1.6756 | -0.4337 | 1000
HEYS41 | HEYS11 | 0.122 | 8.1963 | -0.2446 | 240
HEYS41 | HEYS11 | 0.1658 | 8.4025 | -1.5604 | 240
HEYS41 | HEYS11 | 0.1812 | 8.028 | -0.1253 | 240
HIGM41 | HIGM2* | 0.0326 | 2.3798 | -3.9003 | 500
HIGM41 | HIGM21 | 0.0186 | 1.5729 | -7.729 | 1000
HIGM41 | HIGM4A | 0.0002 | 0.2873 | 0 | 2150
HINP21 | HINP51 | 4.2566 | 124.6774 | 0 | 20
HINP21 | HINP53 | 1.1395 | 34.8994 | 0 | 61
HINP22 | HINP52 | 4.25 | 106.4152 | 0 | 20
HINP22 | HINP54 | 1.1395 | 35.4243 | 0 | 61
HINP41 | HINP21 | 0.0363 | 2.4397 | -2.1073 | 500
HINP41 | HINP22 | 0.0376 | 2.3797 | -3.9009 | 500
HUMR41 | HUMR31 | 0.6667 | 22.467 | -0.1612 | 90
HUMR41 | HUMR31 | 0.6667 | 22.256 | -0.1612 | 90
HURS21 | HURS1B | 0.1221 | 8.0467 | -0.0391 | 240
HURS21 | HURS1C | 0.1382 | 8.1742 | -0.1786 | 240
HURS21 | HURS1D | 0.1392 | 8.4361 | -0.781 | 240
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 240
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 240
HUTT41 | HUTT4* | 0.3195 | 20.7975 | -0.0003 | 80
HUTT41 | HUTT4* | 0.3195 | 20.7975 | -0.0003 | 80
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 143
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 143
INDQ41 | INDQ11 | 0.1278 | 8.0061 | -0.2276 | 240
INDQ41 | INDQ11 | 0.1471 | 8.4008 | -0.1719 | 240
INDQ41 | INDQ11 | 0.1302 | 8.3929 | -10.3672 | 240
INDQ41 | INDQ11 | 0.1303 | 7.8698 | -0.4285 | 240
IROA21 | IROA11 | 0.1221 | 8.0467 | -0.0391 | 240
IROA21 | IROA11 | 0.1685 | 7.8148 | -1.385 | 180
IROA21 | IROA11 | 0.1685 | 7.8148 | -1.385 | 180
IROA21 | IROA12 | 0.1685 | 7.8148 | -1.385 | 180
IROA21 | IROA12 | 0.1685 | 7.8148 | -1.385 | 180
IROA21 | IROA13 | 0.1366 | 8.0648 | -0.0471 | 240
IRON41 | IRON11 | 0.1557 | 8.3736 | -0.4146 | 240
IRON41 | IRON12 | 0.1557 | 8.3736 | -0.4146 | 240
IRON41 | IRON13 | 0.1812 | 8.028 | -0.1253 | 240
IVER21 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 240
IVER21 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 240
IVER21 | IVER11 | 0.1221 | 8.0467 | -0.0391 | 240
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 120
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 120
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 120
IVER22 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 240
IVER22 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 120
IVER41 | IVER21 | 0.0326 | 2.3798 | -3.9003 | 500
IVER41 | IVER2A | 0.0326 | 2.3798 | -3.9003 | 595
IVER42 | IVER21 | 0.0176 | 1.5828 | -0.1018 | 1000
IVER42 | IVER22 | 0.0326 | 2.3798 | -3.9003 | 500
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 100
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 100
KEAD41 | KEAD11 | 0.1302 | 8.3929 | -10.3672 | 240
KEAD41 | KEAD11 | 0.1621 | 8.0984 | -0.0747 | 240
KEAD41 | KEAD41 | 0.0002 | 0.4178 | 0 | 2210
KEAD41 | KEAD41 | 0.0002 | 0.2873 | 0 | 2210
KEAD42 | KEAD11 | 0.1118 | 8.3874 | -0.0906 | 240
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 240
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 240
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 240
KEAR21 | KEAR11 | 0.167 | 7.9774 | -0.2092 | 240
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96
KEAR41 | KEAR21 | 0.0175 | 1.5879 | -4.0069 | 1000
KEAR41 | KEAR21 | 0.0117 | 1.591 | -4.4806 | 1000
KEMS4* | KEMS41 | 0.0071 | 0.2875 | 0 | 2750
KEMS4* | KEMS41 | 0.0071 | 0.2875 | 0 | 2750
KEMS41 | KEMS11 | 0.1658 | 8.426 | -0.2939 | 240
KEMS41 | KEMS11 | 0.1139 | 8.1036 | -2.059 | 240
KEMS41 | SHEE11 | 0.1621 | 8.0984 | -0.0747 | 230
KIBY21 | KIBY1* | 0.1392 | 8.4361 | -0.781 | 240
KIBY21 | KIBY12 | 0.1221 | 8.0467 | -0.0391 | 240
KIBY21 | KIBY2* | 0.1221 | 8.0467 | -0.0391 | 240
KIBY22 | KIBY1* | 0.1594 | 8.6081 | -0.2215 | 240
KIBY22 | KIBY12 | 0.1681 | 8.3396 | -1.4878 | 180
KINO41 | KINO11 | 0.1303 | 7.8698 | -0.4285 | 240
KINO41 | KINO11 | 0.1758 | 8.1226 | -0.2746 | 240
KIRK21 | KIRK11 | 0.1411 | 8.6331 | -0.2264 | 240
KIRK21 | KIRK11 | 0.1147 | 8.673 | -0.0358 | 240
KIRK21 | KIRK11 | 0.1366 | 8.0648 | -0.0471 | 240
KIRK2A | KIRK21 | 0.002 | 0.9802 | 0 | 760
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 240
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 240
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 240
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 240
LACK21 | GRTO61 | 0.1747 | 11.0542 | -0.6256 | 120
LACK21 | GRTO61 | 0.1747 | 11.0542 | -0.6256 | 120
LACK21 | LACK61 | 0.4736 | 16.5344 | -0.54 | 120
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 120
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 120
LACK41 | LACK21 | 0.0174 | 1.598 | -0.1503 | 1100
LACK41 | LACK21 | 0.0175 | 1.5879 | -4.0069 | 1000
LACK41 | LACK2A | 0.0152 | 1.6463 | -0.1118 | 1100
LACK41 | LACK2B | 0.0182 | 1.5763 | -0.0904 | 1100
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 240
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 240
LALE21 | LALE11 | 0.196 | 8.3446 | -0.7059 | 180
LALE21 | LALE11 | 0.1954 | 8.0796 | -0.2295 | 180
LAND41 | LAND11 | 0.148 | 7.4973 | -0.3849 | 240
LAND41 | LAND11 | 0.1812 | 8.028 | -0.1253 | 240
LAND42 | LAND11 | 0.1057 | 7.9352 | -0.339 | 240
LEGA41 | LEGA11 | 0.1175 | 8.6648 | -0.4173 | 240
LEGA41 | LEGA11 | 0.1303 | 7.8698 | -0.4285 | 240
LEGA41 | LEGA11 | 0.1812 | 8.028 | -0.1253 | 240
LEGA41 | LEGA11 | 0.1812 | 8.028 | -0.1253 | 240
LEGA41 | LEGA41 | 0.001 | 0.35 | 0 | 2000
LEGA41 | LEGA41 | 0.001 | 0.35 | 0 | 2000
LISD21 | LISD1* | 0.1441 | 8.6238 | -0.2707 | 240
LISD21 | LISD11 | 0.1221 | 8.0467 | -0.0391 | 240
LISD21 | LISD11 | 0.1441 | 8.6238 | -0.2707 | 240
LISD21 | LISD11 | 0.1266 | 8.6449 | -1.9406 | 240
LITT41 | LITT1* | 0.103 | 7.9231 | -0.0638 | 240
LITT41 | LITT11 | 0.1621 | 8.0984 | -0.0747 | 240
LITT41 | LITT11 | 0.0997 | 8.0088 | -0.093 | 240
LITT41 | LITT2A | 0.014 | 2.6567 | -0.1528 | 865
LITT41 | LITT2B | 0.014 | 2.6567 | -0.1528 | 865
LOVE41 | LOVE11 | 0.1303 | 7.8698 | -0.4285 | 240
LOVE41 | LOVE11 | 0.1758 | 8.1226 | -0.2746 | 240
LOVE41 | LOVE12 | 0.1758 | 8.1226 | -0.2746 | 240
LOVE41 | LOVE12 | 0.1847 | 8.1296 | -0.2979 | 240
LOVE41 | LOVE4* | 0.3995 | 7.99 | -0.1549 | 170
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 100
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 100
MACC41 | MACC21 | 0.018 | 1.6146 | -1.5533 | 750
MAGA21 | GRAN61 | 0.1642 | 10.921 | -0.0326 | 180
MAGA21 | GRAN61 | 0.1642 | 10.921 | -0.0326 | 180
MANN41 | MANN11 | 0.1326 | 8.774 | -0.7141 | 240
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 240
MANN41 | MANN11 | 0.1759 | 7.9134 | -0.267 | 240
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 240
MANN41 | MANN11 | 0.1303 | 7.8698 | -0.4285 | 240
MANN41 | MANN4* | 0.3995 | 7.99 | -0.1549 | 170
MANN41 | MANN4* | 0.3995 | 7.99 | -0.1549 | 170
MELK41 | MELK1* | 0.1184 | 8.3643 | -0.0435 | 240
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 240
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 240
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 240
MELK41 | MELK21 | 0.021 | 1.669 | -12.6082 | 750
MELK41 | MELK2A | 0.017 | 1.6132 | -5.1203 | 580
MILH21 | MILH11 | 0.179 | 8.3648 | -4.7616 | 180
MILH21 | MILH12 | 0.1266 | 8.6449 | -1.9406 | 240
MILH22 | MILH11 | 0.1266 | 8.6449 | -1.9406 | 240
MILH22 | MILH12 | 0.179 | 8.3648 | -4.7616 | 180
MITY41 | MITY11 | 0.122 | 8.1963 | -0.2446 | 240
MITY41 | MITY11 | 0.1139 | 8.1036 | -2.059 | 240
MITY41 | MITY12 | 0.137 | 7.9818 | -0.1471 | 240
MITY41 | MITY12 | 0.1057 | 7.9352 | -0.339 | 240
MONF41 | MONF21 | 0.0181 | 1.6409 | -0.1418 | 1100
MONF41 | MONF22 | 0.0181 | 1.6409 | -0.1418 | 1100
MONF4A | MONF21 | 0.0176 | 1.5828 | -0.1018 | 1000
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 240
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 240
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 240
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 240
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 120
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 120
NEEP4A | NEEP21 | 0.021 | 1.669 | -12.6082 | 750
NEWX21 | NEWX11 | 0.1366 | 8.0648 | -0.0471 | 240
NEWX21 | NEWX11 | 0.1366 | 8.0648 | -0.0471 | 240
NEWX21 | NEWX11 | 0.1221 | 8.0467 | -0.0391 | 240
NEWX21 | NEWX2* | 0.7464 | 26.4895 | -0.5477 | 100
NEWX21 | NEWX2* | 0.7464 | 26.4895 | -0.5477 | 100
NEWX21 | NEWX61 | 0.3204 | 14.3298 | -0.2424 | 180
NEWX21 | NEWX61 | 0.2275 | 10.8456 | -0.0697 | 180
NEWX21 | NEWX62 | 0.3061 | 11.0255 | -0.4552 | 180
NEWX21 | NEWX62 | 0.2972 | 12.4333 | -0.1533 | 180
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 240
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 240
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 240
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 240
NHYD2A | NHYD61 | 0.3062 | 11.0235 | -0.4552 | 180
NHYD2B | NHYD61 | 0.3062 | 11.0235 | -0.4552 | 180
NHYD2B | NHYD61 | 0.2364 | 13.3312 | -0.1908 | 180
NINF41 | NINF11 | 0.1658 | 8.4025 | -1.5604 | 240
NINF41 | NINF11 | 0.1303 | 7.8698 | -0.4285 | 240
NINF41 | NINF12 | 0.1658 | 8.4025 | -1.5604 | 240
NINF41 | NINF12 | 0.1509 | 7.9378 | -0.9251 | 240
NINF41 | NINF4* | 0.1941 | 3.8818 | -0.1327 | 150
NORL21 | NORL31 | 0.545 | 19.7925 | -0.1407 | 100
NORL22 | NORL31 | 0.545 | 19.7925 | -0.1407 | 100
NORM41 | NORW1* | 0.1307 | 7.9515 | -0.1098 | 240
NORM41 | NORW11 | 0.1264 | 8.4534 | -0.357 | 240
NORM41 | NORW12 | 0.1509 | 7.9378 | -0.9251 | 240
NORM41 | NORW13 | 0.1118 | 8.3874 | -0.0906 | 240
NORM41 | NORW14 | 0.103 | 7.9231 | -0.0638 | 240
NORT21 | NORT11 | 0.1748 | 8.3565 | -0.2684 | 240
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 240
NORT22 | NORT11 | 0.1748 | 8.3565 | -0.2684 | 240
NORT22 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 240
NORT41 | NORT21 | 0.0186 | 1.5729 | -7.729 | 1000
NORT41 | NORT22 | 0.0117 | 1.591 | -4.4806 | 1000
NURS41 | NURS11 | 0.1471 | 8.4008 | -0.1719 | 240
NURS41 | NURS11 | 0.1471 | 8.4008 | -0.1719 | 240
NURS4A | NURS11 | 0.103 | 7.9231 | -0.0638 | 240
OCKH21 | OCKH1* | 0.179 | 8.3648 | -4.7616 | 180
OCKH21 | OCKH11 | 0.1221 | 8.0467 | -0.0391 | 240
OCKH21 | OCKH11 | 0.1221 | 8.0467 | -0.0391 | 240
OCKH2A | OCKH21 | 0.0104 | 0.867 | -4.0354 | 760
OFFE21 | OFFE31 | 0.5135 | 18.2228 | -0.5477 | 100
OFFE21 | OFFE32 | 0.5135 | 18.2228 | -0.5477 | 100
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 240
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 240
OLDB4A | OLDB21 | 0.0175 | 1.5879 | -4.0069 | 1000
OSBA41 | OSBA1* | 0.103 | 7.9231 | -0.0638 | 240
OSBA41 | OSBA11 | 0.103 | 7.9231 | -0.0638 | 240
OSBA42 | OSBA11 | 0.1812 | 8.028 | -0.1253 | 240
PADI41 | PADI11 | 0.1373 | 8.1976 | -0.1719 | 240
PADI41 | PADI11 | 0.1373 | 8.1976 | -0.1719 | 240
PELH41 | PELH11 | 0.1175 | 8.6648 | -0.4173 | 240
PELH41 | PELH12 | 0.1175 | 8.6648 | -0.4173 | 240
PELH41 | PELH4* | 0.2777 | 9.9961 | -0.1327 | 150
PELH41 | PELH4* | 0.2761 | 10.0362 | -0.0582 | 150
PEMB41 | PEMB11 | 0.1471 | 8.4008 | -0.1719 | 240
PEMB41 | PEMB11 | 0.1658 | 8.4025 | -1.5604 | 240
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 240
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 240
PENN21 | PENN11 | 0.1441 | 8.6238 | -0.2707 | 240
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 240
PENN41 | PENN21 | 0.0132 | 1.6756 | -0.4337 | 1000
PENN42 | PENN21 | 0.0176 | 1.5828 | -0.1018 | 1000
PENT41 | PENT11 | 0.1471 | 8.4008 | -0.1719 | 240
PENT41 | PENT11 | 0.1621 | 8.0984 | -0.0747 | 240
PEWO21 | PENW11 | 0.1594 | 8.6081 | -0.2215 | 240
PEWO22 | PENW11 | 0.1594 | 8.6081 | -0.2215 | 240
PEWO41 | PENE11 | 0.1812 | 8.028 | -0.1253 | 240
PEWO41 | PENE11 | 0.1812 | 8.028 | -0.1253 | 240
PEWO41 | PENE11 | 0.1812 | 8.028 | -0.1253 | 240
PEWO41 | PENW11 | 0.1311 | 7.9055 | -0.1016 | 240
PEWO41 | PEWO21 | 0.021 | 1.669 | -12.6082 | 750
PEWO41 | PEWO21 | 0.0175 | 1.5879 | -4.0069 | 1000
PEWO41 | PEWO22 | 0.0189 | 1.6132 | -0.7226 | 750
PEWO41 | PEWO22 | 0.0178 | 1.5995 | -1.2431 | 750
PEWO41 | PEWO41 | 0.0046 | 0.2858 | -16.2245 | 2750
PEWO41 | PEWO41 | 0.0071 | 0.2875 | -16.2245 | 2750
PITS21 | PITS31 | 0.2998 | 20.1311 | -0.3705 | 120
PITS21 | PITS31 | 0.2998 | 20.1311 | -0.3705 | 120
PITS21 | PITS32 | 0.4975 | 20.4439 | -0.2606 | 100
PITS21 | PITS32 | 0.4975 | 20.4439 | -0.2606 | 100
POPP21 | POPP31 | 0.4905 | 24.145 | -0.1894 | 100
POPP21 | POPP31 | 0.3008 | 25.0399 | -0.1807 | 120
PYLE21 | PYLE11 | 0.2009 | 8.1596 | -0.5003 | 180
PYLE21 | PYLE11 | 0.1366 | 8.0648 | -0.0471 | 240
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 180
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 180
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 180
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 180
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 240
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 240
RATS41 | RATS11 | 0.1373 | 8.1976 | -0.1719 | 240
RATS41 | RATS12 | 0.1759 | 7.9134 | -0.267 | 240
RATS41 | RATS12 | 0.103 | 7.9231 | -0.0638 | 240
RATS42 | RATS11 | 0.1278 | 8.0061 | -0.2276 | 240
RATS42 | RATS2A | 0.0146 | 1.609 | -1.8746 | 1000
RAYL41 | RAYM11 | 0.1303 | 7.8698 | -0.4285 | 240
RAYL41 | RAYM12 | 0.1759 | 7.9134 | -0.267 | 240
RAYL41 | RAYM13 | 0.1759 | 7.9134 | -0.267 | 240
RAYL41 | RAYM14 | 0.1303 | 7.8698 | -0.4285 | 240
REBR21 | REBR32 | 0.665 | 28.1922 | -0.151 | 100
REBR22 | REBR31 | 0.665 | 28.1922 | -0.151 | 100
REBR22 | REBR31 | 0.3375 | 30.6481 | -0.1769 | 120
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 240
ROCH21 | ROCH12 | 0.2847 | 12.2467 | -1.4346 | 120
ROCH4A | ROCH21 | 0.0175 | 1.5879 | -4.0069 | 1100
ROCK41 | ROCK1A | 0.054 | 4.8906 | -0.1253 | 460
RUGE41 | RUGE11 | 0.1139 | 8.1036 | -2.059 | 240
RUGE41 | RUGE11 | 0.1139 | 8.1036 | -2.059 | 240
RYEH4* | RYEH11 | 0.1326 | 8.774 | -0.7141 | 240
RYEH4* | RYEH13 | 0.1326 | 8.774 | -0.7141 | 240
RYEH41 | RYEH12 | 0.1812 | 8.028 | -0.1253 | 240
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 180
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 180
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240
SEAB41 | SEAB11 | 0.1307 | 7.9515 | -0.1098 | 240
SEAB41 | SEAB11 | 0.1303 | 7.8698 | -0.4285 | 240
SEAB41 | SEAB11 | 0.103 | 7.9231 | -0.0638 | 240
SELL41 | SELL1* | 0.0996 | 8.0568 | -1.1981 | 240
SELL41 | SELL11 | 0.103 | 7.9231 | -0.0638 | 240
SELL41 | SELL12 | 0.1621 | 8.0984 | -0.0747 | 240
SELL41 | SELL13 | 0.0996 | 8.0568 | -1.1981 | 240
SELL41 | SELL4* | 0.1941 | 3.8818 | -0.1327 | 150
SELL41 | SELL4* | 0.1941 | 3.8818 | -0.1327 | 150
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 100
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 100
SHRE4B | SHRE11 | 0.1057 | 7.9352 | -0.339 | 240
SIZE41 | SIZE1* | 0.103 | 7.9231 | -0.0638 | 240
SIZE41 | SIZE1* | 0.103 | 7.9231 | -0.0638 | 240
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 240
SIZE41 | SIZE12 | 0.103 | 7.9231 | -0.0638 | 240
SJOW21 | LODR61 | 0.3062 | 11.0235 | -0.4552 | 180
SJOW21 | LODR62 | 0.3062 | 11.0235 | -0.4552 | 180
SJOW21 | SJOW13 | 0.167 | 7.9774 | -0.2092 | 240
SJOW21 | SJOW13 | 0.1441 | 8.6238 | -0.2707 | 240
SJOW21 | SJOW2* | 0.5094 | 10.1873 | -0.0925 | 150
SJOW21 | SJOW2* | 0.5094 | 10.1873 | -0.0925 | 150
SJOW41 | LODR61 | 0.1529 | 12.1324 | -0.0623 | 240
SJOW41 | LODR61 | 0.1529 | 12.1324 | -0.0623 | 240
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW21 | 0.0224 | 2.5703 | -0.5831 | 750
SJOW41 | SJOW21 | 0.0224 | 2.5703 | -0.5831 | 750
SJOW41 | SJOW2A | 0.0224 | 2.5703 | -0.5831 | 750
SJOW41 | SJOW2B | 0.0224 | 2.5703 | -0.5831 | 750
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 240
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 240
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 240
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 240
SMAN21 | SMAN11 | 0.1441 | 8.6238 | -0.2707 | 240
SMAN21 | SMAN11 | 0.1052 | 8.2077 | -0.6621 | 240
SMAN21 | SMAN12 | 0.1441 | 8.6238 | -0.2707 | 240
SMAN21 | SMAN12 | 0.1221 | 8.0467 | -0.0391 | 240
SPEN41 | SPEN1* | 0.1264 | 8.4534 | -0.357 | 240
SPEN41 | SPEN11 | 0.1264 | 8.4534 | -0.357 | 240
SPEN42 | SPEN11 | 0.1264 | 8.4534 | -0.357 | 240
SSHI21 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 100
SSHI21 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 100
STAH4A | STAH11 | 0.122 | 8.1963 | -0.2446 | 240
STAH4B | STAH11 | 0.1046 | 7.8493 | -0.0881 | 240
STAL21 | STAL11 | 0.1221 | 8.0467 | -0.0391 | 240
STAL21 | STAL12 | 0.1681 | 8.3396 | -1.4878 | 180
STAL21 | STAL12 | 0.1681 | 8.3396 | -1.4878 | 180
STAL21 | STAL13 | 0.1954 | 8.0796 | -0.2295 | 180
STAL42 | STAL21 | 0.0146 | 1.609 | -1.8746 | 1000
STAY41 | STYC11 | 0.103 | 7.9231 | -0.0638 | 240
STAY41 | STYC12 | 0.1046 | 7.8493 | -0.0881 | 240
STAY4A | STAY41 | 0.0002 | 0.4178 | -13.831 | 2150
STEW21 | STEN11 | 0.3392 | 11.9012 | -0.7294 | 120
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 120
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 120
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 120
STEW21 | STES11 | 0.1366 | 8.0648 | -0.0471 | 240
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 120
STEW41 | STEW21 | 0.0107 | 1.5596 | -0.0734 | 1000
STEW41 | STEW21 | 0.0211 | 1.6463 | -14.2471 | 1000
STOB41 | STOB11 | 0.1307 | 7.9515 | -0.1098 | 240
STOB41 | STOB11 | 0.1307 | 7.9515 | -0.1098 | 240
STSB4A | STSB41 | 0.0003 | 0.1825 | 0 | 2000
SUND41 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 240
SUND41 | SUND11 | 0.1303 | 7.8698 | -0.4285 | 240
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 240
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 240
SWAN21 | SWAN1* | 0.1646 | 8.0383 | -0.1808 | 180
SWAN21 | SWAN11 | 0.1923 | 8.2361 | -0.4425 | 180
SWAN4* | SWAN12 | 0.1307 | 7.9515 | -0.1098 | 240
SWAN41 | SWAN11 | 0.1303 | 7.8698 | -0.4285 | 240
SWAN41 | SWAN12 | 0.1303 | 7.8698 | -0.4285 | 240
SWAN41 | SWAN4* | 0.0182 | 1.5763 | -0.0904 | 1100
SWAN4A | SWAN21 | 0.0178 | 1.5995 | -1.2431 | 750
TAUN42 | TAUN11 | 0.1759 | 7.9134 | -0.267 | 240
TEMP21 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 75
TEMP22 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 75
THOM41 | THOM4* | 0.0152 | 1.6463 | -0.1118 | 1100
THOM41 | THOM61 | 0.1844 | 13.1765 | -0.0474 | 180
THOM41 | THOM61 | 0.1844 | 13.1765 | -0.0474 | 180
THOM42 | THOM21 | 0.0185 | 1.614 | -0.5638 | 750
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 180
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 180
THUR21 | THUR61 | 0.1699 | 10.8431 | -0.0403 | 180
TILB21 | TILB11 | 0.3792 | 12.0524 | -0.3982 | 120
TILB22 | TILB12 | 0.3792 | 12.0524 | -0.3982 | 120
TILB41 | TILB1* | 0.1307 | 7.9515 | -0.1098 | 240
TILB41 | TILB14 | 0.1303 | 7.8698 | -0.4285 | 240
TILB4A | TILB22 | 0.0211 | 1.6463 | -14.2471 | 750
TILB4B | TILB21 | 0.0117 | 1.591 | -4.4806 | 1000
TINP21 | TINP31 | 0.4758 | 20.0944 | -0.4489 | 100
TINP21 | TINP32 | 0.5083 | 24.0899 | -0.1921 | 120
TINP22 | TINP31 | 0.4758 | 20.0944 | -0.4489 | 100
TINP22 | TINP32 | 0.5083 | 24.0899 | -0.1921 | 120
TODP21 | TODP61 | 0.459 | 16.6187 | -0.1963 | 101
TODP21 | TODP61 | 0.3931 | 16.4953 | -2.1281 | 120
TOTT21 | TOTT11 | 0.1688 | 8.3316 | -1.1711 | 240
TOTT22 | TOTT11 | 0.179 | 8.3648 | -4.7616 | 180
TOTT23 | TOTT12 | 0.1266 | 8.6449 | -1.9406 | 240
TOTT24 | TOTT12 | 0.1266 | 8.6449 | -1.9406 | 240
TRAW21 | TRAW11 | 0.2847 | 12.2467 | -1.4346 | 120
TRAW21 | TRAW11 | 0.2847 | 12.2467 | -1.4346 | 120
TRAW41 | TRAW21 | 0.0132 | 1.6756 | -0.4337 | 965
TRAW41 | TRAW21 | 0.021 | 1.669 | -12.6082 | 750
TREM21 | TREM31 | 0.593 | 20.7915 | -0.122 | 100
TREM21 | TREM31 | 0.4636 | 17.894 | -0.1238 | 120
TYNE21 | TYNE11 | 0.1411 | 8.6331 | -0.2264 | 240
TYNE21 | TYNE11 | 0.1221 | 8.0467 | -0.0391 | 240
TYNE21 | TYNE51 | 1.2306 | 53.1493 | -0.0143 | 40
TYNE2A | TYNE51 | 1.2306 | 53.1493 | -0.0143 | 40
UPPB21 | UPPB11 | 0.0979 | 8.4415 | -0.018 | 222
UPPB21 | UPPB11 | 0.0979 | 8.4415 | -0.018 | 240
UPPB22 | UPPB31 | 0.4636 | 17.894 | -0.1238 | 100
UPPB22 | UPPB31 | 0.5107 | 17.9527 | -0.2251 | 100
USKM21 | ALST31 | 0.5135 | 18.2228 | -0.5477 | 100
USKM21 | ALST32 | 0.5107 | 17.9527 | -0.2251 | 100
USKM21 | USKM1* | 0.1221 | 8.0467 | -0.0391 | 240
USKM21 | USKM11 | 0.1221 | 8.0467 | -0.0391 | 240
USKM21 | USKM12 | 0.1221 | 8.0467 | -0.0391 | 240
WALH41 | PORH11 | 0.1326 | 8.774 | -0.7141 | 240
WALH41 | PORH11 | 0.1471 | 8.4008 | -0.1719 | 240
WALH41 | PORH11 | 0.1812 | 8.028 | -0.1253 | 240
WALH41 | PORH11 | 0.103 | 7.9231 | -0.0638 | 240
WALP41 | WALP11 | 0.1621 | 8.0984 | -0.0747 | 240
WALP41 | WALP11 | 0.1175 | 8.6648 | -0.4173 | 240
WALP41 | WALP11 | 0.1175 | 8.6648 | -0.4173 | 240
WALP41 | WALP11 | 0.1509 | 8.2849 | -0.3279 | 240
WALP41 | WALP11 | 0.1303 | 7.8698 | -0.4285 | 240
WALX41 | WALX21 | 0.0176 | 1.5828 | -0.1018 | 1000
WALX41 | WALX22 | 0.0176 | 1.5828 | -0.1018 | 1000
WALX42 | WALX21 | 0.0176 | 1.5828 | -0.1018 | 1000
WALX42 | WALX22 | 0.0176 | 1.5828 | -0.1018 | 1000
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 240
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 240
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 240
WASF21 | WASF11 | 0.197 | 7.9698 | -0.2553 | 180
WASF22 | WASF12 | 0.197 | 7.9698 | -0.2553 | 180
WATS21 | WATS11 | 0.1382 | 8.1742 | -0.1786 | 240
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 120
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 120
WATS22 | WATS11 | 0.1392 | 8.4361 | -0.781 | 240
WATS22 | WATS11 | 0.1923 | 8.081 | -1.4418 | 180
WBOL21 | WBOL61 | 0.4736 | 16.5344 | -0.54 | 120
WBOL21 | WBOL61 | 0.1809 | 10.9763 | -0.023 | 180
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 120
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 120
WBUR42 | WBUR11 | 0.1175 | 8.6648 | -0.4173 | 240
WBUR42 | WBUR12 | 0.1175 | 8.6648 | -0.4173 | 240
WHAM41 | WHAM11 | 0.103 | 7.9231 | -0.0638 | 240
WHAM41 | WHAM11 | 0.103 | 7.9231 | -0.0638 | 240
WHAM41 | WHAM12 | 0.1057 | 7.9352 | -0.339 | 240
WHAM41 | WHAM12 | 0.103 | 7.9231 | -0.0638 | 240
WHAM4A | WHAM41 | 0.001 | 0.35 | 0 | 1410
WHAM4B | WHAM41 | 0.001 | 0.35 | 0 | 1410
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 240
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 240
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 240
WHSO21 | WHSO2A | 0.005 | 0.463 | 0 | 750
WHSO21 | WHSO31 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO21 | WHSO31 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO21 | WHSO31 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO22 | WHSO2B | 0.005 | 0.463 | 0 | 750
WHSO22 | WHSO31 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO41 | WHSO22 | 0.0185 | 1.614 | -0.5638 | 750
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 100
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 100
WIEN2* | WIEN11 | 0.1594 | 8.6081 | -0.2215 | 240
WIEN21 | WIEN11 | 0.1366 | 8.0648 | -0.0471 | 240
WILE41 | WILE4* | 0.3995 | 7.99 | -0.1549 | 170
WILE41 | WILL11 | 0.1303 | 7.8698 | -0.4285 | 240
WILE41 | WILL11 | 0.1046 | 7.8493 | -0.0881 | 240
WILE41 | WILL12 | 0.1035 | 8.3458 | -0.0962 | 240
WILE41 | WILL21 | 0.0268 | 2.7989 | -0.3188 | 685
WILL21 | WILL11 | 0.2847 | 12.2467 | -1.4346 | 120
WILL21 | WILL12 | 0.2847 | 12.2467 | -1.4346 | 120
WILT2A | GRST61 | 0.3151 | 12.4456 | -0.1391 | 180
WILT2B | GRST61 | 0.3151 | 12.4456 | -0.1391 | 180
WILT2C | GRST61 | 0.2275 | 10.8456 | -0.0697 | 180
WILT2D | GRST61 | 0.2972 | 12.4333 | -0.1533 | 180
WIMB21 | WIMB1* | 0.179 | 8.3648 | -4.7616 | 180
WIMB21 | WIMB11 | 0.167 | 7.9774 | -0.2092 | 240
WIMB21 | WIMB11 | 0.1923 | 8.081 | -1.4418 | 180
WIMB21 | WIMB11 | 0.1845 | 7.8956 | -0.1938 | 240
WIMB21 | WIMB12 | 0.1845 | 7.8956 | -0.1938 | 240
WIMB21 | WIMB12 | 0.167 | 7.9774 | -0.2092 | 240
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 240
WISD21 | WISD11 | 0.1845 | 7.8956 | -0.1938 | 240
WISD21 | WISD2B | 0.0066 | 0.6494 | -1.5179 | 740
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 180
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 180
WISD22 | WISD11 | 0.167 | 7.9774 | -0.2092 | 240
WISD22 | WISD2A | 0.002 | 0.6673 | 0 | 750
WISD22 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 180
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 120
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 120
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 120
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 120
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 180
WMEL21 | WMEL12 | 0.1923 | 8.2361 | -0.4425 | 180
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 180
WTHU4* | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100
WTHU4A | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100
WWEY21 | WWEY1* | 0.1954 | 8.0796 | -0.2295 | 180
WWEY21 | WWEY11 | 0.1382 | 8.4614 | -0.1786 | 240
WWEY22 | WWEY11 | 0.1954 | 8.0796 | -0.2295 | 180
WWEY22 | WWEY12 | 0.1382 | 8.4489 | -0.1786 | 240
WWEY41 | WWEY21 | 0.017 | 1.6132 | -5.1203 | 750
WWEY41 | WWEY22 | 0.0185 | 1.614 | -0.5638 | 750
WWEY42 | WWEY2* | 0.0178 | 1.5995 | -1.2431 | 750
WWEY42 | WWEY21 | 0.0178 | 1.5995 | -1.2431 | 750
WYLF41 | WYLF1* | 0.1509 | 8.2849 | -0.3279 | 240
WYLF41 | WYLF11 | 0.1368 | 8.5406 | -0.262 | 238
WYLF41 | WYLF11 | 0.1368 | 8.5406 | -0.262 | 238
WYLF41 | WYLF11 | 0.1229 | 8.3873 | -0.1147 | 240
WYMO41 | WYMO11 | 0.1509 | 8.2849 | -0.3279 | 240
WYMO41 | WYMO11 | 0.1303 | 7.8698 | -0.4285 | 240

## B-3-1d
Table B.3.1c - OFTO Transformers 2014/15 | [7 empty] | Back To Menu
OFTO | Node 1 | Node 2 | Voltage Ratio (kV) | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA)
- | BODE41 | GWYN1* | 400/132 | 0.0595 | 4.1662 | -1.1739 | 420
- | BODE41 | GWYN1* | 400/132 | 0.0595 | 4.1662 | -1.1739 | 420
TC Barrow OFTO Ltd | BOSW1* | BOSW3* | 132/33 | 0.0167 | 10 | 0 | 90
- | BURB1* | BURB1* | 132/33 | 0.3443 | 13.8513 | 0 | 90
- | CLEH41 | LONO1* | 400/150 | 0.185 | 6.6641 | 0 | 180
- | CLEH41 | LONO1* | 400/150 | 0.185 | 6.6641 | 0 | 180
- | CLEH41 | LONO1* | 400/150 | 0.185 | 6.6641 | 0 | 180
- | CLEH41 | LONO1* | 400/150 | 0.185 | 6.6641 | 0 | 180
- | GGON1* | GGON1* | 132/13.9 | 0.0241 | 11 | 0 | 90
- | GGON1* | GGON1* | 132/13.9 | 0.0241 | 11 | 0 | 90
- | GGON1* | GGON1* | 132/13.9 | 0.0241 | 11 | 0 | 90
TC Gunfleet Sands OFTO Ltd | GUNS1* | GUNS3* | 132/33 | 0.0002 | 8.575 | 0 | 120
TC Gunfleet Sands OFTO Ltd | GUNS1* | GUNS3* | 132/33 | 0.0002 | 8.575 | 0 | 120
- | GWYN1* | GWYN1* | 132/33 | 0.25 | 11.2472 | 0 | 160
- | GWYN1* | GWYN1* | 132/33 | 0.25 | 11.2472 | 0 | 160
- | GWYN1* | GWYN1* | 132/33 | 0.25 | 11.2472 | 0 | 160
- | GWYN1* | GWYN1* | 132/33 | 0.25 | 11.2472 | 0 | 160
- | GWYN1* | GWYN1* | 132/33 | 0.234 | 10.9975 | -0.1289 | 90
- | GWYN1* | GWYN1* | 132/33 | 0.25 | 11.2472 | 0 | 160
- | GWYN1* | GWYN1* | 132/33 | 0.25 | 11.2472 | 0 | 160
- | HEDO21 | HEDN1* | 275/150 | 0.133 | 8.0758 | -0.2287 | 260
- | HEDO21 | HEDN1* | 275/150 | 0.133 | 8.0758 | -0.2287 | 260
- | HEYS41 | WODS1* | 400/155 | 0.2083 | 4.9957 | 0 | 240
- | HEYS41 | WODS1* | 400/155 | 0.2083 | 4.9957 | 0 | 240
- | HUMG8* | HUMG8* | 132/33 | 0.25 | 11.8724 | 0 | 160
- | HUMG8* | HUMG8* | 132/33 | 0.25 | 11.8724 | 0 | 160
- | HUMG8* | HUMG8* | 275/132 | 0.1052 | 8.2077 | -0.6621 | 240
- | HUMG8* | HUMG8* | 275/132 | 0.1052 | 8.2077 | -0.6621 | 240
- | IGOF1* | IGOF1* | 132/33 | 0.2173 | 23.4434 | 0 | 180
- | IGOF1* | IGOF1* | 132/33 | 0.2173 | 23.4434 | 0 | 180
- | IGOF1* | IGOF1* | 132/33 | 0.2173 | 23.4434 | 0 | 180
- | IGOF1* | IGOF1* | 132/33 | 0.03 | 25.9222 | 0 | 90
- | IGOF1* | IGOF1* | 132/33 | 0.0611 | 25.9221 | 0 | 90
- | LINS4* | LINS1* | 400/132 | 0.0367 | 4.6665 | 0 | 300
- | LINS4* | LINS1* | 400/132 | 0.0367 | 4.6665 | 0 | 300
- | LOAW1* | LOAW3* | 150/33 | 0 | 6.6667 | 0 | 180
- | LOAW1* | LOAW3* | 150/33 | 0 | 6.6667 | 0 | 180
- | LOAW1* | LOAW3* | 150/33 | 0 | 6.6667 | 0 | 180
- | LOAW1* | LOAW3* | 150/33 | 0 | 6.6667 | 0 | 180
TC Ormonde OFTO Ltd | ORMO8* | ORMO8* | 132/33 | 0.7206 | 14.6882 | 0 | 85
TC Ormonde OFTO Ltd | ORMO8* | ORMO8* | 132/33 | 0.7206 | 14.6882 | 0 | 85
TC Robin Rigg OFTO Ltd | RREW1* | RREW3* | 132/33 | 0 | 15.7895 | 0 | 95
TC Robin Rigg OFTO Ltd | RRWW1* | RRWW3* | 132/33 | 0 | 15.7895 | 0 | 95
- | SHSW1* | SHSW3* | 132/33 | 0.4259 | 13.3265 | 0 | 90
- | SHSW1* | SHSW3* | 132/33 | 0.4259 | 13.3265 | 0 | 90
- | SHSW1* | SHSW3* | 132/33 | 0.4259 | 13.3265 | 0 | 90
- | SHSW1* | SHSW3* | 132/33 | 0.4259 | 13.3265 | 0 | 90
Blue Transmission Walney 2 | STAH11 | WABW8* | 132/33 | 0.2083 | 4.9957 | 0 | 240
Blue Transmission Walney 1 | WAAW8* | WAAW8* | 132/33 | 0.2083 | 4.3746 | 0 | 240
- | WERW8* | WERW8* | 150/33 | 1.3333 | 13.2665 | -0.2263 | 120
- | WERW8* | WERW8* | 150/33 | 1.3333 | 13.2665 | -0.2263 | 120
- | WODS1* | WODS3* | 155/33 | 0.0208 | 5 | 0 | 240
- | WODS1* | WODS3* | 155/33 | 0.0208 | 5 | 0 | 240

## B-3-2a
Table B.3.2a - SHE Transmission Transformer Changes 2015/16 to 2023/24 | [7 empty] | Back To Menu
Node 1 | Node 2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
ACHR1R | ACHR3- | 2015 | Addition | 0.5 | 25 | 0 | 90
BRAC2J | BRAC3- | 2015 | Addition | 0.42 | 20 | 0 | 120
BRAC2K | BRAC3- | 2015 | Addition | 0.42 | 20 | 0 | 120
CLAS2- | CLAS3J | 2015 | Addition | 0.42 | 20 | 0 | 120
CRSS1J | CRSS1Q | 2015 | Addition | 0.073 | 1.875 | 0 | 240
CRSS1K | CRSS1R | 2015 | Addition | 0.073 | 1.875 | 0 | 240
CRSS2A | CRSS1J | 2015 | Addition | 0.3422 | 8.8892 | -0.0359 | 240
CRSS2B | CRSS1K | 2015 | Addition | 0.3422 | 8.8892 | -0.0359 | 240
FAUG4- | FAUG1- | 2015 | Addition | 0.2149 | 8.1378 | -0.013 | 240
STRW12 | STRW31 | 2015 | Addition | 0.05 | 18 | 0 | 90
STRW20 | STRW11 | 2015 | Addition | 0.0662 | 5.3329 | -0.0004 | 360
THSO1Q | THSO3- | 2015 | Change | 0.3837 | 24.98 | 0 | 120
THSO1R | THSO3- | 2015 | Change | 0.3837 | 24.98 | 0 | 120
BRAC1Q | BRAC3- | 2015 | Removed | 0.9 | 27.85 | 0 | 60
BRAC1R | BRAC3- | 2015 | Removed | 0.9 | 27.6 | 0 | 60
CORI1J | CORI3J | 2016 | Addition | 8.3 | 27.5001 | 0 | 60
GRUB1Q | GRUB3- | 2016 | Addition | 0.499 | 24.995 | 0 | 90
GRUB1R | GRUB3- | 2016 | Addition | 0.499 | 24.995 | 0 | 90
RANN1Q | RANN3Q | 2016 | Addition | 0.499 | 24.995 | 0 | 90
RANN1R | RANN3Q | 2016 | Addition | 0.499 | 24.995 | 0 | 90
STRW13 | STRW33 | 2016 | Addition | 0.5 | 25 | 0 | 90
STRW13 | STRW34 | 2016 | Addition | 0.5 | 25 | 0 | 90
BLHI2A | BLHI2J | 2017 | Addition | 0.005 | 0.4 | 0 | 1000
BLHI2B | BLHI2K | 2017 | Addition | 0.005 | 0.4 | 0 | 1000
BLHI2J | BLHI1J | 2017 | Addition | 0.3328 | 8.9105 | -0.038 | 240
BLHI2K | BLHI1K | 2017 | Addition | 0.3328 | 8.9105 | -0.038 | 240
BLHI4- | BLHI2J | 2017 | Addition | 0.018 | 1.576 | -0.09 | 1200
BLHI4- | BLHI2K | 2017 | Addition | 0.018 | 1.576 | -0.09 | 1200
CRSS1J | CRSS31 | 2017 | Addition | 0.817 | 27.121 | 0 | 45
DUDH1Q | DUDH3- | 2017 | Change | 0.499 | 24.995 | 0 | 90
DUDH1R | DUDH3- | 2017 | Change | 0.499 | 24.995 | 0 | 90
DUNM1- | DUNM3- | 2017 | Addition | 0.172 | 17.9 | 0 | 120
FARI2K | FARI1K | 2017 | Addition | 0.6786 | 12.1895 | -0.0009 | 120
FYRI2J | FYRI1J | 2017 | Addition | 0.3422 | 8.889 | -0.0359 | 240
FYRI2K | FYRI1K | 2017 | Addition | 0.3423 | 8.889 | -0.0359 | 240
LOCB2J | LOCB1J | 2017 | Addition | 0.3422 | 8.889 | -0.0359 | 240
LOCB2K | LOCB1K | 2017 | Addition | 0.3423 | 8.889 | -0.0359 | 240
TUMB1Q | TUMB3- | 2017 | Addition | 0.499 | 24.995 | 0 | 45
TUMB1R | TUMB3- | 2017 | Addition | 0.499 | 24.995 | 0 | 45
ALLT1Q | ALLT3- | 2018 | Addition | 0.36 | 18 | 0 | 120
BASK1A | BASK3A | 2018 | Addition | 0.174 | 16.667 | 0 | 120
BASK1A | BASK3A | 2018 | Addition | 0.174 | 16.667 | 0 | 120
BASK1A | BASK3B | 2018 | Addition | 0.174 | 16.667 | 0 | 120
BASK1A | BASK3B | 2018 | Addition | 0.174 | 16.667 | 0 | 120
BASK2A | BASK1A | 2018 | Addition | 0.3422 | 8.8892 | -0.0359 | 240
CAAD1Q | CAAD3- | 2018 | Change | 0.499 | 24.995 | 0 | 120
CAAD1R | CAAD3- | 2018 | Change | 0.499 | 24.995 | 0 | 120
CRSS1J | COUW31 | 2018 | Addition | 0.817 | 27.121 | 0 | 45
DORE11 | DORE31 | 2018 | Addition | 0.36 | 17.99 | 0 | 120
DORE12 | DORE32 | 2018 | Addition | 0.36 | 17.99 | 0 | 120
DOUN2- | DOUN2A | 2018 | Addition | 0.3422 | 8.8892 | -0.0359 | 240
FYRI1J | FYRI3J | 2018 | Addition | 0.36 | 18 | 0 | 120
FYRI1K | FYRI3J | 2018 | Addition | 0.36 | 18 | 0 | 120
GILB1J | GILB3J | 2018 | Addition | 0.3599 | 17.9964 | 0 | 120
GILB1K | GILB3J | 2018 | Addition | 0.3599 | 17.9964 | 0 | 120
MEYG1- | MEYG3A | 2018 | Addition | 0.36 | 18 | 0 | 42
MILS1Q | MILS3J | 2018 | Addition | 0.36 | 18.0001 | 0 | 60
MYBS1S | MYBS3M | 2018 | Addition | 0.5 | 25 | 0 | 120
MYBS1T | MYBS3N | 2018 | Addition | 0.5 | 25 | 0 | 120
SALA1- | SALA3- | 2018 | Addition | 0.36 | 17.99 | 0 | 90
SPIT2J | SPIT1J | 2018 | Addition | 0.3423 | 8.8892 | -0.036 | 240
SPIT2J | SPIT1J | 2018 | Addition | 0.3423 | 8.8892 | -0.036 | 240
SPIT2J | SPIT3Y | 2018 | Addition | 0.36 | 18 | 0 | 120
SPIT2K | SPIT1K | 2018 | Addition | 0.3423 | 8.8892 | -0.036 | 240
SPIT2K | SPIT1K | 2018 | Addition | 0.3423 | 8.8892 | -0.036 | 240
THSO1J | THSO3- | 2018 | Addition | 0.3837 | 24.98 | 0 | 120
THSO1K | THSO3- | 2018 | Addition | 0.3837 | 24.98 | 0 | 120
THSO2J | THSO1J | 2018 | Addition | 0.3423 | 8.889 | -0.036 | 240
THSO2J | THSO1J | 2018 | Addition | 0.3423 | 8.889 | -0.036 | 240
THSO2K | THSO1K | 2018 | Addition | 0.3423 | 8.889 | -0.036 | 240
THSO2K | THSO1K | 2018 | Addition | 0.3423 | 8.889 | -0.036 | 240
TOMT2J | TOMT1J | 2018 | Addition | 0.3423 | 8.8892 | -0.036 | 240
TOMT2J | TOMT1J | 2018 | Addition | 0.3423 | 8.8892 | -0.036 | 240
TOMT2K | TOMT1K | 2018 | Addition | 0.3423 | 8.8892 | -0.036 | 240
TOMT2K | TOMT1K | 2018 | Addition | 0.3423 | 8.8892 | -0.036 | 240
WIOW1Q | WIOW3- | 2018 | Change | 0.499 | 24.995 | 0 | 90
WIOW1R | WIOW3- | 2018 | Change | 0.499 | 24.995 | 0 | 90
CRSS1J | CRSS31 | 2018 | Removed | 0.817 | 27.121 | 0 | 45
THSO1Q | THSO3- | 2018 | Removed | 0.3837 | 24.98 | 0 | 120
THSO1R | THSO3- | 2018 | Removed | 0.3837 | 24.98 | 0 | 120
ALYT4- | ALYT2Q | 2020 | Addition | 0.017 | 1.588 | -4.007 | 1000
ALYT4- | ALYT2R | 2020 | Addition | 0.017 | 1.588 | -4.007 | 1000
AULW1S | AULW3- | 2020 | Addition | 0.5 | 25 | 0 | 90
BEAU2J | BEAU1W | 2020 | Addition | 0.3423 | 8.8892 | -0.036 | 480
BEAU2K | BEAU1X | 2020 | Addition | 0.3423 | 8.8892 | -0.036 | 480
BLHI2J | BLHI1K | 2020 | Addition | 0.3423 | 8.8892 | -0.036 | 360
BLHI2J | BLHI1K | 2020 | Addition | 0.3423 | 8.8892 | -0.036 | 360
BLHI2K | BLHI1J | 2020 | Addition | 0.3423 | 8.8892 | -0.036 | 360
BLHI2K | BLHI1J | 2020 | Addition | 0.3423 | 8.8892 | -0.036 | 360
COGA1- | COGA3- | 2020 | Addition | 0.324 | 17.9 | 0 | 90
CROB2- | CROB3J | 2020 | Addition | 0.36 | 18 | 0 | 120
DALN1R | DALN3- | 2020 | Addition | 0.36 | 18 | 0 | 90
DUGR1J | DUGR3- | 2020 | Addition | 0.7 | 21 | 0 | 60
FARI2J | FARI1J | 2020 | Addition | 0.6786 | 12.1895 | -0.0009 | 120
FAUG2J | FAUG1- | 2020 | Addition | 0.2629 | 7.7038 | -0.0005 | 240
FAUG2K | FAUG1- | 2020 | Addition | 0.2629 | 7.7038 | -0.0005 | 240
FAUG4J | FAUG1- | 2020 | Addition | 0.2149 | 8.0138 | -0.013 | 240
FAUG4J | FAUG1J | 2020 | Addition | 0.131 | 7.952 | -0.11 | 240
FAUG4J | FAUG1J | 2020 | Addition | 0.131 | 7.952 | -0.11 | 240
FAUG4J | FAUG2J | 2020 | Addition | 0.018 | 1.576 | -0.09 | 1200
FAUG4K | FAUG1- | 2020 | Addition | 0.2149 | 8.1378 | -0.013 | 240
FAUG4K | FAUG1K | 2020 | Addition | 0.131 | 7.952 | -0.11 | 240
FAUG4K | FAUG1K | 2020 | Addition | 0.131 | 7.952 | -0.11 | 240
FAUG4K | FAUG2K | 2020 | Addition | 0.018 | 1.576 | -0.09 | 1200
FETT4Q | FETT1R | 2020 | Addition | 0.131 | 7.952 | -0.11 | 240
FETT4R | FETT1- | 2020 | Addition | 0.131 | 7.952 | -0.11 | 240
FIDD1S | FIDD3- | 2020 | Addition | 0.4562 | 26.084 | 0 | 90
GLKY1- | GLKY3J | 2020 | Addition | 0.36 | 18.0001 | 0 | 60
KINT4- | KINT2J | 2020 | Addition | 0.017 | 1.588 | -4.007 | 1000
KINT4- | KINT2K | 2020 | Addition | 0.017 | 1.588 | -4.007 | 1000
LAIR2K | LAIR1K | 2020 | Addition | 0.0662 | 5.3329 | -0.0004 | 360
LAIR2Q | LAIR1Q | 2020 | Addition | 0.0662 | 5.3329 | -0.0004 | 360
PEHE4- | PEHE2Q | 2020 | Addition | 0.018 | 1.576 | -0.09 | 1200
PEHE4- | PEHERSV1 | 2020 | Addition | 0.018 | 1.576 | -0.09 | 1200
TOMN1J | TOMN3J | 2020 | Addition | 0.36 | 18 | 0 | 90
FIDD1R | FIDD3- | 2020 | Removed | 0.4562 | 26.084 | 0 | 90
DUGR1Q | DUGR3- | 2020 | Removed | 0.7 | 21 | 0 | 60
FETT2R | FETT1- | 2020 | Removed | 0.2217 | 4.3026 | -0.0071 | 240
BLHI2K | BLHI1K | 2020 | Removed | 0.3328 | 8.9105 | -0.038 | 240
FAUG4- | FAUG1- | 2020 | Removed | 0.2149 | 8.0138 | -0.013 | 240
FAUG4- | FAUG1- | 2020 | Removed | 0.2149 | 8.1378 | -0.013 | 240
FAUG2- | FAUG1- | 2020 | Removed | 0.2629 | 7.7038 | -0.0005 | 240
BEAU2J | BEAU1J | 2020 | Removed | 0.6786 | 12.2312 | -0.0009 | 120
FAUG2- | FAUG1- | 2020 | Removed | 0.2629 | 7.7038 | -0.0005 | 240
BLHI2J | BLHI1J | 2020 | Removed | 0.3328 | 8.9105 | -0.038 | 240
BEIN1- | BEIN3- | 2023 | Addition | 0.36 | 18 | 0 | 120
BHLA1- | BHLA3- | 2023 | Addition | 0.36 | 18 | 0 | 120
GLEM16 | GLEM36 | 2023 | Addition | 0.36 | 17.99 | 0 | 120
INGA4J | INGA1K | 2023 | Addition | 0.131 | 7.952 | -0.11 | 240
INGA4K | INGA1J | 2023 | Addition | 0.131 | 7.952 | -0.11 | 240
LIME1- | LIME3- | 2023 | Addition | 0.36 | 18 | 0 | 120
MYBS1Q | MYBS3J | 2023 | Change | 0.5 | 25 | 0 | 120
MYBS1R | MYBS3J | 2023 | Change | 0.5 | 25 | 0 | 120
SHIN2J | SHIN1- | 2023 | Addition | 0.6786 | 12.1895 | -0.0009 | 120
SHIN2K | SHIN1- | 2023 | Addition | 0.6786 | 12.1895 | -0.0009 | 120
STRL1- | STRL3P | 2023 | Addition | 0.36 | 18 | 0 | 90
STRL1- | STRL3P | 2023 | Addition | 0.36 | 18 | 0 | 90
STRL1- | STRL3Q | 2023 | Addition | 0.36 | 18 | 0 | 90
STRL1- | STRL3Q | 2023 | Addition | 0.36 | 18 | 0 | 90
STRL4J | STRL1J | 2023 | Addition | 0.131 | 7.952 | -0.11 | 240
STRL4J | STRL1J | 2023 | Addition | 0.131 | 7.952 | -0.11 | 240
STRW2Q | STRW31_1 | 2023 | Addition | 0.36 | 18 | 0 | 120
BEAU1K | BEAU1Q | 2023 | Removed | 0.177 | 3.6 | 0 | 150
BEAU1J | BEAU1P | 2023 | Removed | 0.177 | 3.6 | 0 | 150

## B-3-2b
Table B.3.2b - SPT Transformer Changes 2015/16 to 2023/24 | [7 empty] | Back To Menu
Node1 | Node2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
BLKX1- | BLKX3- | 2015 | Addition | 0.3635 | 25.4418 | 0 | 90
BONN1- | BONN3- | 2015 | Change | 0.3635 | 25.4418 | 0 | 90
BONN1- | BONN3- | 2015 | Change | 0.3635 | 25.4418 | 0 | 90
BONN2A | BONN1- | 2015 | Addition | 0.1559 | 8.9445 | -0.1694 | 240
BONN2B | BONN1- | 2015 | Addition | 0.1559 | 8.9445 | -0.1694 | 240
DALM1- | DALM3- | 2015 | Change | 0.469 | 27.3326 | 0 | 90
DENN4- | DENN2- | 2015 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
EWEH1Q | EWEH3- | 2015 | Addition | 0.1984 | 16.6655 | 0 | 90
FALL4- | FALL3A | 2015 | Addition | 0.2564 | 16.6647 | 0 | 120
FALL4- | FALL3B | 2015 | Addition | 0.2564 | 16.6647 | 0 | 120
GALA1- | GALA3- | 2015 | Change | 0.3635 | 25.4418 | 0 | 90
HUNE4- | HUNE2A | 2015 | Addition | 0.0557 | 2.9161 | 0 | 240
HUNE4- | HUNE2B | 2015 | Addition | 0.0557 | 2.9161 | 0 | 240
KAIM2- | KAIM3A | 2015 | Addition | 0.4819 | 20.2443 | -0.2454 | 120
KAIM2- | KAIM3B | 2015 | Addition | 0.4944 | 20.244 | -0.245 | 120
NECU2- | NECU1- | 2015 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
NECU2- | NECU1- | 2015 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
NECU2- | NECU1- | 2015 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
NETS1- | NETS3- | 2015 | Change | 0.8311 | 28.2878 | -0.0097 | 60
POOB2R | POOB3- | 2015 | Change | 0.3244 | 20.4558 | -0.0158 | 120
SIGH2Q | SIGH3A | 2015 | Addition | 0.4536 | 27.274 | 0 | 180
SIGH2R | SIGH3A | 2015 | Addition | 0.4536 | 27.274 | 0 | 180
BONN2B | BONN1- | 2015 | Removed | 0.1559 | 8.9445 | -0.1694 | 240
GRNA1- | EWEH5- | 2015 | Removed | 1.161 | 23.225 | 0 | 40
FALL4- | FALL3B | 2015 | Removed | 0.2564 | 16.6647 | 0 | 120
KAIM2- | KAIM3- | 2015 | Removed | 0.4944 | 20.244 | -0.245 | 120
BONN1- | BONN3- | 2015 | Removed | 0.965 | 21.178 | 0 | 60
KAIM2- | KAIM3- | 2015 | Removed | 0.4819 | 20.2443 | -0.2454 | 120
BONN2A | BONN1- | 2015 | Removed | 0.1559 | 8.9445 | -0.1694 | 240
SIGH2Q | SIGH3A | 2015 | Removed | 0.4536 | 27.274 | 0 | 180
FALL4- | FALL3A | 2015 | Removed | 0.2564 | 16.6647 | 0 | 120
SIGH2R | SIGH3A | 2015 | Removed | 0.4868 | 18.7437 | 0 | 120
BLAC1- | BLAC3A | 2016 | Addition | 0.3635 | 25.4418 | 0 | 90
BLAC1- | BLAC3A | 2016 | Addition | 0.3635 | 25.4418 | 0 | 90
BLAC1- | BLAC3B | 2016 | Addition | 0.3635 | 25.4418 | 0 | 90
BLAC1- | BLAC3B | 2016 | Addition | 0.3635 | 25.4418 | 0 | 90
CUPA1Q | CUPA3- | 2016 | Change | 0.3635 | 25.4418 | 0 | 90
CUPA1R | CUPA3- | 2016 | Change | 0.3635 | 25.4418 | 0 | 90
DALM1- | DALM3- | 2016 | Change | 0.469 | 26.7 | 0 | 90
DENN2- | DENN1- | 2016 | Addition | 0.1452 | 8.6093 | -0.1299 | 240
DERS1Q | DERS3- | 2016 | Addition | 0.1984 | 16.6655 | 0 | 90
DUNH1S | DUNH3- | 2016 | Addition | 0.1984 | 16.6655 | 0 | 90
DUNH1T | DUNH3- | 2016 | Addition | 0.1984 | 16.6655 | 0 | 90
GALA1- | GALA3- | 2016 | Change | 0.3635 | 25.4418 | 0 | 90
GIFF2R | GIFF3- | 2016 | Addition | 0.4536 | 27.274 | 0 | 180
GLGL1Q | GLGL3- | 2016 | Addition | 0.3086 | 27.776 | 0 | 90
GLGL1R | GLGL3- | 2016 | Addition | 0.3086 | 27.776 | 0 | 90
NETS1- | NETS3- | 2016 | Change | 0.3511 | 18.3966 | -0.0097 | 60
NEWF1Q | NEWF3- | 2016 | Addition | 0.1984 | 16.6655 | 0 | 90
TONG1- | TONG3- | 2016 | Addition | 0.7495 | 19.986 | 0 | 30
TONG1- | TONG3- | 2016 | Addition | 0.7495 | 19.986 | 0 | 30
WISH4- | WISH2- | 2016 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
WISH4- | WISH2- | 2016 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
GIFF2R | GIFF3- | 2016 | Removed | 0.4868 | 18.3352 | -0.2147 | 120
BLCW1- | BLCW3A | 2017 | Addition | 0.21 | 16.6687 | 0 | 90
GIFF2Q | GIFF3A | 2017 | Addition | 0.4536 | 27.274 | 0 | 180
KILT2Q | KILT3- | 2017 | Addition | 0.4536 | 27.274 | 0 | 180
NECU2- | NECU1Q | 2017 | Addition | 0.1167 | 8.7367 | -0.1299 | 240
NECU2- | NECU1R | 2017 | Addition | 0.1167 | 8.7367 | -0.1299 | 240
TONG1- | TONG3- | 2017 | Change | 0.3119 | 21.8311 | 0 | 60
TONG1- | TONG3- | 2017 | Change | 0.3119 | 21.8311 | 0 | 60
KILT2Q | KILT3- | 2017 | Removed | 0.4927 | 18.4934 | -0.1756 | 120
GIFF2Q | GIFF3- | 2017 | Removed | 0.4958 | 18.4517 | -0.196 | 120
CRYR4- | AIKE1- | 2018 | Addition | 0.1496 | 10.0489 | -0.0583 | 240
CRYR4- | NNGA2- | 2018 | Addition | 0.076 | 5.333 | -0.008 | 375
CRYR4- | NNGB2- | 2018 | Addition | 0.076 | 5.333 | -0.008 | 375
DALM1- | DALM3- | 2018 | Change | 0.469 | 27.3326 | 0 | 90
EHAU1- | EHAU3- | 2018 | Addition | 0.3488 | 24.4142 | 0 | 120
KIER1R | KIER3- | 2018 | Change | 0.4314 | 27.1188 | -0.0087 | 90
MARG1- | MARG3- | 2018 | Addition | 0.3635 | 25.4418 | 0 | 90
MOFF4- | MOFF1- | 2018 | Addition | 0.1483 | 10.0614 | -0.3432 | 240
NNGA2G | NNGG3A | 2018 | Addition | 0.114 | 8.571 | -0.006 | 280
NNGB2G | NNGG3B | 2018 | Addition | 0.114 | 8.571 | -0.006 | 280
ROWA1- | ROWA3- | 2018 | Addition | 0.3635 | 25.4418 | 0 | 90
WDOD1- | AIKE3A | 2018 | Addition | 0.3488 | 24.4142 | 0 | 120
GAWH1Q | GAWH3- | 2020 | Addition | 0.3635 | 25.4418 | 0 | 90
GLLR1- | GLLR3- | 2020 | Addition | 0.3119 | 21.8311 | 0 | 60
KEON1- | KEON3- | 2020 | Addition | 0.3635 | 25.4418 | 0 | 90
KILG2- | KILG3A | 2020 | Addition | 0.1786 | 12.4987 | 0 | 120
KILG2- | KILG3B | 2020 | Addition | 0.1786 | 12.4987 | 0 | 120
KILG2- | KILG3C | 2020 | Addition | 0.1786 | 12.4987 | 0 | 120
KILS4T | KILS2- | 2020 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
KINC4A | KINC2- | 2020 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
KINC4B | KINC2- | 2020 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
LURR1- | LURR3- | 2020 | Addition | 0.3635 | 25.4418 | 0 | 90
NETS1- | NETS3- | 2020 | Change | 0.8311 | 28.2878 | -0.0097 | 60
NETS1- | NETS3- | 2020 | Addition | 0.8311 | 28.2878 | -0.0097 | 60
BONN4- | BONN1- | 2023 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
BONN4- | BONN1- | 2023 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
COCK2- | COCK3- | 2023 | Change | 0.2841 | 27.8235 | -0.0171 | 120
CRUA2Q | CRUA01 | 2023 | Change | 0.1222 | 9.4733 | -1.1608 | 270
DENN2A | DENN1- | 2023 | Addition | 0.1452 | 8.6093 | -0.1299 | 240
DENN4- | DENN2A | 2023 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
DUMF2- | DUMF1- | 2023 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
DUMF2- | DUMF1- | 2023 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
DUMF4- | DUMF2- | 2023 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
DUMF4- | DUMF2- | 2023 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
DUMF4- | DUMF2- | 2023 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
GLLE2- | GLLE1- | 2023 | Addition | 0.138 | 8.3289 | -0.2121 | 360
GLLE2- | GLLE1- | 2023 | Addition | 0.138 | 8.3289 | -0.2121 | 360
KENN1- | KENN3- | 2023 | Addition | 0.3488 | 24.4142 | 0 | 120
KYPE1- | KYPE3- | 2023 | Addition | 0.3488 | 24.4142 | 0 | 120
NEAR2- | NEAR3- | 2023 | Addition | 0.4856 | 18.2435 | -0.1614 | 120
NEAR2- | NEAR3- | 2023 | Addition | 0.4856 | 18.1602 | -0.1723 | 120
NETS2- | NETS1- | 2023 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
NETS2- | NETS1- | 2023 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
WISH4- | WISH2- | 2023 | Change | 0.0166 | 1.7059 | -0.1199 | 1000
WISH4- | WISH2- | 2023 | Change | 0.0166 | 1.7059 | -0.1199 | 1000
BONN2B | BONN1- | 2023 | Removed | 0.1559 | 8.9445 | -0.1694 | 240
DENN2- | DENN1- | 2023 | Removed | 0.1452 | 8.6093 | -0.1299 | 240
BONN2A | BONN1- | 2023 | Removed | 0.1559 | 8.9445 | -0.1694 | 240
NEAR2R | NEAR3- | 2023 | Removed | 0.4856 | 18.1602 | -0.1723 | 120
NEAR2Q | NEAR3- | 2023 | Removed | 0.4856 | 18.2435 | -0.1614 | 120
DENN4- | DENN2- | 2023 | Removed | 0.015 | 1.6499 | -0.2252 | 1000

## B-3-2c
Table B.3.2c - NGET Transformer Changes 2015/16 to 2023/24 | [7 empty] | Back To Menu
Node 1 | Node 2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
BUST2* | BUST21 | 2015 | Addition | 0.018 | 1.6146 | -1.5533 | 750
BUST2* | BUST21 | 2015 | Addition | 0.018 | 1.6146 | -1.5533 | 750
CARR41 | CARR11 | 2015 | Addition | 0.1812 | 8.028 | -0.1253 | 240
CONQ41 | CONQ12 | 2015 | Addition | 0.1057 | 7.9352 | -0.339 | 240
DAIN41 | DAIN4* | 2015 | Addition | 0.0182 | 1.5763 | -0.0904 | 1100
DAIN41 | DAIN4* | 2015 | Addition | 0.0182 | 1.5763 | -0.0904 | 1100
DIDC41 | DIDC4* | 2015 | Addition | 0.3195 | 20.7975 | -0.4256 | 80
DIDC41 | DIDC4* | 2015 | Addition | 0.3195 | 20.7975 | -0.4256 | 80
ELLA21 | ELLA11 | 2015 | Change | 0.1221 | 8.0467 | -0.0391 | 180
IMPP41 | IMPP31 | 2015 | Addition | 0.2262 | 15.019 | -0.0538 | 143
IMPP41 | IMPP4* | 2015 | Addition | 0.3195 | 20.7975 | -0.4256 | 80
IVER22 | IVER61 | 2015 | Change | 0.2856 | 11.1999 | -2.5672 | 180
MELK41 | MELK4* | 2015 | Addition | 0.3195 | 20.7975 | -0.4256 | 80
MELK41 | MELK4* | 2015 | Addition | 0.3195 | 20.7975 | -0.4256 | 80
NEWX21 | NEWX11 | 2015 | Addition | 0.1366 | 8.0648 | -0.0471 | 180
NEWX21 | NEWX11 | 2015 | Addition | 0.1366 | 8.0648 | -0.0471 | 240
RATS41 | RATS12 | 2015 | Addition | 0.1046 | 7.8493 | -0.0881 | 240
STAL21 | STAL2* | 2015 | Addition | 0.3209 | 20.5475 | -0.1224 | 80
STAL21 | STAL2* | 2015 | Addition | 0.3209 | 20.5475 | -0.1224 | 80
THOM41 | THOM4* | 2015 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
TILB41 | TILB11 | 2015 | Addition | 0.1307 | 7.9515 | -0.1098 | 120
DRAK41 | DRAK41 | 2015 | Removed | 0.017 | 1.6132 | -5.1203 | 750
DEES42 | CONQ12 | 2015 | Removed | 0.1264 | 8.4534 | -0.357 | 240
CARR21 | CARR11 | 2015 | Removed | 0.1681 | 8.3396 | -1.4878 | 180
CARR21 | CARR12 | 2015 | Removed | 0.2847 | 12.2467 | -1.4346 | 120
CARR21 | CARR12 | 2015 | Removed | 0.2264 | 12.2479 | -0.6062 | 120
IMPP41 | IMPP31 | 2015 | Removed | 0.2262 | 15.019 | -0.0538 | 143
NEWX21 | NEWX11 | 2015 | Removed | 0.1366 | 8.0648 | -0.0471 | 240
TILB21 | TILB11 | 2015 | Removed | 0.3792 | 12.0524 | -0.3982 | 120
THOM42 | THOM21 | 2015 | Removed | 0.0185 | 1.614 | -0.5638 | 750
CARR21 | CARR11 | 2015 | Removed | 0.1927 | 8.5256 | -0.5357 | 180
RATS41 | RATS12 | 2015 | Removed | 0.1759 | 7.9134 | -0.267 | 240
DRAK41 | DRAK21 | 2015 | Removed | 0.0178 | 1.5995 | -1.2431 | 750
CARR21 | CARR1* | 2015 | Removed | 0.1927 | 8.5256 | -0.5357 | 180
NEWX21 | NEWX11 | 2015 | Removed | 0.1366 | 8.0648 | -0.0471 | 240
CARR41 | PATT08* | 2016 | Addition | 0.068 | 3.1061 | 0 | 515
CARR41 | PATT08* | 2016 | Addition | 0.068 | 3.1061 | 0 | 515
CONQ41 | CONQ13 | 2016 | Addition | 0.1057 | 7.9352 | -0.339 | 240
FLIB4* | FLIB4* | 2016 | Addition | 0 | 0.08 | 0 | 3000
IMPP41 | IMPP31 | 2016 | Addition | 0.2262 | 15.019 | -0.0538 | 143
IMPP41 | IMPP4* | 2016 | Addition | 0.3195 | 20.7975 | -0.4256 | 80
IVER21 | IVER61 | 2016 | Change | 0.2856 | 11.1999 | -2.5672 | 120
KNAR21 | KNAR11 | 2016 | Addition | 0.1441 | 8.6238 | -0.2707 | 240
KNAR21 | KNAR12 | 2016 | Addition | 0.1441 | 8.6238 | -0.2707 | 240
LACK21 | LACK2* | 2016 | Addition | 0.0026 | 3.61 | 0 | 500
NEWX21 | NEWX61 | 2016 | Addition | 0.3204 | 14.3298 | -0.2424 | 180
SJOW41 | SJOW2A | 2016 | Change | 0.0178 | 1.5995 | -0.4997 | 750
DRAK21 | DRAK2* | 2016 | Removed | 0.2756 | 9.9228 | -0.0925 | 150
NEWX21 | NEWX61 | 2016 | Removed | 0.3204 | 14.3298 | -0.2424 | 180
ELST22 | ELST14 | 2016 | Removed | 0.3567 | 11.136 | -0.7303 | 120
ELST21 | ELST13 | 2016 | Removed | 0.3567 | 11.136 | -0.7303 | 120
IMPP41 | IMPP31 | 2016 | Removed | 0.2262 | 15.019 | -0.0538 | 143
DEES41 | CONQ13 | 2016 | Removed | 0.1057 | 7.9352 | -0.339 | 240
DRAK21 | DRAK11 | 2016 | Removed | 0.2264 | 12.2479 | -0.6062 | 120
BARK21 | BARW31 | 2017 | Addition | 0.618 | 29.2635 | -0.2527 | 100
BARK22 | BARK11 | 2017 | Addition | 0.1646 | 8.0383 | -0.1808 | 180
HIBU41 | HIBU11 | 2017 | Addition | 0.1264 | 8.4534 | -0.357 | 240
HIBU41 | HIBU11 | 2017 | Addition | 0.1264 | 8.4534 | -0.357 | 240
HIBU41 | HIBU11 | 2017 | Addition | 0.1264 | 8.4534 | -0.357 | 240
BARK22 | BARK11 | 2017 | Removed | 0.1646 | 8.0383 | -0.1808 | 180
DEES41 | DEES4* | 2017 | Removed | 0 | 2 | 0 | 600
BARK21 | BARW31 | 2017 | Removed | 0.618 | 29.2635 | -0.2527 | 100
CANW4* | CANW1* | 2018 | Addition | 0.1139 | 8.1036 | -2.059 | 240
CANW4* | CANW1* | 2018 | Addition | 0.1139 | 8.1036 | -2.059 | 240
CANW4* | CANW1* | 2018 | Addition | 0.1139 | 8.1036 | -2.059 | 240
CANW4* | CANW1* | 2018 | Addition | 0.1139 | 8.1036 | -2.059 | 240
CANW4* | CANW1* | 2018 | Addition | 0.1139 | 8.1036 | -2.059 | 240
PEMB41 | PEMB4* | 2018 | Addition | 0.0351 | 2.6313 | 0 | 570
SELW41 | Eleclink HVDC Connections* | 2018 | Addition | 0 | 1 | 0 | 1200
SWAN41 | SWAN4* | 2018 | Addition | 0.0182 | 1.5763 | -0.0904 | 1100
SWAN41 | SWAN4* | 2018 | Addition | 0.0182 | 1.5763 | -0.0904 | 1100
SWAN41 | SWAN4* | 2018 | Addition | 0.0182 | 1.5763 | -0.0904 | 1100
WIMB41 | WIMB2* | 2018 | Addition | 0.014 | 2.6567 | -0.1528 | 950
WIMB41 | WIMB2* | 2018 | Addition | 0.014 | 2.6567 | -0.1528 | 950
WISD4* | WISD21 | 2018 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
WISD4* | WISD22 | 2018 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
SJOW41 | SJOW2A | 2018 | Removed | 0.0178 | 1.5995 | -0.4997 | 750
SJOW41 | SJOW2B | 2018 | Removed | 0.0224 | 2.5703 | -0.5831 | 750
IVER42 | IVER21 | 2020 | Addition | 0.0152 | 1.6463 | -0.1118 | 775
KIBY41 | KIBY22 | 2020 | Addition | 0.0152 | 1.6463 | -0.1118 | 750
KIBY41 | KIBY22 | 2020 | Addition | 0.0152 | 1.6463 | -0.1118 | 750
KIBY42 | KIBY21 | 2020 | Addition | 0.0152 | 1.6463 | -0.1118 | 750
KIBY42 | KIBY21 | 2020 | Addition | 0.0152 | 1.6463 | -0.1118 | 750
LISD2* | LISD21 | 2020 | Addition | 0.002 | 0.9802 | 0 | 760
RICH4* | RICH4* | 2020 | Addition | 0.0282 | 1.4373 | 0 | 1100
WALP41 | WALP1* | 2020 | Addition | 0.0417 | 2.1646 | 0 | 300
WALP41 | WALP1* | 2020 | Addition | 0.0417 | 2.1646 | 0 | 300
WASF41 | WASF11 | 2020 | Addition | 0.1264 | 8.4534 | -0.357 | 180
WASF42 | WASF12 | 2020 | Addition | 0.1264 | 8.4534 | -0.357 | 180
WHAM4A | WYMO41 | 2020 | Addition | 0.001 | 0.35 | 0 | 1410
WIMB41 | WIMB11 | 2020 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB11 | 2020 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB12 | 2020 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB12 | 2020 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WASF21 | WASF12 | 2020 | Removed | 0.197 | 7.9698 | -0.2553 | 180
WIMB21 | WIMB11 | 2020 | Removed | 0.1923 | 8.081 | -1.4418 | 180
WIMB21 | WIMB12 | 2020 | Removed | 0.179 | 8.3648 | -4.7616 | 180
PEWO41 | PEWO22 | 2020 | Removed | 0.0178 | 1.5995 | -1.2431 | 750
IVER42 | IVER21 | 2020 | Removed | 0.0326 | 2.3798 | -3.9003 | 500
WIMB21 | WIMB12 | 2020 | Removed | 0.167 | 7.9774 | -0.2092 | 240
WIMB21 | WIMB11 | 2020 | Removed | 0.1845 | 7.8956 | -0.1938 | 240
WASF22 | WASF11 | 2020 | Removed | 0.197 | 7.9698 | -0.2553 | 180
PEWO41 | PEWO21 | 2020 | Removed | 0.0175 | 1.5879 | -4.0069 | 1000
BRIM4* | BRIM1* | 2023 | Addition | 0.1264 | 7.974 | -0.1303 | 240
BRIM4* | BRIM11 | 2023 | Addition | 0.1264 | 7.974 | -0.1303 | 240
BRWA4* | BRWA11 | 2023 | Addition | 0.1307 | 7.9515 | -0.1098 | 180
BRWA4* | BRWA11 | 2023 | Addition | 0.1307 | 7.9515 | -0.1098 | 180
HACK41 | HACK61 | 2023 | Addition | 0.1529 | 12.1324 | -0.0623 | 240
HACK41 | HACK61 | 2023 | Addition | 0.1529 | 12.1324 | -0.0623 | 240
HAWP41 | HAWP4* | 2023 | Addition | 0.0023 | 0.175 | 0 | 3000
PEMB41 | PEMBHV1 | 2023 | Addition | 0.0018 | 0.2562 | 0 | 4000
PEMB41 | PEMBHV1 | 2023 | Addition | 0.0018 | 0.2562 | 0 | 4000
SAFO41 | SAFO11 | 2023 | Addition | 0.1307 | 7.9515 | -0.1098 | 200
SAFO41 | SAFO12 | 2023 | Addition | 0.1307 | 7.9515 | -0.1098 | 180
THOM41 | THOM4* | 2023 | Addition | 0.165 | 3.2959 | 0 | 500
WALP41 | WALP1* | 2023 | Change | 0.0417 | 2.1646 | 0 | 500
WIMB41 | WIMB11 | 2023 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB12 | 2023 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
HACK22 | HACK61 | 2023 | Removed | 0.2793 | 13.3304 | -0.6737 | 180
BRWA2B | BRWA11 | 2023 | Removed | 0.167 | 7.9774 | -0.2092 | 240
HACK41 | HACK21 | 2023 | Removed | 0.0182 | 1.5763 | -0.0904 | 1100
CARR4* | CARR21 | 2023 | Removed | 0.0185 | 1.614 | -0.5638 | 750
WALX42 | WALX22 | 2023 | Removed | 0.0176 | 1.5828 | -0.1018 | 1000
BRIM2C | BRIM11 | 2023 | Removed | 0.1688 | 8.3316 | -1.1711 | 240
BRWA2A | BRWA11 | 2023 | Removed | 0.167 | 7.9774 | -0.2092 | 240
WIMB21 | WIMB12 | 2023 | Removed | 0.1845 | 7.8956 | -0.1938 | 240
WIMB21 | WIMB11 | 2023 | Removed | 0.167 | 7.9774 | -0.2092 | 240
BRIM2D | BRIM1* | 2023 | Removed | 0.1688 | 8.3316 | -1.1711 | 240
SEAB41 | SEAB11 | 2023 | Removed | 0.1307 | 7.9515 | -0.1098 | 240
HACK41 | HACK22 | 2023 | Removed | 0.0182 | 1.5763 | -0.0904 | 1100
CARR4* | CARR21 | 2023 | Removed | 0.0185 | 1.614 | -0.5638 | 750
WALX42 | WALX21 | 2023 | Removed | 0.0176 | 1.5828 | -0.1018 | 1000
HACK21 | HACK61 | 2023 | Removed | 0.2793 | 13.3304 | -0.6737 | 180

## B-3-2d
Table B.3.2d - Offshore Transmission Transformer Changes 2015/16 to 2023/24 | [8 empty] | Back To Menu
Node 1 | Node2 | Voltage Ratio (kV) | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
BOLN41 | RAMP1* | 400/132 | 2015 | Addition | 0.0282 | 4.3546 | -0.2109 | 460
BOLN41 | RAMP1* | 400/132 | 2015 | Addition | 0.0282 | 4.3546 | -0.2109 | 460
MIDL41 | WAEN8* | 400/132 | 2015 | Addition | 0.1295 | 4.2085 | -1.553 | 380
MIDL41 | WAEN8* | 400/132 | 2015 | Addition | 0.1295 | 4.2085 | -1.553 | 380
WAEN8* | WAEN8* | 150/33 | 2015 | Addition | 0 | 6.6667 | 0 | 180
WAEN8* | WAEN8* | 150/33 | 2015 | Addition | 0 | 6.6667 | 0 | 180
WAEN8* | WAEN8* | 150/33 | 2015 | Addition | 0 | 6.6667 | 0 | 180
WAEN8* | WAEN8* | 150/33 | 2015 | Addition | 0 | 6.6667 | 0 | 180
BOLN41 | RAMP1* | 400/132 | 2016 | Removed | 0.0282 | 4.3546 | -0.2109 | 460
BOLN41 | RAMP1* | 400/132 | 2016 | Removed | 0.0282 | 4.3546 | -0.2109 | 460
BOLN41 | RAMP1* | 400/132 | 2017 | Addition | 0.0282 | 4.3546 | -0.2109 | 460
BOLN41 | RAMP1* | 400/132 | 2017 | Addition | 0.0282 | 4.3546 | -0.2109 | 460
GAOF1* | GAOF8* | 132/33 | 2017 | Addition | 0.5556 | 36.6625 | 0 | 180
GAOF1* | GAOF8* | 132/33 | 2017 | Addition | 0.5556 | 36.6625 | 0 | 90
GAOF1* | GAOF8* | 132/33 | 2017 | Addition | 0.5556 | 36.6625 | 0 | 90
GAOF1* | GAOF8* | 132/33 | 2017 | Addition | 0.5556 | 36.6625 | 0 | 180
GAOF1* | GAOF8* | 132/33 | 2017 | Addition | 0.5556 | 36.6625 | 0 | 180
GAON1* | GAON1* | 132/13.9 | 2017 | Addition | 0.0241 | 11 | 0 | 90
GAON1* | GAON1* | 132/13.9 | 2017 | Addition | 0.0241 | 11 | 0 | 90
GAON1* | GAON1* | 132/13.9 | 2017 | Addition | 0.0241 | 11 | 0 | 90
NECT4* | NECT11 | 400/132 | 2017 | Addition | 0.1326 | 8.774 | -0.7141 | 240
NECT4* | NECT12 | 400/132 | 2017 | Addition | 0.1326 | 8.774 | -0.7141 | 240
BODE41 | BODE4* | 400/220 | 2018 | Addition | 0.3827 | 12.8514 | -0.246 | 140
BODE41 | BODE4* | 400/220 | 2018 | Addition | 0.3827 | 12.8514 | -0.246 | 140
BUBW8* | BUBW8* | 220/33 | 2018 | Addition | 0.3514 | 13.8884 | -0.5676 | 140
BUBW8* | BUBW8* | 220/33 | 2018 | Addition | 0.3514 | 13.8884 | -0.5676 | 140
BRFO41 | BRFO4* | 400/275 | 2020 | Addition | 0.2857 | 0.8835 | -1.6361 | 700
BRFO41 | BRFO4* | 400/275 | 2020 | Addition | 0.2857 | 0.8835 | -1.6361 | 700
DOCS1* | DOCS3* | 132/33 | 2020 | Addition | 0.1923 | 4.0381 | -0.5138 | 260
DOCS1* | DOCS3* | 132/33 | 2020 | Addition | 0.1923 | 4.0381 | -0.5138 | 260
HORN4* | HORN4* | 400/320 | 2020 | Addition | 0 | 1.5 | 0 | 1000
HORN4* | HORN4* | 400/320 | 2020 | Addition | 0 | 1.5 | 0 | 1000
IRIS81 | IRIS-1 | 400/132 | 2020 | Addition | 0.3448 | 2.1449 | -1.3551 | 580
IRIS82 | IRIS-1 | 400/132 | 2020 | Addition | 0.3448 | 2.1449 | -1.3551 | 580
RACB1* | RACB3* | 132/33 | 2020 | Addition | 0.1923 | 4.0381 | -0.5138 | 260
RACB1* | RACB3* | 132/33 | 2020 | Addition | 0.1923 | 4.0381 | -0.5138 | 260
BRFO41 | BRFO4* | 400/132 | 2023 | Addition | 0.3448 | 2.1449 | -1.3551 | 580
BRFO41 | BRFO4* | 400/132 | 2023 | Addition | 0.3448 | 2.1449 | -1.3551 | 580
BRFO41 | BRFO4* | 400/132 | 2023 | Addition | 0.3448 | 2.1449 | -1.3551 | 580
BRFO41 | BRFO4* | 400/275 | 2023 | Addition | 0.2857 | 0.8835 | -1.6361 | 700
DOGG4* | DOGG4* | 400/320 | 2023 | Addition | 0 | 1.5 | 0 | 1000
DOGG4* | DOGG4* | 400/320 | 2023 | Addition | 0 | 0 | 0 | --
HORN4* | HORN4* | 400/320 | 2023 | Addition | 0 | 1.5 | 0 | 1000
PEMB41 | GRPM8* | 400/275 | 2023 | Addition | 0.0023 | 0.3417 | 0 | 3000
PEMB41 | GRPM8* | 400/275 | 2023 | Addition | 0.0023 | 0.3417 | 0 | 3000
STAH41 | STAH4* | 400/132 | 2023 | Addition | 0.0775 | 0.1606 | -6.0343 | 2580
WALP41 | WALP4* | 400/320 | 2023 | Addition | 0 | 1.5 | 0 | 1000

## B-4-1a
Table B.4.1a - SHE Transmission Reactive Compensation Equipment, Winter 2014/15 | [6 empty] | Back To Menu
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
DOUNREAY | DOUN3X | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
DOUNREAY | DOUN3W | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
KINTORE | KINT3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
KINTORE | KINT3Y | 3 |  | 60 | Shunt Reactor - SGT tertiary | 33
TEALING | TEAL3W | 1 |  | 30 | Shunt Reactor - SGT tertiary | 33
TEALING | TEAL3Y | 3 |  | 30 | Shunt Reactor - SGT tertiary | 33
TEALING | TEAL2J | 1 | 225 | 75 | SVC | 275
TEALING | TEAL10 | 1 | 45 |  | Mechanically Switched Capacitor | 132
TEALING | TEAL10 | 2 | 45 |  | Mechanically Switched Capacitor | 132
BEAULY | BEAU2J | 1 | 150 | 150 | SVC | 275
BEAULY | BEAU3U | 1 |  | 90 | Shunt Reactor - SGT tertiary | 33
BEAULY | BEAU3V | 2 |  | 90 | Shunt Reactor - SGT tertiary | 33
BEAULY | BEAU1K | 1 | 45 |  | Mechanically Switched Capacitor | 132
BEAULY | BEAU1J | 2 | 45 |  | Mechanically Switched Capacitor | 132
FORT AUGUSTUS | FAUG3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3Y | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3X | 3 |  | 60 | Shunt Reactor - SGT tertiary | 33

## B-4-1b
Table B.4.1b - SPT Reactive Compensation Equipment, Winter 2014/15 | [6 empty] | Back To Menu
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
DEWAR PLACE | DEWP3- | 1 |  | 60 | REACTOR | 33
DEWAR PLACE | DEWP3- | 2 |  | 60 | REACTOR | 33
ELVANFOOT | ELVA4- | 1 | 225 |  | MSCDN | 400
GIFFNOCK | GIFF3- | 1 |  | 60 | REACTOR | 33
NEILSTON | NEIL3U | 1 |  | 50 | Shunt Reactor - SGT tertiary | 33
SHRUBHILL | SHRU3- | 1 |  | 60 | REACTOR | 33
SHRUBHILL | SHRU3- | 2 |  | 60 | REACTOR | 33
SIGHTHILL | SIGH3- | 1 |  | 60 | REACTOR | 33
TORNESS | TORN4- | 1 |  | 150 | REACTOR | 400
TORNESS | TORN4- | 2 |  | 150 | REACTOR | 400
WEST GEORGE STREET | WGEO3- | 1 |  | 60 | REACTOR | 33
WEST GEORGE STREET | WGEO3- | 2 |  | 60 | REACTOR | 33
WINDYHILL | WIYH3V | 3 |  | 60 | Shunt Reactor - SGT tertiary | 33
WINDYHILL | WIYH2- | 1 | 150 |  | MSCDN | 275
WISHAW | WISH3V | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
LONGANNET | LOAN2- | 1 | 225 |  | MSCDN | 275
LONGANNET | LOAN2- | 2 | 225 |  | MSCDN | 275
MOFFAT | MOFF4- | 1 | 225 |  | MSCDN | 400

## B-4-1c
Table B.4.1c - NGET Reactive Compensation Equipment, Winter 2014/15 | [6 empty] | Back To Menu
Site Name | Node | Unit Number | Mvar Generation | Mvar Absorption | Compensation Type | Connection Voltage (kV)
ABERTHAW | ABTH12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
ABERTHAW | ABTH12 | 2 | 60 |  | Mechanically Switched Capacitor | 132
ABHAM | ABHA11 | 1 | 45 |  | Mechanically Switched Capacitor | 132
ABHAM | ABHA12 | 2 | 45 |  | Mechanically Switched Capacitor | 132
ALVERDISCOTT | ALVE10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
BARKING | BARK10 | 1 |  | 60 | Reactor | 132
BARKING | BARK10 | 2 |  | 60 | Reactor | 132
BEDDINGTON | BEDD11 | 1 |  | 60 | Reactor | 132
BEDDINGTON | BEDD11 | 2 |  | 60 | Reactor | 132
BEDDINGTON | BEDD11 | 3 |  | 60 | Reactor | 132
BEDDINGTON | BEDD11 | 4 |  | 60 | Reactor | 132
BEDDINGTON | BEDD1A | 2 |  | 15 | Reactor | 132
BEDDINGTON | BEDD1B | 1 |  | 15 | Reactor | 132
BEDDINGTON | BEDD21 | 2 | 150 |  | Mechanically Switched Capacitor | 275
BEDDINGTON | BEDD21 | 1 |  | 100 | Reactor | 275
BEDDINGTON | BEDD22 | 1 | 150 |  | Mechanically Switched Capacitor | 275
BEDDINGTON | BEDD22 | 1 |  | 100 | Reactor | 275
BERKSWELL | BESW10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
BERKSWELL | BESW10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
BERKSWELL | BESW10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
BERKSWELL | BESW20 | 1 | 150 |  | Mechanically Switched Capacitor | 275
BIRKENHEAD | BIRK10 | 1 |  | 60 | Reactor | 132
BISHOPS WOOD | BISW10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
BISHOPS WOOD | BISW10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
BISHOPS WOOD | BISW10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
BLYTH | BLYT21 | 1 | 150 |  | Mechanically Switched Capacitor | 275
BLYTH | BLYT22 | 2 | 150 |  | Mechanically Switched Capacitor | 275
BOLNEY | BOLN11 | 4 | 60 |  | Mechanically Switched Capacitor | 132
BOLNEY | BOLN12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
BOLNEY | BOLN12 | 1 |  | 60 | Reactor | 132
BOLNEY | BOLN13 | 2 | 60 |  | Mechanically Switched Capacitor | 132
BOLNEY | BOLN13 | 2 |  | 60 | Reactor | 132
BOLNEY | BOLN14 | 3 | 60 |  | Mechanically Switched Capacitor | 132
BOLNEY | BOLN40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
BRADFORD WEST | BRAW11 | 1 |  | 60 | Reactor | 132
BRADFORD WEST | BRAW12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
BRADFORD WEST | BRAW12 | 2 |  | 60 | Reactor | 132
BRAMFORD | BRFO10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
BRAMFORD | BRFO10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
BRAMFORD | BRFO10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
BREDBURY | BRED10 | 1 |  | 60 | Reactor | 132
BREDBURY | BRED10 | 2 |  | 60 | Reactor | 132
BRIDGEWATER | BRWA10 | 1 | 45 |  | Mechanically Switched Capacitor | 132
BRIDGEWATER | BRWA10 | 2 | 45 |  | Mechanically Switched Capacitor | 132
BRIDGEWATER | BRWA2B |  | 60 |  | SVC | Tertiary Connected
BUSHBURY | BUSH10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
BUSHBURY | BUSH10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
BUSHBURY | BUSH10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
BUSHBURY | BUSH10 | 1 |  | 60 | Reactor | 132
BUSHBURY | BUSH20 | 1 | 150 |  | Mechanically Switched Capacitor | 275
BUSTLEHOLM | BUST10 | 1 | 20 |  | Mechanically Switched Capacitor | 132
BUSTLEHOLM | BUST10 | 1 |  | 60 | Reactor | 132
BUSTLEHOLM | BUST10 | 2 |  | 60 | Reactor | 132
CAPENHURST | CAPE21 | 1 | 150 |  | Mechanically Switched Capacitor | 275
CELLARHEAD | CELL11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
CELLARHEAD | CELL11 | 3 | 60 |  | Mechanically Switched Capacitor | 132
CELLARHEAD | CELL11 | 4 | 60 |  | Mechanically Switched Capacitor | 132
CELLARHEAD | CELL11 | 1 |  | 60 | Reactor | 132
CELLARHEAD | CELL11 | 2 |  | 60 | Reactor | 132
CELLARHEAD | CELL12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
CELLARHEAD | CELL40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
CELLARHEAD | CELL40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
CELLARHEAD | CELL40 | 5 | 150 | -75 | SVC | 400
CELLARHEAD | CELL40 | 6 | 150 | -75 | SVC | 400
CHESTERFIELD | CHTE11 | 1 |  | 60 | Reactor | 132
CHICKERELL | CHIC10 | 1 |  | 60 | Reactor | 132
CHICKERELL | CHIC42 | 1 | 225 |  | Mechanically Switched Capacitor | 400
CILFYNYDD | CILF2A | 2 |  | 60 | Reactor | 275
CILFYNYDD | CILF2B | 1 |  | 60 | Reactor | 275
CILFYNYDD | CILF40 | 1 |  | 200 | Reactor | 400
CITY ROAD | CITR11 | 2 | 55 |  | Mechanically Switched Capacitor | 132
CITY ROAD | CITR12 | 1 | 55 |  | Mechanically Switched Capacitor | 132
CITY ROAD | CITR41 | 1 |  | 200 | Reactor | 400
CONNAH'S QUAY | CONQ11 | 1 |  | 60 | Reactor | 132
COVENTRY | COVE10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
COVENTRY | COVE10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
COVENTRY | COVE10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
COVENTRY | COVE10 | 1 |  | 60 | Reactor | 132
COVENTRY | COVE20 |  | 60 |  | SVC | Tertiary Connected
COWLEY | COWL10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
COWLEY | COWL10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
COWLEY | COWL10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
COWLEY | COWL40 | 1 |  | 200 | Reactor | 400
CREYKE BECK | CREB11 | 1 |  | 60 | Reactor | 132
CREYKE BECK | CREB11 | 2 |  | 60 | Reactor | 132
DRAKELOW | DRAK21 | 6 | 150 | -75 | SVC | 275
DRAKELOW | DRAK41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
DRAKELOW | DRAK42 | 1 | 225 |  | Mechanically Switched Capacitor | 400
DRAX | DRAX11 | 2 |  | 60 | Reactor | 132
DRAX | DRAX12 | 1 |  | 60 | Reactor | 132
EAST CLAYDON | ECLA10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
EAST CLAYDON | ECLA10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
EAST CLAYDON | ECLA10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
EAST CLAYDON | ECLA10 | 1 |  | 60 | Reactor | 132
EAST CLAYDON | ECLA10 | 2 |  | 60 | Reactor | 132
EAST CLAYDON | ECLA40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
EAST CLAYDON | ECLA40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
EAST CLAYDON | ECLA40 | 6 | 150 | -75 | SVC | 400
ELLAND | ELLA12 | 1 |  | 60 | Reactor | 132
ELSTREE | ELST21 |  | 60 |  | SVC | Tertiary Connected
ELSTREE | ELST22 |  | 60 |  | SVC | Tertiary Connected
ELSTREE | ELST40 | 1 |  | 200 | Reactor | 400
ENDERBY | ENDE40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
ENDERBY | ENDE40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
EXETER | EXET10 | 1 | 51 |  | Mechanically Switched Capacitor | 132
EXETER | EXET10 | 1 | 56 |  | Mechanically Switched Capacitor | 132
EXETER | EXET40 | 3 | 150 | -75 | SVC | 400
EXETER | EXET41 | 5 | 150 | -75 | SVC | 400
EXETER | EXET42 | 4 | 60 | -30 | Synchronous Compensator | 400
FECKENHAM | FECK20 | 1 |  | 60 | Reactor | 275
FECKENHAM | FECK20 | 6 | 150 | -75 | SVC | 275
FLEET | FLEE11 | 1 | 52 |  | Mechanically Switched Capacitor | 132
FLEET | FLEE11 | 2 | 52 |  | Mechanically Switched Capacitor | 132
FLEET | FLEE11 | 3 | 52 |  | Mechanically Switched Capacitor | 132
FLEET | FLEE11 | 2 |  | 60 | Reactor | 132
FLEET | FLEE12 | 1 |  | 60 | Reactor | 132
FLEET | FLEE40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
GLOUCESTER | GLOU11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
GLOUCESTER | GLOU11 | 1 |  | 60 | Reactor | 132
GLOUCESTER | GLOU11 | 2 |  | 60 | Reactor | 132
GLOUCESTER | GLOU12 | 2 | 60 |  | Mechanically Switched Capacitor | 132
GLOUCESTER | GLOU12 | 3 | 60 |  | Mechanically Switched Capacitor | 132
GRENDON | GREN11 | 1 |  | 60 | Reactor | 132
GRENDON | GREN12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
GRENDON | GREN12 | 2 | 60 |  | Mechanically Switched Capacitor | 132
GRENDON | GREN12 | 3 | 60 |  | Mechanically Switched Capacitor | 132
GRENDON | GREN40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
GRENDON | GREN40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
GRENDON | GREN40 | 3 | 225 |  | Mechanically Switched Capacitor | 400
GRENDON | GREN40 | 4 | 225 |  | Mechanically Switched Capacitor | 400
HAMS HALL | HAMH40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
HAMS HALL | HAMH40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
HAMS HALL | HAMH40 |  | 60 |  | SVC | Tertiary Connected
HARKER | HARK21 | 1 | 150 |  | Mechanically Switched Capacitor | 275
HARKER | HARK21 | 7 | 150 | -75 | SVC | 275
HARKER | HARK22 | 8 | 150 | -75 | SVC | 275
HARKER | HARK40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
HARKER | HARK40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
HARKER | HARK40 | 3 | 225 |  | Mechanically Switched Capacitor | 400
HURST | HURS1A | 1 |  | 60 | Reactor | 132
HURST | HURS1B | 2 |  | 60 | Reactor | 132
HURST | HURS20 | 1 | 150 |  | Mechanically Switched Capacitor | 275
HURST | HURS20 | 1 |  | 100 | Reactor | 275
HURST | HURS20 | 2A |  | 100 | Reactor | 275
HURST | HURS20 | 3A |  | 100 | Reactor | 275
HURST | HURS20 | 4 |  | 100 | Reactor | 275
HUTTON | HUTT40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
INDIAN QUEENS | INDQ10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
INDIAN QUEENS | INDQ10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
INDIAN QUEENS | INDQ10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
INDIAN QUEENS | INDQ10 | 1 |  | 60 | Reactor | 132
INDIAN QUEENS | INDQ40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
INDIAN QUEENS | INDQ40 | 1 |  | 200 | Reactor | 400
IRON ACTON | IROA1 | 1 | 45 |  | Mechanically Switched Capacitor | 132
IRON ACTON | IROA20 |  | 60 |  | SVC | Tertiary Connected
IRON ACTON | IROA20 |  | 60 |  | SVC | Tertiary Connected
IRONBRIDGE | IRON11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
IRONBRIDGE | IRON12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
IRONBRIDGE | IRON12 | 3 | 60 |  | Mechanically Switched Capacitor | 132
IRONBRIDGE | IRON40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
IVER | IVER21 | 1 | 40 | -30 | Synchronous Compensator | 275
IVER | IVER21 | 3 | 40 | -30 | Synchronous Compensator | 275
IVER | IVER22 | 2 |  | 60 | Reactor | 275
IVER | IVER22 | 2 | 40 | -30 | Synchronous Compensator | 275
IVER | IVER2A | 1 |  | 60 | Reactor | 275
JORDANTHORPE | JORD30 | 1 |  | 60 | Reactor | 33
KEARSLEY | KEAR11 | 1 | 52 |  | Mechanically Switched Capacitor | 132
KEARSLEY | KEAR11 | 2 | 52 |  | Mechanically Switched Capacitor | 132
KEARSLEY | KEAR11 | 3 | 52 |  | Mechanically Switched Capacitor | 132
KEARSLEY | KEAR11 | 1 |  | 60 | Reactor | 132
KINGSNORTH | KINO10 | 1 |  | 60 | Reactor | 132
KINGSNORTH | KINO10 | 2 |  | 60 | Reactor | 132
KIRKBY | KIBY11 | 1 | 45 |  | Mechanically Switched Capacitor | 132
KIRKBY | KIBY11 | 4 | 45 |  | Mechanically Switched Capacitor | 132
KIRKBY | KIBY12 | 2 | 45 |  | Mechanically Switched Capacitor | 132
KIRKBY | KIBY12 | 3 | 45 |  | Mechanically Switched Capacitor | 132
KIRKSTALL | KIRK10 | 1 |  | 60 | Reactor | 132
KIRKSTALL | KIRK10 | 2 |  | 60 | Reactor | 132
KIRKSTALL | KIRK20 | 1 | 150 |  | Mechanically Switched Capacitor | 275
LACKENBY | LACK60 | 1 | 60 |  | Mechanically Switched Capacitor | 66
LALEHAM | LALE20 | 1 |  | 100 | Reactor | 275
LALEHAM | LALE20 | 2 |  | 100 | Reactor | 275
LANDULPH | LAND10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
LANDULPH | LAND10 | 1 |  | 60 | Reactor | 132
LANDULPH | LAND40 |  | 60 |  | SVC | Tertiary Connected
LEGACY | LEGA11 | 1 |  | 60 | Reactor | 132
LEGACY | LEGA11 | 2 |  | 60 | Reactor | 132
LEGACY | LEGA40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
LISTER DRIVE | LISD20 | 1 |  | 100 | Reactor | 275
LOVEDEAN | LOVE11 | 1 |  | 60 | Reactor | 132
LOVEDEAN | LOVE12 | 2 |  | 60 | Reactor | 132
LOVEDEAN | LOVE40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
LOVEDEAN | LOVE40 | 1 |  | 200 | Reactor | 400
LOVEDEAN | LOVE40 | 7 |  | 200 | Reactor | 400
LOVEDEAN | LOVE40 | 5 | 150 | -75 | SVC | 400
MANNINGTON | MANN10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN10 | 4 | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN10 | 5 | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN10 | 6 | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN40 | 1 | 150 | -75 | SVC | 400
MANNINGTON | MANN41 | 2 | 150 | -75 | SVC | 400
MELKSHAM | MELK10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
MELKSHAM | MELK10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
MELKSHAM | MELK10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
MELKSHAM | MELK2A | 2 |  | 60 | Reactor | 275
MELKSHAM | MELK2B | 1 |  | 60 | Reactor | 275
MELKSHAM | MELK40 | 1 |  | 200 | Reactor | 400
MILL HILL | MILH11 | 1 |  | 60 | Reactor | 132
MILL HILL | MILH11 | 2 |  | 60 | Reactor | 132
MONK FRYSTON | MONF22 | 1 | 150 |  | Mechanically Switched Capacitor | 275
NECHELLS | NECH11 | 1 |  | 60 | Reactor | 132
NECHELLS | NECH12 | 2 |  | 60 | Reactor | 132
NEWCROSS | NEWX20 | 1 |  | 100 | Reactor | 275
NEWCROSS | NEWX20 | 3 |  | 100 | Reactor | 275
NINFIELD | NINF40 | 6 | 150 | -150 | SVC | 400
NORTON | NORT12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
NORWICH TROWSE | NORW10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
NORWICH TROWSE | NORW10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
NORWICH TROWSE | NORW10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
OCKER HILL | OCKH20 | 1 | 150 |  | Mechanically Switched Capacitor | 275
OLDBURY | OLDB10 | 1 |  | 60 | Reactor | 132
OLDBURY | OLDB20 |  | 60 |  | SVC | Tertiary Connected
OSBALDWICK | OSBA11 | 1 |  | 60 | Reactor | 132
PELHAM | PELH11 | 1 |  | 60 | Reactor | 132
PELHAM | PELH12 | 2 |  | 60 | Reactor | 132
PELHAM | PELH40 | 5 | 150 | -75 | SVC | 400
PELHAM | PELH40 | 6 | 150 | -75 | SVC | 400
PEMBROKE | PEMB10 | 1 |  | 60 | Reactor | 132
PEMBROKE | PEMB10 | 2 |  | 60 | Reactor | 132
PENN | PENN20 |  | 60 |  | SVC | Tertiary Connected
PENTIR | PENT40 | 1 |  | 200 | Reactor | 400
PENWORTHAM | PEWO21 | 1 |  | 60 | Reactor | 275
PITSMOOR | PITS32 | 1 |  | 60 | Reactor | 33
PITSMOOR | PITS32 | 2 |  | 60 | Reactor | 33
PYLE | PYLE20 |  | 60 |  | SVC | Tertiary Connected
PYLE | PYLE20 |  | 60 |  | SVC | Tertiary Connected
RAINHILL | RAIN11 | 1 | 45 |  | Mechanically Switched Capacitor | 132
RAINHILL | RAIN11 | 3 | 45 |  | Mechanically Switched Capacitor | 132
RAINHILL | RAIN12 | 2 | 45 |  | Mechanically Switched Capacitor | 132
RAINHILL | RAIN12 | 4 | 45 |  | Mechanically Switched Capacitor | 132
RATCLIFFE-ON-SOAR | RATS10 | 1 |  | 60 | Reactor | 132
RAYLEIGH | RAYL12 | 1 |  | 60 | Reactor | 132
ROCHDALE | ROCH10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
ROCHDALE | ROCH10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
ROCHDALE | ROCH10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
SELLINDGE | SELL40 | 1 | 1040 |  | Filter
SELLINDGE | SELL40 | 1 |  | 200 | Reactor | 400
SELLINDGE | SELL40 | 1 | 150 | -150 | SVC | 400
SELLINDGE | SELL40 | 2 | 150 | -150 | SVC | 400
SKELTON GRANGE | SKLG10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
SKELTON GRANGE | SKLG10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
SKELTON GRANGE | SKLG10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
SKELTON GRANGE | SKLG20 | 1 | 150 |  | Mechanically Switched Capacitor | 275
SKELTON GRANGE | SKLG20 | 1 |  | 100 | Reactor | 275
SPENNYMOOR | SPEN10 | 1 |  | 60 | Reactor | 132
ST JOHNS WOOD | SJOW11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
ST JOHNS WOOD | SJOW11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
ST JOHNS WOOD | SJOW11 | 3 | 60 |  | Mechanically Switched Capacitor | 132
ST JOHNS WOOD | SJOW1W | 1 |  | 60 | Reactor | 132
ST JOHNS WOOD | SJOW20 | 1 | 150 | -106 | SVC | 275
ST JOHNS WOOD | SJOW20 | 3 | 150 | -106 | SVC | 275
ST JOHNS WOOD | SJOW40 | 1 |  | 200 | Reactor | 400
ST JOHNS WOOD | SJOW40 | 4 |  | 200 | Reactor | 400
STAYTHORPE | STAY41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
STELLA WEST | STEW40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
STELLA WEST | STEW40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
SUNDON | SUND11 | 1 |  | 60 | Reactor | 132
SUNDON | SUND12 | 2 |  | 60 | Reactor | 132
SUNDON | SUND41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
SUNDON | SUND41 | 7 | 60 | -30 | Synchronous Compensator | 400
SUNDON | SUND42 | 1 | 225 |  | Mechanically Switched Capacitor | 400
SUNDON | SUND42 | 6 | 60 | -30 | Synchronous Compensator | 400
SWANSEA | SWAN12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
SWANSEA | SWAN12 | 2 | 60 |  | Mechanically Switched Capacitor | 132
SWANSEA | SWAN12 | 3 | 60 |  | Mechanically Switched Capacitor | 132
THORPE MARSH | THOM40 | 2 |  | 200 | Reactor | 400
TOTTENHAM EAST | TOTE21 | 1 |  | 100 | Reactor | 275
TOTTENHAM WEST | TOTW21 | 1 |  | 100 | Reactor | 275
TOTTENHAM WEST | TOTW22 | 2 |  | 100 | Reactor | 275
TYNEMOUTH | TYNE10 | 1 |  | 60 | Reactor | 132
USKMOUTH | USKM10 | 1 | 45 |  | Mechanically Switched Capacitor | 132
WALPOLE | WALP11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
WALPOLE | WALP11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
WALPOLE | WALP11 | 3 | 60 |  | Mechanically Switched Capacitor | 132
WALPOLE | WALP12 | 1 |  | 60 | Reactor | 132
WALPOLE | WALP1M | 2 |  | 60 | Reactor | 132
WARLEY | WARL10 | 1 | 45 |  | Mechanically Switched Capacitor | 132
WARLEY | WARL10 | 2 | 45 |  | Mechanically Switched Capacitor | 132
WARLEY | WARL10 | 3 | 45 |  | Mechanically Switched Capacitor | 132
WEST BOLDON | WBOL60 | 1 | 60 |  | Mechanically Switched Capacitor | 66
WEST BURTON | WBUR40 | 1 |  | 200 | Reactor | 400
WEST HAM | WHAM40 | 1 |  | 200 | Reactor | 400
WEST HAM | WHAM40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
WEST MELTON | WMEL12 | 1 | 45 |  | Mechanically Switched Capacitor | 132
WEST MELTON | WMEL12 | 2 | 45 |  | Mechanically Switched Capacitor | 132
WEST MELTON | WMEL12 | 3 | 45 |  | Mechanically Switched Capacitor | 132
WEST WEYBRIDGE | WWEY21 |  | 60 | -30 | Synchronous Compensator | 275
WEST WEYBRIDGE | WWEY21 |  | 60 | -30 | Synchronous Compensator | 275
WHITEGATE | WHGA10 | 1 |  | 60 | Reactor | 132
WHITEGATE | WHGA20 | 1 | 150 |  | Mechanically Switched Capacitor | 275
WILLESDEN | WISD10 | 1 |  | 60 | Reactor | 132
WILLESDEN | WISD10 | 2 |  | 60 | Reactor | 132
WILLINGTON | WILE40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
WILLINGTON | WILE40 | 8 | 150 | -75 | SVC | 400
WILLINGTON | WILE40 |  | 225 |  | Mechanically Switched Capacitor | 400
WIMBLEDON | WIMB20 | 1 |  | 100 | Reactor | 275
WIMBLEDON | WIMB20 | 2 |  | 100 | Reactor | 275
WYMONDLEY | WYMO40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
WYMONDLEY | WYMO40 | 2 | 225 |  | Mechanically Switched Capacitor | 400

## B-4-1d
Table B.4.1d - OFTO Reactive Compensation Equipment, 2014/15 | [6 empty] | Back To Menu
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
Barrow | HEYS1 | 1 |  | 24 | Shunt Reactor | 132
Barrow | BOSW3 | 1 | 5 |  | Capacitor | 33
Barrow | BOSW3 | 2 | 5 |  | Capacitor | 33
Lincolnshire | LINS1 | 1 |  | 40 | Shunt Reactor | 132
Lincolnshire | LINS1 | 2 |  | 40 | Shunt Reactor | 132
Robin Rigg East | RREW10 | 1 | 18 |  | Capacitor | 132
Robin Rigg East | RREW10 | 1 |  | 12 | Reactor | 132
Robin Rigg East | RREW10 | 1 | 18 | 18 | SVC | 132
Robin Rigg West | RRWW10 | 1 | 18 |  | Capacitor | 132
Robin Rigg West | RRWW10 | 1 |  | 12 | Reactor | 132
Robin Rigg West | RRWW10 | 1 | 18 | 18 | SVC | 132
Walney I |  | 1 |  | 40 | Reactor | 132
Westermost Rough | HEDN10 | 1 | 50 | 50 | SVC | 132
West of Duddon Sands |  | 2B |  | 60 | Shunt Reactor | 155
West of Duddon Sands |  | 3A |  | 60 | Shunt Reactor | 155
West of Duddon Sands Onshore | HEYS40 | 1B | 25 | 25 | SVC | 400
West of Duddon Sands Onshore | HEYS40 | 2B | 25 | 25 | SVC | 400
Westermost Rough | WERW1 | 1 |  | 15 | Shunt Reactor | 132
Westermost Rough | WERW1 | 2 |  | 15 | Shunt Reactor | 132

## B-4-2a
Table B.4.2a - SHE Transmission Reactive Compensation Equipment, 2015/16 to 2022/13 | [8 empty] | Back To Menu
Site Name | Change Type | Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
FORT AUGUSTUS | Addition | 2015 | FAUG3Z | 4 |  | 60 | Shunt Reactor - SGT tertiary | 33
CROSSAIG | Addition | 2015 | CRSS3X | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
CROSSAIG | Addition | 2015 | CRSS3W | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
DOUNREAY | Addition | 2018 | DOUN3Y | 3 |  | 90 | Shunt Reactor - SGT tertiary | 33
ORKNEY | Addition | 2018 | ORKN3Y | 1 |  | 90 | Shunt Reactor - SGT tertiary | 33
GILLS BAY | Addition | 2018 | GILB3J | 1 |  | 30 | Shunt Reactor | 33
TUMMEL | Addition | 2018 | TUMM2J | 1 | 225 | 75 | SVC | 275

## B-4-2b
Table B.4.2b - SPT Reactive Compensation Equipment, 2015/16 to 2023/24 | [8 empty] | Back To Menu
Site Name | Change Type | Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
GRETNA | Addition | 2015 | GRNA4- | 1 | 560 |  | SERIES CAPACITOR | 400
ECCLES | Addition | 2015 | ECCL4- | 1 | 442 |  | SERIES CAPACITOR | 400
ECCLES | Addition | 2015 | ECCL4- | 2 | 442 |  | SERIES CAPACITOR | 400
MOFFAT | Addition | 2015 | MOFF4- | 1 | 560 |  | SERIES CAPACITOR | 400
COCKENZIE | Addition | 2015 | COCK2- | 1 | 225 |  | MSCDN | 275

## B-4-2c
Table B.4.2c - NGET Reactive Compensation Equipment, 2015/16 to 2023/24 | [8 empty] | Back To Menu
Site Name | Change Type | Commissioning Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
Drakelow | Removal | 2015 | DRAK21 | 6 | 150 | -75 | SVC | 275
New Cross | Addition | 2015 | NEWX20 | 6 |  | 100 | Shunt Reactor | 275
St Johns Wood | Addition | 2015 | SJOW40 | 2 |  | 200 | Shunt Reactor | 400
Thorpe Marsh | Addition | 2015 | THOM40 | 6 |  | 225 | Shunt Reactor | 400
Thorpe Marsh | Removal | 2015 | THOM40 | 2 |  | 200 | Shunt Reactor | 400
Daines | Addition | 2016 | DAIN40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Lackenby | Addition | 2016 | LACK40 | 1 |  | 200 | Shunt Reactor | 400
Lackenby | Addition | 2016 | LACK40 | 2 |  | 200 | Shunt Reactor | 400
New Cross | Addition | 2016 | NEWX20 | 5 |  | 100 | Shunt Reactor | 275
New Cross | Removal | 2016 | NEWX20 | 1 |  | 100 | Shunt Reactor | 275
Flintshire Bridge | Addition | 2016 | LACK40 | 1 |  | 235 | Shunt Reactor | 400
Flintshire Bridge | Addition | 2016 | LACK40 | 2 |  | 235 | Shunt Reactor | 400
Daines | Addition | 2017 | DAIN40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Bolney | Addition | 2018 | BOLN40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Bolney | Addition | 2018 | BOLN40 | 1 | 75 | 75 | SVC | 400
Ninfield | Addition | 2018 | NINF40 | 1 | 75 | 75 | SVC | 400
Richborough | Addition | 2020 | RICH40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Richborough | Addition | 2020 | RICH40 | 1 | 75 | 75 | SVC | 400
Wimbledon | Removal | 2023 | WIMB20 | 1 |  | 100 | Shunt Reactor | 275
Wimbledon | Removal | 2023 | WIMB20 | 2 |  | 100 | Shunt Reactor | 275

## B-4-2d
Table B.4.2d - OFTO Reactive Compensation Equipment, 2015/16 to 2023/24 | [8 empty] | Back To Menu
Site Name | Change Type | Commissioning Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
Dudgeon | Addition | 2017 | LITD2 | 1 |  | 300 | Shunt Reactor | 275
Dudgeon | Addition | 2017 | LITD2 | 2 |  | 300 | Shunt Reactor | 275
Galloper | Addition | 2017 |  | 1 | 50 | 50 | SVC | 132
Galloper | Addition | 2017 |  | 2 | 50 | 50 | SVC | 132
Galloper | Addition | 2017 |  | 3 | 50 | 50 | SVC | 132
Galloper | Addition | 2017 |  | 1 | 55.1 |  | Mechanically Switched Capacitor | 13.9
Galloper | Addition | 2017 |  | 2 | 55.1 |  | Mechanically Switched Capacitor | 13.9
Galloper | Addition | 2017 |  | 3 | 55.1 |  | Mechanically Switched Capacitor | 13.9
Galloper | Addition | 2017 |  | 1 |  | 43.1 | Shunt Reactor | 13.9
Galloper | Addition | 2017 |  | 2 |  | 43.1 | Shunt Reactor | 13.9
Galloper | Addition | 2017 |  | 3 |  | 43.1 | Shunt Reactor | 13.9
Necton | Addition | 2017 |  | 1 | 95 | 95 | SVC | 132
Necton | Addition | 2017 |  | 2 | 95 | 95 | SVC | 132
Bodelwyddan | Addition | 2019 |  | 1 | 7.5 | 7.5 | SVC | 400
Bodelwyddan | Addition | 2019 |  | 2 | 7.5 | 7.5 | SVC | 400
Burbo Bank Extension | Addition | 2018 |  | 1 |  | 50 | Shunt Reactor | 220
Burbo Bank Extension | Addition | 2018 |  | 2 |  | 50 | Shunt Reactor | 220
Docking Shoal | Addition | 2020 | DOCS1 | 1 |  | 40 | Shunt Reactor | 132
Docking Shoal | Addition | 2020 | DOCS1 | 2 |  | 25 | Shunt Reactor | 132
Docking Shoal | Addition | 2020 | DOCS1 | 3 |  | 15 | Shunt Reactor | 132
Race Bank | Addition | 2020 | RACB1 | 1 |  | 40 | Shunt Reactor | 132
Race Bank | Addition | 2020 | RACB1 | 2 |  | 25 | Shunt Reactor | 132
Race Bank | Addition | 2020 | RACB1 | 3 |  | 15 | Shunt Reactor | 132