# Grid Code Workgroup Consultation Response Proforma

GC0102 EU Connection Codes GB Implementation – Mod 3

Industry parties are invited to respond to this consultation expressing their views and supplying the rationale for those views, particularly in respect of any specific questions detailed below.

Please send your responses by 5pm on Thursday 9th November 2017 to grid.code@nationalgrid.com.  Please note that any responses received after the deadline or sent to a different email address may not receive due consideration by the Workgroup.

Any queries on the content of the consultation should be forwarded to grid.code@nationalgrid.com with subject clearly stating ‘GC0102 Consultation Query’

| Respondent: | Isaac Gutierrez Senior Electrical Engineer Telephone number work: 01416143104 Mobile: 07761693652 Email: igutierrez2@scottishpower.com |
| --- | --- |
| Company Name: | Scottishpower Renewable Ltd (UK) |
| Please express your views regarding the Workgroup Consultation, including rationale. (Please include any issues, suggestions or queries) | ## For reference, the Grid Code objectives are: - To permit the development, maintenance and operation of an efficient, coordinated and economical system for the transmission of electricity - To facilitate competition in the generation and supply of electricity (and without limiting the foregoing, to facilitate the national electricity transmission system being made available to persons authorised to supply or generate electricity on terms which neither prevent nor restrict competition in the supply or generation of electricity) - Subject to sub-paragraphs (i) and (ii), to promote the security and efficiency of the electricity generation, transmission and distribution systems in the national electricity transmission system operator area taken as a whole - To efficiently discharge the obligations imposed upon the licensee by this license and to comply with the Electricity Regulation and any relevant legally binding decisions of the European Commission and/or the Agency; and - To promote efficiency in the implementation and administration of the Grid Code arrangements |

Standard Workgroup Consultation questions

| Q | Question | Response |
| --- | --- | --- |
| 1 | Do you believe that GC0102 Original Proposal, or any potential alternatives for change that you wish to suggest, better facilitates the Grid Code Objectives? | Yes |
| 2 | Do you support the proposed implementation approach? | No, timescales for implementation of the modifications are being rushed. |
| 3 | Do you have any other comments? | No |
| 4 | Do you wish to raise a WG Consultation Alternative Request for the Workgroup to consider? | No If yes, please complete a WG Consultation Alternative Request form, available on National Grid's website, http://www2.nationalgrid.com/uk/industry-information/electricity-codes/grid-code/modifications/forms-and-guidance/ and return to the Grid Code inbox at grid.code@nationalgrid.com |

Specific GC0102 Consultation Questions

| Q | Question | Response |
| --- | --- | --- |
| 5 | Do you have any comments on the structure of the proposed relationship between the D Code, G59 and G83, and G98 and G99? In particular which of the three options in Section 3.2 of this consultation do you support and why? | SPR preferred option is number 2 as both type A and micro generator requirements will be covered in one document |
| 6 | Do you agree with the organization of G99 and how it applies to the different Types of generation? Do you have any alternative suggestions for structure? | Yes |
| 7 | Do you agree with the current view of how the Grid and Distribution Codes (and G98 and G99) will be applied to installations where new PGMs are installed alongside existing pre-RfG equipment? (see page 11) | Yes |
| 8 | Do you agree on the introduction of a Preliminary Operation Notification relating to the Compliance process for Transmission connected Type B and Type C PGMs? (See Workgroup discussions section) | Yes |
| 9 | Do you agree with the retaining of the current GB arrangements for automatic connection and reconnection and the logic for it? If not, what alternative should be proposed? (see section 4.1.2.2) | Yes |
| 10 | Do you consider any parts of the proposed compliance, simulation or testing requirements for distribution-connected generators to be disproportionately onerous? (See section 5.2.5) | Yes, in particular the Fault ride through testing. Although it appears in the current UK Grid Code there is no evidence that in the UK any developer has carried out such test. SPR suggest removal of this section as the current practice for compliance is for the wind turbine manufacturer to type test generating units at the factory, provide a type test report to NGET and provide FRT simulations that prove compliance with the UK Grid Code. Also LFSM-U shall not be requested for windfarms |
| 11 | Do you agree it is appropriate to drop the designation Large and Small from the Distribution Code as proposed in section 3.3.1 of this consultation? Do you believe it is appropriate to drop the designation Large, Medium and Small from the Grid Code? | Yes, although compliance process will need further revision if this categorization is dropped. |
| 12 | Do you have any comments on the draft requirements for fault recording equipment for distribution-connected Type C PGMs as drafted in Section 13.11 and Appendix C3 of G99? | Section C3.2.1 does not specify the minimum inputs required for the recording device Section C3.4 under what circumstances the DNO has the right to request demonstration of accuracy and functionality. Need to be clearer on this requirement |
| 13 | Do you agree that it is appropriate to include storage in G98 and G99, noting that as storage is explicitly excluded from the RfG, the technical requirements that arise solely from the RfG are not applied to storage in G09 and G99? | Yes |
| 14 | Do you agree that it is appropriate to include Type A PGMs <800W in capacity in G99, noting that those technical requirements that emanate from the RfG are not applied to PGMs <800W? | No, SPR disagree |
| 15 | If you do not consider the proposed solution to sufficiently harmonise the connection requirements for new parties connecting to the transmission and distribution networks, how would you propose this to be addressed? (See Workgroup discussions section) | No comment |
| 16 | G98 and G99 include specific requirements for power quality, harmonic compliance etc. Do you believe it should be possible to use other international standards or requirements to achieve these ends such that these specific requirements can be dropped from these documents? An explanation of your views would be useful. | Yes, other standards should be use as well. For example, currently in the UK developers have to meet the planning levels at the PoC in line with the requirements of Engineering recommendations G5/4. The power quality measurement equipment in continental Europe facilitates harmonics measurements in line with IEC standard which is not included in G99. Allowing the use of other standards like IEC will definitively facilitate procurement of equipment for power stations. |
| 17 | Do you agree that the explanation of type testing, both full and partial, and the inclusion of equipment certificates, is sufficiently clear and unambiguous in G99 drafting? Please make any suggestions that could add clarity. | Disagree. It is not clear the scope of what fully type tested or partially type tested should be. There should be a section indicating what makes a power generating unit fully type tested (list of criteria to meet) i.e FRT type testing, VC type testing?. From SPR experience and according to G99 it would be impossible for a wind turbine to be fully type tested as protection interface always is done on site. |
| 18 | The application of new technical requirements to non-type tested generation connecting to distribution networks will give rise to new processes etc. Please comment on how comprehensive the coverage of this is in the current drafting of G99 and please suggest any improvements |  |
| 19 | Do you have any views on how the data and information required and articulated within G99 can or should relate to the Distribution Data Registration Code in the Distribution Code? | No |
| 20 | Do you believe that this modification helps to promote transparency across the Industry and if not which areas should be improved? (see Workgroup discussions section) | Yes |

Legal drafting questions

| Q | Question | Response |
| --- | --- | --- |
| 21 | The Proposed draft Grid Code legal text contains a number of comments incorporating both internal and workgroup comments. Please feel free to provide further comment on the documents (Annex 1-5) | Annex 1 PC.A.5.1.1 Each Generator (including those undertaking OTSDUW), with existing or proposed Power Stations directly connected, or to be directly connected, to the National Electricity Transmission System, shall provide NGET with data relating to that Plant and Apparatus, both current and forecast, as specified in PC.A.5.2, PC.A.5.3, PC.A.5.4 and PC.A.5.7 as applicable. Each DC Converter Station owner or HVDC System Owner, with existing or proposed DC Converter Stations or HVDC Systems (including Generators undertaking OTSDUW which includes an OTSDUW DC Converter) directly connected, or to be directly connected, to the National Electricity Transmission System, shall provide NGET with data relating to that Plant and Apparatus, both current and forecast, as specified in PC.A.5.2 and PC.A.5.4. For Power Generating Modules the data suppied by the Generator should reflect the true and accurate behaviour of each Power Generating Module under both steady state and dyanamic conditions. Generators who supply Power Generating Module simulation models (including DC Connected Power Park Modules) and HVDC System Owners who supply HVDC System models shall ensure that the models provided have been verified against the compliance tests and results submitted as specified in ECPXXX and confirmed as a true and accurate refelction of their performance by NGET. Allowance will be made for new forms of Power Generating Modules (including DC Connected Power Park Modules) and HVDC Systems where new technology has been employed and the final model cannot be verified until site tests have been completed. In which case Generators and HVDC System Owners are required to submit preliminary data which in their and NGET’s view best represents the performance of their equipment Annex 2 ECC.6.3.6.1.2.1 Type A Power Generating Modules shall be equipped with a logic interface (input port) in order to cease Active Power output within five seconds following an instruction being received at the input port. . NGET may specify any additional requirements (including remote operation) ECC.6.3.6.1.2.2 Type B Power Generating Modules shall be equipped with an interface (input port) in order to be able to reduce Active Power output following an instruction at the input port. NGET may specify any additional requirements (including remote operation) ECC.6.3.17.1 Subsynchronous Torsional Interaction Damping Capability ECC.6.3.17.2.1 Not withstanding the requirements of ECC6.1.9 and ECC.6.1.10, wWhen several HVDC Converter Stations or other plants and User’s equipment are within close electrical proximity, NGET the relevant TSO may specify that a study is required, and the scope and extent of that study, to demonstrate that no adverse interaction will occur. If adverse interaction is identified, the studies shall identify possible mitigating actions to be implemented to ensure compliance with the requirements of the Grid Code ECC.6.5.6.2 Type B, Type C and Type D Power Park Modules, HVDC Equipment, Network Operators and Non Embedded Customers are required to be capable of exchanging operational metering data with NGET and Relevant Transmission Licensees (as applicable) with time stamping as specified by NGET. ECC.6.5.6.7 The automatic controller referred to in ECC.6.5.6.5 paragraph 1 shall be capable of receiving the following signal types from NGET the relevant system operator: (a) operational metering signals, receiving at least the following: (i) start-up command; (ii) Active Power setpoints; (iii) Frequency Sensitive Mode settings; (iv) Reactive Power, voltage or similar setpoints; (v) Reactive Power control modes; (vi) power oscillation damping control; and (vii)if available synthetic inertia. ECC.6.6.2.1 Each Type C and Type D Power Generating Module including DC Connected Power Park Modules shall be fitted with equipment capable of monitoring the real time Active Power output of a Power Generating Module when operating in Frequency Sensitive Mode ECC.6.6.2.2 with regard to real-time monitoring of FSM: (i) To monitor the operation of Active Power frequency response as detailed in ECC.6.6.2.1, each Generator shall be equipped with a communication interface capable of to transfertransferring at the least the following Frequency response data signals the Frequency response data in real time and in a secured manner from the Power Station to NGET:. the network control centre of the relevant system operator or the relevant TSO. At the request of NGET the relevant system operator or the relevant TSO, the Generator should provide at least the following signals: — status signal of FSM (on/off), — scheduled Active Power output, — actual value of the Active Power output, — actual parameter settings for Active Power Frequency response, — droop and deadband; ECC.6.5.6.4 (a) NGET shall provide system control and data acquisition (SCADA) outstation interface equipment. Subject to the requirements of ECC.6.5.6.5, the User shall provide such voltage, current, Frequency, Active Power and Reactive Power measurement outputs and plant status indications and alarms to the Transmission SCADA outstation interface equipment as required by NGET in accordance with the terms of the Bilateral Agreement. In the case of OTSDUW, the User shall provide such SCADA outstation interface equipment and voltage, current, Frequency, Active Power and Reactive Power measurement outputs and plant status indications and alarms to the SCADA outstation interface equipment as required by NGET in accordance with the terms of the Bilateral Agreement. (b) For the avoidance of doubt, for Active Power and Reactive Power measurements, circuit breaker and disconnector status indications from: (i) CCGT Modules from Type B, Type C and Type D Power Generating Modules at Large Power Stations, the outputs and status indications must each be provided to NGET on an individual CCGT Unit basis. In addition, where identified in the Bilateral Agreement, Active Power and Reactive Power measurements from Unit Transformers and/or Station Transformers must be provided. (ii) DC Converters at DC Converter Stations and OTSDUW DC Converters, the outputs and status indications must each be provided to NGET on an individual DC Converter basis. In addition, where identified in the Bilateral Agreement, Active Power and Reactive Power measurements from converter and/or station transformers must be provided. (iii) Type B, Type C and Type D Power Park Modules at Embedded Large Power Stations and at directly connected Power Stations, the outputs and status indications must each be provided to NGET on an individual Power Park Module Annex 3 CPECP.6.6.1 The Interim Operational Notification will be time limited, the expiration date being specified at the time of issue. The Interim Operational Notification may be renewed by NGET for up to a maximum of 24 months from the date of the first issue of the Interim Operational Notification. NGET may only issue an extension to an Interim Operational Notification beyond 24 months provided the Generator or HVDC System Owner has applied for a derogation for any remaining Unresolved Issues to the Authority as detailed in ECP.9. ECP.7.2.2 In the case of any Power Generating Module, OTSUA (if applicable) or DC ConverterHVDC Equipment these tests will reflect the relevant technical requirements and will comprise one or more of the following: (a) Rreactive capability tests to demonstrate that the Power Generating Module, OTSUA (if applicable) or DC ConverterHVDC Equipment can meet the requirements of CC.ECC.6.3.2. These may be witnessed by NGET on site if there is no metering to the NGET Control Centre. (b) voltage control system tests to demonstrate that the Power Generating Module, OTSUA (if applicable) or DC ConverterHVDC Equipment can meet the requirements of CC.ECC.6.3.6, CC.ECC.6.3.8 and, in the case of Power Park Module, OTSUA (if applicable) and DC ConverterHVDC Equipment, the requirements of CC.ECC.A.7 and, in the case of Generating UnitSynchronous Power Generating Module and CCGT Module, the requirements of CC.ECC.A.6, and any terms specified in the Bilateral Agreement as applicable. These tests may also be used to validate the Excitation System model (PC.A.5.3) or voltage control system model (PC.A.5.4) as applicable. These tests may be witnessed by NGET. (c) governor or frequency control system tests to demonstrate that the Power Generating Module, OTSUA (if applicable) or HVDC Equipment can meet the requirements of CC.ECC.6.3.6, CC.ECC.6.3.7, where applicable CC.ECC.A.3, and BC.3.7. The results will also validate the Mandatory Service Agreement required by CC.ECC.8.1. These tests may also be used to validate the Governor model (PC.A.5.3) or frequency control system model (PC.A.5.4) as applicable. These tests may be witnessed by NGET. (d) fault ride through tests in respect of a Power Station with a Registered Maximum Capacity of 100MW or greater, comprised of one or more Power Park Modules, to demonstrate compliance with ECC.6.3.15.1 (a), (b) and (c), CC.ECC.6.3.15.2 (a), (b) and (c), CC.ECC.A.4.1, CC.ECC.A.4.2 and CC.ECC.A.4.3. Where test results from a Manufacturers Data & Performance Report as defined in CPECP.10 have been accepted this test will not be required. (e) any further tests reasonably required by NGET and agreed with the User to demonstrate any aspects of compliance with the Grid Code and the CUSC Contracts. ECP.7.5 If a Final Operational Notification can not be issued because the requirements of CPECP.7.2 and CPECP.7.3 have not been successfully met prior to the expiry of an Preliminary Operational Notification or an Interim Operational Notification then the Generator or DC Converter Station ownerHVDC System Owner (where licensed in respect of its activities) and/or NGET shall apply to the Authority for a derogation. The provisions of CPECP.9 shall then apply. ECP.10.4A Generator referencing a Manufacturer’s Data & Performance Report should insert the relevant Manufacturer’s Data & Performance Report reference in the appropriate place in the DRC data submission and / or in the User Data File Structure. NGET will consider the suitability of a Manufacturer’s Data & Performance Report: (a) in place of DRC data submissions a mathematical model suitable for representation of the entire Power Park Module as per CPECP.A.3.4.4. For the avoidance of doubt only the relevant sections as specified in PC.A.2.5.5.7 apply. Site specific parameters will still need to be submitted by the Generator. (b) in place of Fault simulation studies as follows; NGET will not require Fault Ride Through simulation studies to be conducted as per CPECP.A.3.5.1 and qualified in CPECP.A.3.5.2 provided that; (i) Adequate and relevant Power Park Unit data is included in respect of Fault Ride Through testing covered in CPECP.A.614.7.1 in the relevant Manufacturer’s Data & Performance Report , and (ii) For each type and duration of fault as detailed in CPECP.A.3.5.1, the expected minimum retained voltage is greater than the corresponding minimum voltage achieved and successfully ridden through in the fault ride through tests covered by the Manufacturer’s Data & Performance Report. (c) to reduce the scope of compliance site tests as follows; (i) Where there is a Manufacturer’s Data & Performance Report in respect of a Power Park Unit which covers Fault Ride Through, NGET may agree that no Fault Ride Through testing is required. ECP.A.3.6.23 The simulation study should comprise of a Generating UnitSynchronous Power Generating Module, DC Converter or Power Park Module Power Generating Module or HVDC Equipment connected to the total System with a local load shown as “X” in figure CPECP.A.3.6.1. The load “X” is in addition to any auxiliary load of the Power Station connected directly to the Generating UnitSynchronous Power Generating Module, DC Converter or Power Park Module Power Generating Module or HVDC Equipment and represents a small portion of the System to which the Generating UnitSynchronous Power Generating Module, DC Converter or Power Park Module Power Generating Module or HVDC Equipment is attached. ECP.A.3.6.66 To allow validation of the model used to simulate load rejection in accordance with CCECC.6.3.7(c)(i) as described a further simulation study is required to represent the largest positive Frequency injection step or fast ramp (BC1 and BC3 of Figure 2) that will be applied as a test as described in OC5.A.2ECP.A.5.8 and OC5.A.3ECP.A.6.6. ECP.A.3.7.2 To demonstrate the LFSM-U low Frequency control when operating in Limited Frequency Sensitive Mode the Generator or HVDC System Owner shall submit a simulation study representing the response of the Power Generating Module or HVDC Equipment operating at 80% of Maximum Capacity. The simulation study event shall be equivalent to: (i) a sufficiently large reduction in the measured System Frequency ramped over 10 seconds to cause an increase in Active Power output to the Maximum Capacity followed by (ii) 60 seconds of steady state with the measured System Frequency depressed to the same level as in ECP.A.3.6.8.1 (i) as illustrated in Figure ECP.A.3.6.1 below. (iii) then increase of the measured System Frequency ramped over 10 seconds to cause a reduction in Active Power output back to the original Active Power level followed by at least 60 ECP.A.4.3.2 NGET accept that the signals specified in ECP.A.4.3.1(c) may have lower effective sample rates than those required in ECC.6.6.2 although any signals supplied for connection to NGET’s recording equipment which do not meet at least the sample rates detailed in ECC.6.6.2 should have the actual sample rates indicated to NGET before testing commences.. ECP.A.6.3 Power Park Modules with Maximum Capacity ≥100MW Pre 70% Power Park Module Tests ECP.A.6.6.4 Prior to conducting the full set of tests as per ECP.A.6.6.6, Generators are required to conduct the preliminary set of tests below to confirm the frequency injection method is correct and the plant control performance is within expectation. The test numbers refer to Figure 1 below. The test should be conducted when sufficient MW resource is forecasted in order to generate at least 65% of Maximum Capacity of the Power Park Module. The following frequency injections shall be applied when operating at module load point 4. Test No (Figure1); Frequency Injection; Notes. 8; • Inject -0.5Hz frequency fall over 10 sec • Hold for a further 20 sec • At 30 sec from the start of the test, Inject a +0.3Hz frequency rise over 30 sec. • Hold until conditions stabilise • Remove the injected signal. 13; • Inject - 0.5Hz frequency fall over 10 sec • Hold until conditions stabilise • Remove the injected signal. 14; • Inject +0.5Hz frequency rise over 10 sec • Hold until conditions stabilise • Remove the injected signal. H; • Inject - 0.5Hz frequency fall as a stepchange • Hold until conditions stabilise • Remove the injected signal. I; • Inject +0.5Hz frequency rise as a stepchange • Hold until conditions stabilise • Remove the injected signal. ECP.A.6.6.7 The tests are divided into the following two types; (i) Frequency response volume tests as per ECP.A.5.8. Figure 1. These tests consist of frequency profile and ramp tests. (ii) System islanding and step response tests as shown by ECP.A.6.6. Figure 2. (iii) Frequency response tests in Limited Frequency Sensitive Mode (LFSM) to demonstrate LFSM-O and LFSM-U capability as shown by ECP.A.6.6 Figure 2. MLP6 LFSM and MLP4 LFSM -0.6Hz and -0.1Hz shall be removed from windfarm testing ECP.A.6.6.9 The target frequency adjustment facility should be demonstrated from the normal control point within the range of 49.9Hz to 50.1Hz by step changes to the target frequency setpoint ECP.A.6.7 Fault Ride Through Testing Additional comments to Annex 3 an appendix should be included showing the formatting of a generic compliance statement as issued by NGET |
| 22 | Do you have any views on the structure of the Grid Code drafting for System Management and Compliance? (Annex 1-5) | No |
| 23 | Are there are any areas in the Grid Code or Distribution Code drafting which you do not believe reflect the requirements of the RfG or HVDC Codes and, if so, why do you believe they are deficient? (Annex 1-9) | Yes, particularly those sections in relation to grid code testing of windfarms for LFSM-U. The testing for widnfarm under LFSM-U should be removed as teh requirement is not mandatory if you do not have the headroom to provide it whihc in LFSM is not possible for a windfarm unless the windfarm de-loads. FRT testing should also be considered for removal |
| 24 | Please make any other comments on the legal text drafting for the Distribution Code, G98 and G99 using the appropriate templates issued with this consultation. |  |